## Front & Preliminaries
|  |  |  | SPECIFICATION | November
|  |  |  | S-734L | 2020
Information Requirements for
AC Uninterruptible Power Supply (UPS)
System (PIP ELSAP04)
Revision history
| VERSION | DATE | PURPOSE
| 1 | November 2020 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-734L Information Requirements for
AC Uninterruptible Power Supply (UPS) System (PIP ELSAP04)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
S-734L Information Requirements for
AC Uninterruptible Power Supply (UPS) System (PIP ELSAP04)
Introduction
The purpose of this information requirements specification (IRS) is to define Information requirements for the procurement of AC uninterruptible power supply (UPS) systems in accordance with IOGP S-734 for application in the petroleum and natural gas industries. This document defines the information requirements, including format, timing and purpose, for information to be provided by the manufacturer. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the supplementary requirements specification IOGP S-734, quality requirements specification IOGP S-734Q and equipment data sheet IOGP S-734D which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification

## Supplier Instructions
S-734L Information Requirements for
AC Uninterruptible Power Supply (UPS) System (PIP ELSAP04)
Supplier Instructions
In response to Invitation To Tender (ITT)
Tenderers to submit information as defined in column E - 'Submit At Proposal' in 'Requirements' sheet, in accordance with ITT instructions
On award of contract
Specified Information requirements shall be submitted in accordance with contract information submission instructions. Suppliers to prepare and submit 'Supplier Master Information Schedule' (SMIS) incorporating information requirements in accordance with columns F - 'First Issue Post Purchase Order' in 'Requirements' sheet. Supplier to demonstrate compliance with each information requirement either by providing document number cross reference to the Requirement in 'Supplier Master Information Schedule' (SMIS) and, if specified in the Contract, using column J 'Fulfilled by Document Number(s)' in the IRS Requirements Sheet.
On completion of scope
Supplier to validate that the information delivered meets the IRS requirements either through cross reference to the deliverable type in a as-built version of the 'Supplier Master Information Schedule' SMIS and, if specified in the Contract, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in Requirement sheet populated with the specific document numbers issued to the Purchaser.
IRS Structure Contents
1 |  | 'Front & Preliminaries' Tab
The 'Front & Preliminaries ' tab includes an IOGP Front sheet for the IRS followed by Acknowledgements, a Disclaimer, Copyright Notice, Foreword and Introduction
2 |  | 'Supplier Instructions' Tab
This 'Supplier Instructions' tab provides instructions that Suppliers are to follow in response to this IRS.
3 |  | 'Requirements' Tab
The 'Requirements' tab lists the suite of information requirements that are to be supplied during tendering and following award of the purchase order to deliver the purchase order scope. The information requirements are grouped under three broad categories; Management information requirements: Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. Technical information requirements: Technical information developed by the supplier or their sub suppliers, during the design and development, acquisition, manufacture, assembly and testing of the contracted scope. Purchase Order Specific Information Requirements: Information requirements specified by individual owners-operators in addition to those specified by IOGP-JIP33 to meet specific operational, project or legislative requirements. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. "The 'Requirements' tab includes columns A to L, including Column A for the relevant requirement code and Column B for the Requirement for the different Information Requirements (Data, Documents and/or Models) to be provided by suppliers, based on the parent standard, IOGP Specification or the specified parent industry Standard. Condition Invoking Revoking Requirement Column C is included to allow any specific conditions to be identified that may require a additional deliverable(s). Typical Deliverable Column D is provided for Purchaser to identify the deliverable type that the information would typically appear within; this also allows the Purchaser's Requisitioning Engineers to group the various Information Requirements by Deliverable Type. Column E includes Submission Requirements (Yes or No) at Proposal, while columns F, G & H identify Issue Purpose (For Information or For Acceptance) and Durations (Period or Weeks/Months) for First Issue of the particular deliverable Post Purchase Order. Required As Built, Fulfilled by Document Number(s), Translation Required and Remarks columns I, J, K & L are also included. Definitions for each column are contained in the rows above the columns: Abbreviations used for various submission requirements in Column H are shown in table 3.1 below:
Table 3.1 - Information Submission Abbreviations
4 |  | 'Definitions' Tab
The 'Definitions' tab includes several columns A to F, including Column A for the relevant Code & Column B for the Requirement for the different Information (Data, Documents and/or Models) Requirements to be provided by Suppliers, all copied from the 'Requirements' tab. Column C includes a full description of the Information Requirement based on the Parent Standard, IOGP Specification or an Industry Standard. Column D gives a reference to the Parent Standard, IOGP Specification or an Industry Standard that the Information requirement is identified in. Column E identifies the Requirement format as listed in Table 9.1 below. Column F relates the CFIHOS discipline document type that could be used to classify the document having this IRS content. Definitions for each column are contained in the rows above the columns:
5 |  | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various tabs of this workbook.
Buyer |  |  | Organisation placing a Contract or Purchase Order with Supplier for equipment or services on project; may be alternatively referred to as 'User' or 'Purchaser'
CFIHOS |  |  | Capital Facilities Information Hand Over Specification
Company |  |  | Project Operating Entity or the organisation Contractor is under contract to
Contractor |  |  | Project Contractor responsible for procuring equipment.
Information |  |  | Data, Documents and/or Models
IRS |  |  | Information Requirements Specification
PO |  |  | Purchase Order
QRS |  |  | Quality Requirements Specification
SMIS |  |  | Supplier Master Information Schedule
Supplier |  |  | Organisation supplying equipment or services to Company and/or Contractor on project; may alternatively be referred to as "Vendor", "Seller" or “Manufacturer”.
6 |  | CFIHOS
The Information Requirements are also classified according to document classification published in v1.4 of Capital Facilities Information Hand Over Specification (CFIHOS). The objective of CFIHOS is to create a common information standards across the process industries. Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org/about/
7 |  | Document Metadata
Typical Metadata for Information Deliverables to be provided by Suppliers is shown in Table 7.1 below
Table 7.1 - Supplier Deliverable Metadata
8 |  | Deliverable Formats
The format of the relevant Information Deliverable to be submitted by Supplier for Buyer/Contractor is to be as described in table 8.1 below. Where required to be ‘As Built’, deliverables are to be updated and handed over in the native format.
Table 8.1 – Deliverable Formats

## Requirements
S-734L Information Requirements for AC Uninterruptible Power Supply (UPS) System (PIP ELSAP04)
Requirements
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement based on the description in the Parent Standard, IOGP Specification or an Industry Standard Information Requirement Title.
C | Condition Invoking Requirement - describes special condition(s) under which the Information Requirement is required; e.g.. service offshore and weight greater than 1 tonne means information is required. NB: if blank, always required
D | Typical Deliverable - Purchaser to advise the short description of the Information Deliverable that would typically include this Information Requirement
E | Submit With Proposal - Yes or No, where 'Yes' means the Information Requirement is required to be submitted with Suppliers Proposal or 'No' is not required
F, G & H | First Issue Post Purchase Order - issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the Information Requirement and Period defined after Purchase Order placement.
I | Required As Built - Yes or No, where 'Yes' means the Information Requirement is required to be 'As Built' on completion or delivery of equipment or 'No' is not required 'As Built'
J | Fulfilled by Information Deliverable Number(s) - identifies which Information Requirement(s) listed in the Supplier Master Information Schedule (SMIS) addresses the Purchasers requirements. NB; it should be noted that one Information Deliverable can fulfil more than one Information Requirement.
K | Translation Required -Yes or No, where 'Yes' means the Information Requirement should be translated into a language(s) (to be advised) other than English and 'No' means to be provided in English
L | Remarks - may include bid clarification questions & decisions (specify author & date)
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S734-IR-1 | Supplier master information schedule |  | Information Deliverables List | No | For Acceptance |  | WAO | Yes |  | No
S734-IR-2 | Delivery schedule |  | Delivery/Production Schedule | Yes | For Information |  | WAO | No |  | No
S734-IR-3 | Progress report |  | Progress Report | No | For Information |  | WAO (Monthly) | No |  | No
S734-IR-4 | Quality plan | Required for CAS A, B, C | Quality Plan | Yes | For Acceptance |  | - | No
S734-IR-6 | Inspection and test plan |  | Inspection and Test Plan (ITP) | No | For Acceptance |  | WAO | No |  | No
S734-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | WAO (Monthly) | Yes |  | No
S734-IR-8 | Non-conformance records |  | Nonconformance History | No | For Acceptance |  | WPTD | Yes |  | No
S734-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No |  | No
S734-IR-61 | Nominated sub-supplier list and scope | Required for CAS A and B | Sub-Supplier List | Yes | For Information |  | WAO | No |  | No
S734-IR-64 | Inspection Release Notes (Authorization to Release Equipment) |  | Inspection Release Notes | No | For Acceptance |  | WAT | No |  | No
Technical Information Deliverables
S734-IR-20 | General Arrangement Drawing |  | General Arrangement Drawing | Yes | For Information |  | WAO | Yes |  | No
S734-IR-29 | Design Datasheet |  | Design Datasheet | Yes | For Acceptance |  | WAO | Yes |  | No
S734-IR-23 | Supplier Technical Information |  | Manufacturers Datasheet | Yes | For Information |  | WAO | No |  | No
S734-IR-24 | Single Line Diagram |  | Single Line Diagram | Yes | For Acceptance |  | WAO | Yes |  | No
S734-IR-25 | Wiring Diagram |  | Wiring Diagram | No | For Acceptance |  | WAO | Yes |  | No
S734-IR-65 | Schematic Diagram |  | Schematic Diagram | No | For Acceptance |  | WAO | Yes |  | No
S734-IR-60 | Short Circuit Protection Device Coordination Data |  | Short Circuit Protection Device Coordination Data | No | For Information |  | WAO | Yes |  | No
S734-IR-32 | Bill Of Materials |  | Bill Of Materials | No | For Information |  | WPTD | Yes |  | No
S734-IR-66 | Recommended Spare Part List |  | Spare Part List | No | For Information |  | WPTD | Yes |  | No
S734-IR-34 | Packing List |  | Packing List | No | For Information |  | WPTD | No |  | No
S734-IR-35 | Installation Manual |  | Installation Manual | No | For Information |  | WPTD | No |  | No | Include Hardcopy (Yes / No)
S734-IR-37 | Operating Manual |  | Operating Manual | No | For Information |  | WPTD | No |  | No | Include Hardcopy (Yes / No)
S734-IR-36 | Maintenance Manual |  | Maintenance Manual | No | For Information |  | WPTD | No |  | No | Include Hardcopy (Yes / No)
S734-IR-67 | Obsolescence management plan |  | Obsolescence management plan | Yes | For Information |  | WPTD | No |  | No
S734-IR-39 | Factory Acceptance Test (FAT) Procedure |  | Factory Acceptance Test (FAT) Procedure | No | For Acceptance |  | WPTT | No |  | No
S734-IR-41 | Factory Acceptance Test (FAT) Records |  | Factory Acceptance Test (FAT) Records | No | For Acceptance |  | WAT | No |  | No
S734-IR-43 | Type Test Report |  | Type Test Report | No | For Information |  | WAO | No |  | No | Type Test data to be made available upon request.
S734-IR-68 | Seismic Certification | When seismic certification is required due to site location | Certificate of Conformance | No | For Acceptance |  | WPTD | No |  | No
S734-IR-45 | Nameplates |  | Name Plate Drawing | No | For Acceptance |  | WAO | Yes |  | No
S734-IR-46 | Full Load Heat Rejection Rate |  | Heat Dissipation Calculation & Loads | Yes | For Information |  | WAO | No |  | No
S734-IR-55 | Efficiency, Reliability & Availability |  | Reliability, Availability, Safety Integrity Level Calculation | Yes | For Information |  | WAO | No |  | No
S734-IR-57 | Battery Sizing Calculation |  | Design Calculation | Yes | For Information |  | WAO | No |  | No
S734-IR-62 | Site Acceptance Test (SAT) Procedure |  | Site Acceptance Test (SAT) Procedure | No | For Acceptance |  | WPTT | No |  | No
S734-IR-63 | Site Acceptance Test (SAT) Records |  | Site Acceptance Test (SAT) Records | No | For Acceptance |  | WAT | No |  | No | Applicable only if site test (battery capacity test) is included in the order.
Purchase Order Specific Information Requirements

## Definitions
S-734L Information Requirements for AC Uninterruptible Power Supply (UPS) System (PIP ELSAP04)
Definitions
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement that would typically provide the Information required, based on the description in the Parent Standard, IOGP Specification or an Industry Standard Title.
C | Description - an excerpt from the Parent Standard, IOGP Specification or Industry Standard.
D | Reference - reference to the Parent Standard, IOGP Specification or Industry Standard that the Information Deliverable is identified in.
E | Format - defines the required format of the relevant Information Requirement to be submitted by Supplier for Purchaser/Contractor for information and acceptance as shown in Table 9.1 of Instructions Tab and selected from pick list.
F | CFIHOS Discipline Document Type Code - the CFIHOS discipline document type that could be used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Deliverables
S734-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Supplier] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Supplier] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S734-IR-2 | Delivery schedule | Schedule depicting design, supply, manufacture, inspection, testing and delivery activities to be executed by [supplier]. Schedule details typically** include; a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [supplier's] standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S734-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, internal and outsourced inspection and audit activities. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S734-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [supplier], and when applicable [sub-supplier] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q1/Q2 may be used to inform the development of Service Quality Plans] |  | PDF
S734-IR-6 | Inspection and test plan | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [supplier], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. | (IOGP S-734, 4.20, 4.22.1) | PDF | CFIHOS-70000180
S734-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000389
S734-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [supplier/sub-supplier] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [supplier] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S734-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. | (IOGP S-734, 4.21.1) | PDF | CFIHOS-70000154
S734-IR-61 | Nominated sub-supplier list and scope | Definition of products, services or processes, that will be externally provided and the controls to be applied by the supplier to ensure conformance with agreed requirements. |  | Native
S734-IR-64 | Inspection Release Notes (Authorization to Release Equipment) | Supplier Release Notes are to be issued by the Buyer, which the Supplier is to endorse together with the Buyers representative. In some circumstances the Buyer may decide to waive final inspection, in which case the Buyer is to complete a Release Note, which is to be endorsed 'Inspection waived' at the Buyer's office. | (IOGP S-734, 4.21.2) | PDF
Technical Information Deliverables
S734-IR-20 | General Arrangement Drawing | The drawing(s) will contain the following information: • Overall dimensions, critical interface dimensions • Equipment / components with cross sectional views • Location of ventilation openings • Terminal blocks for field connections • Weights of assemblies, equipment and components • Location of cabinet grounds • Center of gravity • Withdrawal/installation and maintenance space • Installation, achoring and mounting details (including removal cable gland plates) • Lifting arrangement | (IOGP S-734, 4.22.1, 4.22.2, 4.22.3) | PDF
S734-IR-29 | Design Datasheet | The S-734 datasheet provides technical information about the UPS equipment, including supplier information. | (IOGP S-734, 4.22.3, Table 1) | Native | CFIHOS-70000117
S734-IR-23 | Supplier Technical Information | Documentation providing technical data and characteristics about material, products or systems and their environment for proper implementation. These documents provide a structured data form containing part number/model, design information, I/O data address mapping, operational data and limitations of the equipment relating to meeting the performance criteria of S-734 specification, PIP ELSAP04 Table 1 and purchasers data sheet S-734D. | (IOGP S-734, 4.22.3, Table 1) | PDF | CFIHOS-70000416
S734-IR-24 | Single Line Diagram | A diagram depicting the main equipment items and current ratings (e.g. rectifiers, charger, batteries, transformers, protection and isolation devices). | (IOGP S-734, 4.22.1, 4.22.2, 4.22.3) | PDF | CFIHOS-70000371
S734-IR-25 | Wiring Diagram | Diagram providing information on the circuitry, including the following: – Graphical symbols representing the objects – Graphical symbols representing the connections among objects – Reference designations – Terminal designations – Signal level conventions (applicable to logic signals) – Information necessary to trace paths and circuits (signal designations, location references) – Supplementary information necessary for the understanding of functions – Customer connections to be clearly identified – Cable and cable core identification. | (IOGP S-734, 4.17.4, 4.22.1, 4.22.2, 4.22.3) | PDF | CFIHOS-70000268
S734-IR-65 | Schematic Diagram | A pictorial representation of the main elements and functions of a control circuit for electrical equipment with input/output sources (switches, relays etc.) and their relationships. Details logic functions of the circuit. | (IOGP S-734, 4.22.1, 4.22.2, 4.22.3) | PDF | CFIHOS-70000328
S734-IR-60 | Short Circuit Protection Device Coordination Data | Short Circuit Protection Device Coordination Data for Purchaser power system studies. Necessary to determine the capacity of electrical equipment under fault conditions. Typically input and output circuit breakers and fuses. | (IOGP S-734, Figure 1, Table 1) | PDF
S734-IR-32 | Bill Of Materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and references to material specifications. | (IOGP S-734, 4.22.1, 4.22.2, 4.22.3) | PDF | CFIHOS-70000028
S734-IR-66 | Recommended Spare Part List | Table containing list items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for later use. Mandatory content of information: – Item reference number; – Quantity; – Part number or global identifier (together with manufacturer / supplier); – Part name. Optional content of information: – Type designation; – Specifying technical data; – Descriptive technical data; – Mass, dimensions; – Reference to document; – Remark. | (IOGP S-734, 4.22.1, 4.22.3) |  | CFIHOS-70000374
S734-IR-34 | Packing List | A detailed list of the equipment being packaged and shipped. | (IOGP S-734, 4.21.11, 4.22.1, 4.22.3) | PDF | CFIHOS-70000269
S734-IR-35 | Installation Manual | Description of equipment installation methods including the mounting, setting, erection, etc. | (IOGP S-734, 4.22.3) | PDF | CFIHOS-70000181
S734-IR-37 | Operating Manual | Description of equipment operation including instructions, procedures, drawings, tables, etc. for the operation, startup, switching and isolation. Supplier to include in the operating manual (or hand over to purchaser) any system configured/protected password needed for the maintenance and operation (e.g. battery float and equalize voltages, temperature alarms and battery charge duration) of the equipment. | (IOGP S-734, 4.22.3) | PDF | CFIHOS-70000228
S734-IR-36 | Maintenance Manual | Description of equipment maintenance. Typically originating from the equipment or package supplier. | (IOGP S-734, 4.22.3) | PDF | CFIHOS-70000206
S734-IR-67 | Obsolescence management plan | Plan defining the manufacturer's co-ordinated activities to direct and control the strategies for the identification and mitigation of the effects of obsolescence to the user, through all stages of the life of all components within the UPS System. An example of the principles of this plan is defined within IEC 62402, Obsolescence management – Application guide. | (IOGP S-734, 4.1.4.1, 4.22.3, Table 3) | PDF
S734-IR-39 | Factory Acceptance Test (FAT) Procedure | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document includes: - All testing activities and their acceptance criteria - Test set-up and test equipment to be used - Transfer of data via specified communication protocol demonstration/simulation | (IOGP S-734, 4.20.1, 4.20.6, 4.20.7) | PDF
S734-IR-41 | Factory Acceptance Test (FAT) Records | The FAT report will be used for acceptance of the equipment being supplied. This document includes all testing activities, test results, corresponding analysis and outcome. This includes S-734Q: routine and special testing (4.3), functional testing (4.4) and full load testing (4.5) | (IOGP S-734, 4.20.1, 4.20.6, 4.20.7) | PDF
S734-IR-43 | Type Test Report | The results of test performed to provide evidence that the design meets the requirements of the functional specification shall be made available upon request. | (IOGP S-734, 4.20.3) | PDF
S734-IR-68 | Seismic Certification | Document providing equipment certification by third party for seismic design. | (IOGP S-734, 4.2.6) | PDF | CFIHOS-70000013
S734-IR-45 | Nameplates | Graphic and equipment information posted on the UPS that depicts layout and procedures required as referenced to PIP ELSAP04 (4.19 Tagging and Nameplates). | (IOGP S-734, 4.19, 4.22) | PDF
S734-IR-46 | Full Load Heat Rejection Rate | This document contains the calculation by the manufacturer to arrive at the heat load produced by the equipment, which is typically used for HVAC sizing. | (IOGP S-734, 4.22.1) | PDF
S734-IR-55 | Efficiency, Reliability & Availability | Demonstrates operating reliability and availability of purchased equipment (e.g. mean time between failure data) and UPS system overall efficiency. | (IOGP S-734, 4.1.4.1, 4.1.4.2, 4.20.6 7 i) | PDF | CFIHOS-70000312
S734-IR-57 | Battery Sizing Calculation | Document providing information about data, and basic conditions and assumptions used for selection and sizing of appropriate batteries. | (IOGP S-734, 4.13.2) | PDF | CFIHOS-70000086
S734-IR-62 | Site Acceptance Test (SAT) Procedure | Procedure documenting the manufacturers recommended site tests including battery capacity test, discrete functional unit and overall system, interlocks (electrical, mechanical), interfaces, protection and communications. | (IOGP S-734, 4.20.1) | PDF
S734-IR-63 | Site Acceptance Test (SAT) Records | Records demonstrating results of site tests including battery capacity test, discrete functional unit and overall system, interlocks (electrical, mechanical), interfaces, protection and communications. | (IOGP S-734, 4.20.1, 4.20.2) | PDF
Purchase Order Specific Information Requirements

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
Intelligent Vector (CAD)
Multi media (Film)
Raster Image (Bitmap)
Structured Data (MS Apps)
Technical Publication (Text)
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: