## Front & Preliminaries
|  |  |  | SPECIFICATION | October
|  |  |  | S-737D | 2021
Procurement Data Sheet for
Deluge Skids
Revision history
| VERSION | DATE | PURPOSE
| 1 | October 2021 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-737D Data Sheet for
Deluge Skids
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
S-737D Data Sheet for
Deluge Skids
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of deluge skids in accordance with IOGP S-737 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-737), information requirements specification (IOGP S-737L) and quality requirements specification (IOGP S-737Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Procurement Data Sheet
Row | S-737D Procurement Data Sheet for Deluge Skids | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Applicable to : | select |  | select | [5 empty] | select | proposal | purchase | as-built
5 |  | Skid build (model) number : | input data |  | input data
6 |  | Quantity of deluge valves on skid : | input data |  | input data
7 |  | Base frame (skid) material : | input data |  | input data
8 |  | Deluge system type : | select |  | select | [5 empty] | select | water | foam-water
9 |  | Spill containment : | select |  | select | [5 empty] | select | required | not required
10 |  | Project owner : | input data |  | input data
11 |  | Purchaser name : | input data |  | input data
12 |  | Project name : | input data |  | input data
13 |  | Site location : | input data |  | input data
14 |  | Package supplier : | input data |  | input data
15 |  | Structural design code : | select |  | select | [5 empty] | select | NORSOK | Eurocode | DNVGL | ISO | EEMUA | ASTM | API | AWS/AISC
16 |  | Package piping design code : | select |  | select | [5 empty] | select | ASME B31.3 | EN 13480 | supplier standard piping design code
17 |  | Conformity assessment system (CAS) level : | select |  | select | [5 empty] | select | A | B | C | D
18 |  | Local language : | input data |  | input data
19 | 4.3 | Design life : | input data | years | input data | years
20 |  | Fluid type : | select |  | select | [5 empty] | select | sea water | fresh water | industrial water | other
21 |  | Maximum skid dimensions
22 |  | Maximum length : | input data | select | input data | select |  |  |  |  | select | mm | in
23 |  | Maximum width : | input data | select | input data | select |  |  |  |  | select | mm | in
24 |  | Maximum height : | input data | select | input data | select |  |  |  |  | select | mm | in
25 |  | Foam concentrate fluid data
26 |  | Foam concentrate manufacturer and product name : | input data |  | input data
27 |  | Maximum viscosity at minimum temperature : | input data | cP | input data | cP
28 |  | Minimum viscosity at maximum temperature : | input data | cP | input data | cP
29 |  | Site conditions
30 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
31 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
32 |  | Seismic design requirements : | input data |  | input data
33 |  | Severe corrosive atmospheres : | select |  | select | [5 empty] | select | yes | no
34 |  | Unusual conditions : | select |  | select | [5 empty] | select | dust | fume | dust and fume | corrosive agents | not applicable
35 | 4.6 | Special weather protection : | select |  | select | [5 empty] | select | tropicalization | winterization | not required
36 |  | Minimum and maximum design temperature range : | input data | select | input data | select |  |  |  |  | select | °C | °F
37 |  | Relative humidity at design temperature range : | input data | % | input data | %
38 | 4.6 | Ice load : | input data | select | input data | select |  |  |  |  | select | kg/m² | lb/ft²
39 | 4.6 | Snow load : | input data | select | input data | select |  |  |  |  | select | kg/m² | lb/ft²
40 |  | Design wind velocity : | input data | select | input data | select |  |  |  |  | select | m/s | ft/s
41 |  | Wave induced acceleration loads : | input data | select | input data | select |  |  |  |  | select | m/s² | ft/s²
42 |  | Blast drag pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag | inH₂O
43 |  | Blast over pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag | inH₂O
44 |  | Deluge valve skid location : | select |  | select | [5 empty] | select | indoor | outdoor | partially enclosed
45 |  | Explosive atmospheres
46 |  | Hazardous area certification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
47 |  | IEC 60079 / NFPA 70, 505
48 |  | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0
49 |  | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC
50 |  | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
51 |  | NFPA 70, 500
52 |  | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | division 2 | division 1
53 |  | Explosion group : | select |  | select | [5 empty] | select | Class I Group A | Class I Group B | Class I Group C | Class I Group D
54 |  | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T2A | T2B | T2C | T2D | T3 | T3A | T3B | T3C | T4 | T4A | T5 | T6
55 |  | SIL
56 | 4.8 | SIL requirement for deluge valve : | select |  | select | [5 empty] | select | SIL 1 | SIL 2 | SIL 3 | none
57 | 4.8 | SIL requirement for pressure transmitter : | select |  | select | [5 empty] | select | SIL 1 | SIL 2 | SIL 3 | none
58 | 4.8 | SIL requirement for solenoid : | select |  | select | [5 empty] | select | SIL 1 | SIL 2 | SIL 3 | none
59 |  | Performance requirements
60 | 4.2, 4.7.8 | Deluge system 1 - design water flow rate : | input data | select | input data | select |  |  |  |  | select | l/min | m³/hr | gpm
61 | 4.2, 4.7.8 | Deluge system 2 - design water flow rate : | input data | select | input data | select |  |  |  |  | select | l/min | m³/hr | gpm
62 | 4.2, 4.7.8 | Deluge system 3 - design water flow rate : | input data | select | input data | select |  |  |  |  | select | l/min | m³/hr | gpm
63 | 4.2, 4.7.8 | Deluge system 4 - design water flow rate : | input data | select | input data | select |  |  |  |  | select | l/min | m³/hr | gpm
64 | 4.2, 4.7.8 | Deluge system 5 - design water flow rate : | input data | select | input data | select |  |  |  |  | select | l/min | m³/hr | gpm
65 | 4.7.8, 6.2.5.6 | Deluge system 1 - minimum downstream operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
66 | 4.7.8, 6.2.5.6 | Deluge system 2 - minimum downstream operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
67 | 4.7.8, 6.2.5.6 | Deluge system 3 - minimum downstream operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
68 | 4.7.8, 6.2.5.6 | Deluge system 4 - minimum downstream operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
69 | 4.7.8, 6.2.5.6 | Deluge system 5 - minimum downstream operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
70 | 6.4.3 | Skid inlet minimum water pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
71 | 6.4.3 | Maximum skid inlet pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
72 | 10.2.1, 5.8.6, 6.4.10 | Skid inlet minimum foam concentrate pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
73 | 10.2.1, 5.8.6, 6.4.10 | Skid inlet maximum foam concentrate pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
74 |  | System components
75 |  | Deluge valve
76 | 5.1.2.1, 5.1.2.2, 5.1.2.3 | Deluge valve manufacturer : | input data |  | input data
77 | 5.1.2.1 | Deluge valve size system 1 : | select |  | select | [5 empty] | select | NPS 2 | NPS 3 | NPS 4 | NPS 6 | NPS 8 | NPS 10 | NPS 12 | DN 50 | DN 80 | DN 100 | DN 150 | DN 200 | DN 250 | DN 300
78 | 5.1.2.1 | Deluge valve size system 2 : | select |  | select | [5 empty] | select | NPS 2 | NPS 3 | NPS 4 | NPS 6 | NPS 8 | NPS 10 | NPS 12 | DN 50 | DN 80 | DN 100 | DN 150 | DN 200 | DN 250 | DN 300
79 | 5.1.2.1 | Deluge valve size system 3 : | select |  | select | [5 empty] | select | NPS 2 | NPS 3 | NPS 4 | NPS 6 | NPS 8 | NPS 10 | NPS 12 | DN 50 | DN 80 | DN 100 | DN 150 | DN 200 | DN 250 | DN 300
80 | 5.1.2.1 | Deluge valve size system 4 : | select |  | select | [5 empty] | select | NPS 2 | NPS 3 | NPS 4 | NPS 6 | NPS 8 | NPS 10 | NPS 12 | DN 50 | DN 80 | DN 100 | DN 150 | DN 200 | DN 250 | DN 300
81 | 5.1.2.1 | Deluge valve size system 5 : | select |  | select | [5 empty] | select | NPS 2 | NPS 3 | NPS 4 | NPS 6 | NPS 8 | NPS 10 | NPS 12 | DN 50 | DN 80 | DN 100 | DN 150 | DN 200 | DN 250 | DN 300
82 | 5.1.2.1 | Deluge valve model system 1 : | input data |  | input data
83 | 5.1.2.1 | Deluge valve model system 2 : | input data |  | input data
84 | 5.1.2.1 | Deluge valve model system 3 : | input data |  | input data
85 | 5.1.2.1 | Deluge valve model system 4 : | input data |  | input data
86 | 5.1.2.1 | Deluge valve model system 5 : | input data |  | input data
87 | 5.1.2.1, 6.2.5.6 | Pressure regulating : | select |  | select | [5 empty] | select | yes | no
88 |  | Speed control : | select |  | select | [5 empty] | select | required | not required
89 |  | Deluge valve approval : | select |  | select | [5 empty] | select | required | not required
90 |  | Deluge valve approval standard : | input data |  | input data
91 |  | Solenoid valve
92 | 6.2.5.7 | Solenoid valve make and model : | input data |  | input data
93 | 6.2.5.7 | Solenoid valve normal state : | select |  | select | [5 empty] | select | energized | not energized
94 |  | Solenoid valve approval : | select |  | select | [5 empty] | select | required | not required
95 |  | Solenoid valve approval standard : | input data |  | input data
96 |  | Isolation valves
97 | 6.2.4.3 | System approval body/organisation : | input data |  | input data
98 | 6.2.1.1, 6.2.1.2, 6.2.1.3, 6.2.4.3, 6.2.5.3 | Globe valve design code : | input data |  | input data
99 | 6.2.1.1, 6.2.1.2, 6.2.1.3, 6.2.4.3, 6.2.5.3 | Butterfly valve design code : | input data |  | input data
100 | 6.2.1.1, 6.2.1.2, 6.2.1.3, 6.2.4.3, 6.2.5.3 | Ball valve design code : | input data |  | input data
101 | 6.2.1.1, 6.2.1.2, 6.2.1.3, 6.2.4.3, 6.2.5.3 | Gate valve design code : | input data |  | input data
102 | 5.1.3.2 | Water supply isolation valve : | select |  | select | [5 empty] | select | required | not required
103 |  | Check valve
104 | 6.2.5.2, 6.3.2.2 | Check valve design code : | input data |  | input data
105 |  | Test line
106 | 10.1.3, 6.2.4.1, 6.2.4.2, 6.2.4.3 | Test line functional requirement : | select |  | select | [5 empty] | select | full flow | minimum flow to demonstrate performance | not required
107 | 6.2.4.1 | Test line size : | select |  | select | [5 empty] | select | mm | inch | not applicable
108 | 5.8.2 | Foam sample drain valve : | select |  | select | [5 empty] | select | required | not required
109 | 6.2.4.2 | Dry test connection : | select |  | select | [5 empty] | select | required | not required
110 |  | Bypass line
111 | 10.1.4, 6.1.1, 6.1.2, 6.2.1.2, 6.2.1.3 | Bypass line : | select |  | select | [5 empty] | select | required | not required
112 | 10.1.4, 6.1.2 | Type of bypass isolation valve : | input data |  | input data
113 |  | Pipe and fittings
114 | 4.4.4 | Piping design code/specification : | input data |  | input data
115 |  | Strainer
116 | 5.6.1.1, 5.6.1.2, 5.6.1.3, 6.3.4.1, 6.3.4.3 | Main pipeline strainer : | select |  | select | [5 empty] | select | required | not required
117 |  | Main pipeline strainer approval : | input data |  | input data
118 |  | Strainer casing material : | input data |  | input data
119 |  | Strainer basket material : | input data |  | input data
120 | 5.6.1.2 | Foam concentrate line strainers : | select |  | select | [5 empty] | select | required | not required
121 | 6.3.4.2, 6.3.4.3 | Flushing drain hose connection details : | input data |  | input data
122 | 5.6.1.2 | Spray nozzle / sprinkler orifice size : | input data | select | input data | select |  |  |  |  | select | mm | in
123 |  | Foam concentrate proportioner
124 | 5.1.1.1, 6.3.2.4, 6.4.1, 6.4.2, 6.4.3, 6.4.7 | Foam concentrate proportioning method : | input data |  | input data
125 | 5.8.6, 5.8.7 | Foam concentrate proportioner pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa
126 | 6.4.2 | Foam mixing ratio : | select | % | select | % |  |  |  |  | select | 1 | 3 | 6
127 | 5.1.1.1 | Foam chemical properties : | select |  | select | [5 empty] | select | information provided | information not provided
128 |  | Foam injection point : | select |  | select | [5 empty] | select | downstream deluge valve | upstream deluge valve
129 | 6.4.3 | Foam proportioning inlet pressure differential : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
130 |  | Foam proportioner approval : | select |  | select | [5 empty] | select | required | not required
131 |  | Foam proportioner approval standard : | input data |  | input data
132 |  | System approval body/organization : | input data |  | input data
133 |  | Transfer hose connection equipped with a dip pipe : | select |  | select | [5 empty] | select | required | not required
134 |  | Foam pump
135 |  | Back up foam concentrate pump : | select |  | select | [5 empty] | select | required | not required
136 |  | Foam pump approval : | select |  | select | [5 empty] | select | required | not required
137 |  | Foam pump approval standard : | input data |  | input data
138 |  | Manufacturer : | input data |  | input data
139 |  | Model number : | input data |  | input data
140 |  | Pump size : | input data |  | input data
141 |  | Number of stages : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
142 |  | Rated flow : | input data | select | input data | select |  |  |  |  | select | m³/h | US gpm
143 |  | Rated discharge pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
144 |  | Foam supply
145 | 6.4.6, 6.4.8, 6.4.9 | Foam concentrate source : | select |  | select | [5 empty] | select | atmospheric type storage tank | pressure type storage tank | connection to foam concentrate distribution line | not applicable
146 |  | Foam tank approval : | input data |  | input data
147 |  | Foam tank design standard : | select |  | select | [5 empty] | select | ASME section VIII Div. 1 | ASME section VIII Div. 2 | EN 13445 | PD 5500 | other | not applicable
148 |  | ASME code stamp : | select |  | select | [5 empty] | select | required | not required
149 |  | PED compliant : | select |  | select | [5 empty] | select | required | not required
150 |  | Foam concentrate tank design capacity : | input data | select | input data | select |  |  |  |  | select | m³ | US gal
151 | 5.8.6 | Foam concentrate tank pressure vacuum device : | select |  | select | [5 empty] | select | open vent | valve | goose neck | suppliers standard
152 |  | Air accumulator
153 |  | Air accumulator : | select |  | select | [5 empty] | select | required | not required
154 |  | Air accumulator design standard : | select |  | select | [5 empty] | select | ASME section VIII Div. 1 | ASME section VIII Div. 2 | EN 13445 | PD 5500 | other | not applicable
155 |  | Air accumulator capacity : | input data | select | input data | select |  |  |  |  | select | m³ | US gal
156 |  | Air accumulator accessories : | input data |  | input data
157 |  | ASME code stamp : | select |  | select | [5 empty] | select | required | not required
158 |  | PED compliant : | select |  | select | [5 empty] | select | required | not required
159 |  | Control panel
160 |  | Deluge skid control panel / fire suppression approval : | select |  | select | [5 empty] | select | required | not required
161 |  | Deluge skid control panel / fire suppression approval standard : | input data |  | input data
162 |  | Skid enclosure
163 | 4.4.2 | Enclosure : | select |  | select | [5 empty] | select | required | not required
164 |  | Enclosure material : | Select |  | select | [5 empty] | select | carbon steel | AISI 316 | manufacturer's standard
165 | 5.4.2.1 | Enclosure lighting : | select |  | select | [5 empty] | select | required | not required
166 | 5.5.2.2, 6.3.1.2 | Enclosure heating : | select |  | select | [5 empty] | select | required | not required
167 |  | Enclosure lifting lugs : | select |  | select | [5 empty] | select | required | not required
168 |  | Enclosure special requirements : | input data |  | input data
169 | 8.2.1 | Thermal insulation type : | input data |  | input data
170 | 8.2.1 | Thermal insulation thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
171 |  | Passive fire protection : | select |  | select | [5 empty] | select | required | not required
172 |  | Passive fire protection rating : | input data |  | input data
173 |  | Passive fire protection test performance standard : | input data |  | input data
174 |  | Enclosure fireproof method : | input data |  | input data
175 | 5.5.2.1 | Ventilation type : | select |  | select | [5 empty] | select | mechanical | natural | not required
176 | 5.5.1.2.1, Figure 2, Figure 3 | Foundation bolt type : | select |  | select | [5 empty] | select | Figure 2 | Figure 3
177 |  | Utilities
178 |  | Electric supply
179 |  | Power supply voltage : | input data | V | input data | V
180 |  | Power supply frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
181 |  | Air
182 |  | Air quality : | select |  | select | [5 empty] | select | oil free air | plant air
183 |  | Skid inlet maximum pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
184 |  | Skid inlet minimum pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
185 |  | Accessories
186 |  | Flow orifice
187 |  | Flow orifice : | select |  | select | [5 empty] | select | required | not required
188 |  | Flow orifice location : | input data |  | input data
189 |  | Fire department connection
190 |  | Type : | input data |  | input data
191 |  | Arrangement : | select |  | select | [5 empty] | select | system side of deluge valve | supply side of deluge valve | not required
192 |  | Size : | select |  | select | [5 empty] | select | DN 100 (NPS 4) | DN 150 (NPS 6) | other
193 |  | Termination : | select |  | select | [5 empty] | select | 2 x DN 65 (NPS 2½) flange | other | not applicable
194 |  | Pilot line
195 | 6.2.5.1, 6.2.5.4, 6.2.5.5, 6.2.5.8 | Deluge valve pilot line : | select |  | select | [5 empty] | select | hydraulic | hydraulic and pneumatic
196 |  | Pilot line routed to skid edge : | select |  | select | [5 empty] | select | required | not required
197 |  | Pneumatic air source : | select |  | select | [5 empty] | select | external source | air compressor | not applicable
198 |  | Pneumatic line pressure regulating valve : | select |  | select | [5 empty] | select | required | not required
199 |  | Package noise level
200 |  | Noise threshold, sound pressure level, Lp at 1 m : | input data | dB(A) | input data | dB(A)
201 |  | Equipment sound pressure level exceeds the noise threshold : | select |  | select | [5 empty] | select | yes | no
202 |  | Tubing and fittings
203 |  | Material : | input data |  | input data
204 |  | Manufacturer and type : | input data |  | input data
205 |  | Sizes : | input data | select | input data | select |  |  |  |  | select | mm | in
206 |  | Threads : | input data |  | input data
207 |  | Surface preparation and painting
208 |  | Environmental corrosivity class for coating : | select |  | select | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX | not required
209 |  | Coating standard : | select |  | select | [5 empty] | select | ISO 12944-5 | ISO 12944-9 | IOGP S-715
210 |  | Preservation and shipment
211 |  | Duration of outdoor storage : | input data | months | input data | months
212 |  | Export boxing required : | select |  | select | [5 empty] | select | required | not required
213 |  | Lifting devices for transportation and installation : | select |  | select | [5 empty] | select | required | not required
214 |  | Common electrical and instrumentation
215 | 5.4.5.3 | Electrical and instrumentation design code : | select |  | select | [5 empty] | select | IEC standard | North American standard
216 | 4.5 | Ingress protection standard : | select |  | select | [5 empty] | select | IEC 60079 | NEMA 250
217 | 4.5 | Electric motor ingress protection rating : | input data |  | input data
218 | 4.5 | Instrument control panel ingress protection rating : | input data |  | input data
219 | 4.5 | Instruments ingress protection rating : | input data |  | input data
220 | 4.5 | Junction boxes ingress protection rating : | input data |  | input data
221 | 4.5 | Cable glands ingress protection rating : | input data |  | input data
222 | 4.5 | Luminaries ingress protection rating : | input data |  | input data
223 | 5.4.4.1, 5.4.4.2 | Cable gland material : | select |  | select | [5 empty] | select | SS 316 | brass with nickel coating | copper free aluminium | plastic
224 |  | Junction box material : | select |  | select | [5 empty] | select | SS 316L | glass-reinforced plastic | fibreglass reinforced plastic | carbon steel with coating
225 | 5.4.5.2, 5.4.5.3 | Cable tray, ladder and support material : | select |  | select | [5 empty] | select | SS 316 | copper free aluminium | glass reinforced plastic | hot dip galvanized mild steel
226 | 5.4.1.1, 5.4.1.2, 5.4.1.3 | Earthing and grounding system : | select |  | select | [5 empty] | select | resistance earthed | solidly earthed | other
227 |  | Fire resistant cable : | select |  | select | [5 empty] | select | not required | 1 hour | 2 hours
228 |  | Intrinsically safe cable outer sheath colour : | select |  | select | [5 empty] | select | blue | manufacturer's standard
229 | 5.4.7.5 | Cable transit certification type : | input data |  | input data
230 |  | Weights
231 |  | Deluge skid dry weight : | input data | select | input data | select |  |  |  |  | select | kg | Ibs
232 |  | Deluge skid operational weight : | input data | select | input data | select |  |  |  |  | select | kg | lbs
233 |  | Welding quality requirements
234 | 7.1, 7.2.1 | Welding specification for piping and pressure containing equipment : | input data |  | input data
Note on C4: Supplier or purchaser to select the status of the order stage.
Note on C5: Supplier to advise the assigned build/model of the product/system where applicable.
Note on C6: Supplier or purchaser to advise on the quantity of deluge valves included in the skid.
Note on C8: Purchaser to select the fire protection system type.
Note on C9: Purchaser to specify if the spill containment is required for the skid.
Note on C10: End user or operating company.
Note on C11: Agency responsible for placing the purchaser order on the equipment supplier. Could be an EPC contractor or operating company.
Note on C12: Name of the project.
Note on C14: Confirm the deluge skid supplier.
Note on C16: Supplier to provide their standard in "additional notes" column if different from ASME B31.3 or EN 13480. Valve design code to be stated here.
Note on C20: If other selected, provide details in "additional notes" column.
Note on C22: Input required at the proposal stage.
Note on C23: Required at the proposal stage.
Note on C24: Required at the proposal stage.
Note on C26: Purchaser to indicate the specific manufacturer and product name.
Note on C32: Purchaser to specify the seismic design standards or, when not applicable, to indicate not required.
Note on C33: Identify if the deluge skid is subjected to severe corrosive atmosphere.
Note on C35: See the definition of winterization in IOGP S-737.
Note on C36: A minimum and maximum temperature ratings required for components.
Note on C37: Purchaser to specify the relative humidity for the maximum and minimum temperature range specified.
Note on C41: Forces in floating structures. Refer to the met-ocean data report attached.
Note on C48: Specify the hazardous zone in which the functional or physical object is expected to operate.
Note on C49: Specify the gas group classification of the physical object in accordance with IEC 60079 or NFPA 70, 505.
Note on C50: Specify the temperature classification of the physical object in accordance with IEC 60079 or NFPA 70, 505.
Note on C52: Specify the hazardous classified location in which the functional or physical object is expected to operate.
Note on C53: Specify, for purposes of testing, approval, and area classification, various air mixtures (not oxygen-enriched) grouped in accordance with NFPA 70, 500.6(A) and (B).
Note on C54: Specify the temperature classification of the physical object in accordance with NFPA 70, 500
Note on C56: Purchaser to specify SIL requirements for the release of the deluge valve upon signal from fire and gas.
Note on C57: Purchaser to specify the SIL requirements for the pressure transmitter.
Note on C60: Purchaser to provide the design water flowrate.
Note on C61: Purchaser to provide the design water flowrate.
Note on C62: Purchaser to provide the design water flowrate.
Note on C63: Purchaser to provide the design water flowrate.
Note on C64: Purchaser to provide the design water flowrate.
Note on C65: The required pressure on the downstream side of the deluge valve to achieve the system design application rates.
Note on C66: The required pressure on the downstream side of the deluge valve to achieve the system design application rates.
Note on C67: The required pressure on the downstream side of the deluge valve to achieve the system design application rates.
Note on C68: The required pressure on the downstream side of the deluge valve to achieve the system design application rates.
Note on C69: The required pressure on the downstream side of the deluge valve to achieve the system design application rates.
Note on C71: Purchaser to provide the maximum skid inlet pressure at no flow / minimum flow condition.
Note on C72: Purchaser to confirm the upstream operating foam pressure.
Note on C73: Purchaser to confirm the upstream maximum foam pressure.
Note on C88: Purchaser to specify if the speed control (open and/or close) is required. If required, purchaser to provide supplementary details on the requirement.
Note on C90: Purchaser to specify the certification standard if the deluge valve is certified e.g. UL 260.
Note on C95: Specify the certification standard if the solenoid valve is certified.
Note on C97: Define the approval body e.g. IMO, FM approvals, UL, EU.
Note on C98: Specify the globe valve design code.
Note on C99: Specify the butterfly valve design code.
Note on C100: Specify the ball valve design code.
Note on C101: Specify the gate valve design code.
Note on C102: Purchaser to specify if the supplier is to include the isolation valve(s) at every water supply connection.
Note on C104: Specify the check valve design code.
Note on C112: Purchaser to specify if a particular type of valve is required to manually regulate the pressure.
Note on C114: NFPA 11,13,15,16 provides examples of applicable piping design codes.
Note on C116: Specify if a strainer is required.
Note on C117: If required, specify the certification standard e.g. FM 5551.
Note on C124: Specify the method of foam concentrate proportioning e.g. balanced foam proportioning.
Note on C125: Operating pressure loss across the foam proportioning unit to be specified.
Note on C126: Purchaser to confirm the foam mixing ratio.
Note on C127: Material safety data sheet (MSDS) to be provided.
Note on C129: Purchaser to specify the minimum pressure differential for foam injection e.g. 100 kPa (14,5 psi).
Note on C132: Define the approval body e.g. IMO, FM approvals, UL, EU.
Note on C135: When a back-up foam concentrate pump is specified, purchaser to provide additional details to include items like the pump operational sequence and configuration.
Note on C141: Supplier to advise the number of pump impeller stages.
Note on C145: Source of foam concentrate to be specified, especially when a foam tank is required to ensure it is added to the scope of the deluge skid.
Note on C146: If required, specify the certification standard.
Note on C147: If the pressure vessel has been specified.
Note on C153: The air accumulator can be used for air or nitrogen.
Note on C161: If required, specify the certification standard e.g. UL 864 or FM 3010.
Note on C163: Specify if an enclosure is required.
Note on C164: If required, clarify material for the enclosure where excessive climatic or mechanical exposures are expected.
Note on C165: Confirm if lighting is required inside the enclosure.
Note on C167: Purchaser to confirm.
Note on C168: Special requirements to e.g. size, shaping of skid.
Note on C169: Insulation type to be specified.
Note on C172: If required, specify the duration/rating.
Note on C173: If required, specify the applicable fire test performance standard.
Note on C174: Specify fire barrier, insulation material or intumescent paint. If fire proofing is not required, indicate "not required".
Note on C182: Instrument air is generally oil free.
Note on C188: Purchaser to indicate location(s) of flow orifices. When multiple locations are required, input all locations.
Note on C190: If required, specify the type of fire department connection.
Note on C191: For single deluge valve skids, fire department connections should connect on the system side of the deluge valve. For multiple deluge valves, a single fire department connection piping is typically arranged on the supply side of the valves.
Note on C192: Where other size is desired, purchaser to indicate the specific value in "additional comments" column. When a fire department connection is not required, selection to be blank.
Note on C193: Where other is selected, purchaser to include the type required in "additional comments" column. When a fire department connection is not required, selection to be blank.
Note on C196: When the deluge system design philosophy includes extension of the pilot line to the field for fire detection, purchaser to provide the direction for the supplier to provide a connection at the skid edge for connection to the field pilot line piping
Note on C206: Supplier to specify thread type used e.g. BSP, NPT.
Note on C209: Purchaser to select the appropriate coating standard which matches the selected corrosivity class.
Note on C229: Purchaser to specify which kind of certification type is needed, e.g. fire resistance, water tightness, hazardous area.
Note on C234: Purchaser to specify the project welding specification or international standard or IOGP S-705.

## Supplement
Row |  | S-737D Procurement Data Sheet for Deluge Skids | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
9
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
S-737D Procurement Data Sheet for
Deluge Skids
Guidance on the use of this procurement data sheet
To be used in conjunction with :
IOGP S-737 Specification for Deluge SKids.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data

## Back Cover
Month XXXX