## Front & Preliminaries
|  |  |  | SPECIFICATION | January 2024
|  |  |  | IOGP S-743D | Version 1.0
Procurement Data Sheet for
Metal-Clad Switchgear (IEEE)
Revision history
| VERSION | DATE | PURPOSE
| 1 | January 2024 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-743D (1.0) Procurement Data Sheet for
Metal-Clad Switchgear (IEEE)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-743D (1.0) Procurement Data Sheet for
Metal-Clad Switchgear (IEEE)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of metal-clad switchgear in accordance with IOGP S-743 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-743), information requirements specification (IOGP S-743L) and quality requirements specification (IOGP S-743Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)

## Procurement Data Sheet
Row | IOGP S-743D (1.0) Procurement Data Sheet for Metal-Clad Switchgear (IEEE) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Equipment identification
4 | 7.4.1 | Tag number : | input data |  | input data
5 | 7.4.1 | Tag description : | input data |  | input data
6 |  | General
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | Select | A | B | C | D
8 |  | Site conditions
9 | 4 paragraph 1, 4.1.3, 7.3.12.4.1, 8.1.1, 8.4 | Ambient air temperature - upper limit : | 40 | °C | 40 | °C |  |  |  |  | Select | 40 | 45 | 50
10 | 4 paragraph 1, 4.1.3, 7.3.12.4.1, 8.1.2, 8.4 | Ambient air temperature - lower limit : | -5 | °C | -5 | °C |  |  |  |  | Select | 0 | -5 | -20 | -30 | -40
11 | 4 paragraph 1, 4.1.3, 7.3.12.4.1, 8.1.3, 8.4, Table 8 | Altitude of installation : | ≤ 1000 | m | ≤ 1000 | m |  |  |  |  | Select | ≤ 1000 | other
12 | 4 paragraph 1, 4.1.3, 7.3.12.4.1, 8.1.4.3 | Humidity limit : | < 95 | % | < 95 | % |  |  |  |  | Select | < 95 | other
13 | 4 paragraph 1, 7.3.12.4.1 | Seismic design : | not required |  | not required | [5 empty] | Select | not required | required
14 | 4 paragraph 1 | Site location : | input data |  | input data
15 | 8.1.4.6 | Seismic certificate : | not required |  | not required | [5 empty] | Select | not required | required
16 | 4 paragraph 1, 4.1.3, 7.3.12.4.1, 8.1.4, B.3.8.1 | Installation environment : | indoor climate controlled |  | indoor climate controlled | [5 empty] | Select | indoor climate controlled | indoor ventilated | outdoor
17 | 4 paragraph 1, 4.1.3, 7.3.12.4.1, 7.30.2, 8.1.4, B.3.8.1 | Application/operating environment : | select |  | select | [5 empty] | Select | onshore | offshore - fixed | offshore - floating | marine - ship | other
18 | 4 paragraph 1, 4.1.3, 7.3.12.4.1, 7.17, 8.1.4, B.3.8.1 | Unusual environments : | none |  | none | [5 empty] | Select | none | corrosive gases | fumes-vapors-steam-salt air | excessive or metallic dust | hot and humid climates | abnormal vibration-shocks-tilting | other or multiple
19 | 7.30.2, 8.1.4.5 | Certification - additional : | not required |  | not required | [5 empty] | Select | not required | USCG/ABS | other
20 | 7.26.1, 7.26.2, 7.26.13, 7.26.14 | Arc-resistant certification : | third-party certified |  | third-party certified | [5 empty] | Select | third-party certified | self-declared | not applicable
21 |  | Electrical power system parameters
22 | 8.2 | Nominal voltage : | select | kV | select | kV |  |  |  |  | Select | 2.4 | 4.16 | 6.9 | 12.47 | 13.8 | 24.9 | 34.5 | other
23 | 5.3, 8.2 | Frequency : | 60 | Hz | 60 | Hz |  |  |  |  | Select | 50 | 60 | other
24 | 8.2 | Phase/wire : | 3-phase 3-wire |  | 3-phase 3-wire | [5 empty] | Select | 3-phase 3-wire | 3-phase 4-wire | other
25 | 8.2 | System grounding : | select |  | select | [5 empty] | Select | low resistance | high resistance | solid | ungrounded
26 | 8.5 | Available fault current (symmetrical) : | input data | kA | input data | kA
27 | 8.5 | System X/R ratio : | input data |  | input data
28 | 5.2.1 | System connection : | wye |  | wye | [5 empty] | Select | wye | delta | other
29 |  | Enclosure construction
30 | 7.26.1, 7.26.2, 7.26.9, 7.26.12 - 7.26.15 | Arc-resistant construction : | Type 2B |  | Type 2B | [5 empty] | Select | Type 2 | Type 2B | other | not required
31 | 7.26.13, 7.26.14 | Arc plenum : | not required |  | not required | [5 empty] | Select | not required | single per assembly | segregated per bus
32 | 7.26.13, 7.26.14 | Arc plenum exhaust : | not applicable |  | not applicable | [5 empty] | Select | not applicable | plenum interior exhaust | plenum exterior exhaust
33 | 8.1.4.1, 8.1.4.3 | Enclosure paint color : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | ANSI 61 | other
34 | 7.28.1.9, 8.1.4.1, 8.1.4.3, 9.2.3 | Space heater : | not required |  | not required | [5 empty] | Select | required | not required
35 | 7.28.1.9, 7.28.1.10.1, 8.1.4.1, 8.1.4.3 | Space heater control : | not applicable |  | not applicable | [5 empty] | Select | not applicable | fixed (constant ON) | thermostat | hygrostat
36 | 7.28.1.9, 7.28.1.10.1 | Space heater power supply : | external |  | external | [5 empty] | Select | external | internal
37 | 7.4.1.10 | Mimic bus : | not required |  | not required | [5 empty] | Select | not required | required
38 | 7.4.3, B.3.6 | Circuit breaker viewing window : | not required |  | not required | [5 empty] | Select | not required | required
39 |  | Bus
40 | 5.2.1, 8.2, 8.3 | Rated maximum voltage : | select | kV | select | kV |  |  |  |  | Select | 4.76 | 8.25 | 15 | 27 | 38 | other
41 | 5.4.2, 7.1.7, 8.4 | Main bus rating : | select | A | select | A |  |  |  |  | Select | 1200 | 2000 | 3000 | 4000 | other
42 | 5.4.5, 5.4.6 | Short-circuit current rating : | select | kA | select | kA |  |  |  |  | Select | 25 | 31.5 | 40 | 50 | 63 | other
43 | 7.1.7, 8.1.4.1 | Power bus plating material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | tin | silver
44 | 6.5.1, C.1 | Partial discharge test : | not required |  | not required | [5 empty] | Select | not required | required
45 | 5.2.3 | Bus tap cable insulation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | rated maximum voltage
46 |  | Incoming section
47 | 7.4.6 | Service entrance application : | not required |  | not required | [5 empty] | Select | not required | required
48 | 7.1.3.3 | Cable entry : | required |  | required | [5 empty] | Select | required | not required
49 | 7.1.3.3 | Conductor size : | input data | AWG | input data | AWG
50 | 7.1.3.3 | Conductor material : | select |  | select | [5 empty] | Select | copper | aluminum
51 | 7.1.3.3 | Number of conductors per phase : | select |  | select | [5 empty] | Select | 1 | 2 | 3 | 4 | other
52 | 7.1.3.3 | Incoming cable grounding conductor size : | input data | AWG | input data | AWG
53 | 7.1.3.3 | Number of incoming cable grounding conductors : | select |  | select | [5 empty] | Select | 1 | 2 | 3 | 4 | other
54 | 7.27.6 | Bus duct entry : | not required |  | not required | [5 empty] | Select | required | not required
55 | 7.27.6 | Incoming cable/bus entry location : | select |  | select | [5 empty] | Select | top | bottom
56 |  | Circuit breakers
57 | 7.1.3.3 | Outgoing cable entry location : | select |  | select | [5 empty] | Select | top | bottom
58 | 7.25.2 | Mechanism charging voltage : | 125 V dc |  | 125 V dc | [5 empty] | Select | 120 V ac | 125 V dc | other
59 | 7.25.2, 7.25.13 | Trip coil voltage : | 125 V dc |  | 125 V dc | [5 empty] | Select | 120 V ac | 125 V dc | 48 V dc | other
60 | 7.25.9 | Dual trip coils : | not required |  | not required | [5 empty] | Select | not required | required | breaker dependent
61 | 7.25.2 | Close coil voltage : | 125 V dc |  | 125 V dc | [5 empty] | Select | 120 V ac | 125 V dc | other
62 | 7.25.13 | Control power source : | external |  | external | [5 empty] | Select | internal control power transformer (CPT) | external
63 | 7.3.12.9 | Status indicator lights : | open-closed |  | open-closed | [5 empty] | Select | not required | open-closed | open-closed-trip
64 | 7.3.12.9.2 | Trip coil monitoring : | not required |  | not required | [5 empty] | Select | not required | indicating light | protective relay
65 | 7.3.12.6 | Circuit breaker control switch : | required |  | required | [5 empty] | Select | not required | required
66 | 7.3.12.7 | Lockout relay : | not required |  | not required | [5 empty] | Select | not required | required
67 | 7.3.12.11 | E-stop pushbutton : | not required |  | not required | [5 empty] | Select | not required | required | breaker dependent
68 | 8.1.3, 8.3, 8.7.2.1 - 8.7.2.3, 8.7.2.5 - 8.7.2.9 | Surge arresters : | not required |  | not required | [5 empty] | Select | not required | required | breaker dependent
69 | 8.3 | Surge capacitors : | not required |  | not required | [5 empty] | Select | not required | required | breaker dependent
70 |  | Metering and control
71 | 7.3.12.2, 7.3.12.3 | Incoming metering : | not required |  | not required | [5 empty] | Select | not required | power quality meter | microprocessor | digital meters | analog meters
72 | 7.3.12.2, 7.3.12.3 | Feeder metering : | not required |  | not required | [5 empty] | Select | required | not required
73 | 7.3.12.7.5, 7.3.12.8 | Test switches : | not required |  | not required | [5 empty] | Select | not required | required
74 | 7.26.3 | Arc flash detection system : | not required |  | not required | [5 empty] | Select | not required | required
75 | 7.27.7 | Auto transfer scheme : | not required |  | not required | [5 empty] | Select | not required | required
76 | 7.27.7 | Breaker interlocking scheme : | not required |  | not required | [5 empty] | Select | not required | required
77 | 7.3.12.4.5 | Provisions for remote monitoring and control : | not required |  | not required | [5 empty] | Select | not required | monitoring only | monitoring and control
78 | 7.3.3.4.2.1, 7.3.3.4.2 | Communication media : | select |  | select | [5 empty] | Select | ethernet copper | ethernet fiber | serial | multiple | other
79 | 7.3.3.4.2.1, 7.3.3.4.2 | Network redundancy : | select |  | select | [5 empty] | Select | none | parallel (PRP) | high availability (HSR) | multiple | other
80 | 7.3.3.4.2.1, 7.3.3.4.2 | Communication protocol : | select |  | select | [5 empty] | Select | PROFIBUS | PROFINET | Modbus TCP/IP | IEC 61850 | multiple | other
81 | 7.3.12.4.5 | Communication system power supply : | select |  | select | [5 empty] | Select | internal simplex | internal redundant | external simplex | external redundant
82 |  | Accessories
83 | 7.29.10.1 | Continuous thermal monitoring : | not required |  | not required | [5 empty] | Select | not required | required
84 | 7.29.10.1 | Thermal monitoring analytical software : | not required |  | not required | [5 empty] | Select | not required | required
85 | 7.29.9, B.3.6 | Thermal scanning inspection windows : | not required |  | not required | [5 empty] | Select | not required | required
86 | 7.29.10.4 | Partial discharge monitoring : | not required |  | not required | [5 empty] | Select | not required | required
87 | 7.29.10.2.1, 7.29.10.2.3 - 7.29.10.2.5, 7.29.10.2.12, 7.29.10.3 | Motor condition monitoring : | not required |  | not required | [5 empty] | Select | not required | local (manual) | continuous
88 | 7.15, 7.29.6 | Portable lift truck : | 1 |  | 1 | [5 empty] | Select | not required | 1 | 2 | other
89 | 8.1.4.2 | Ventilation filters : | not required |  | not required | [5 empty] | Select | not required | required
90 | 7.29.10.1.4 | Application software : | not required |  | not required | [5 empty] | Select | not required | required
91 | 7.29.7 | Handheld control station : | not required |  | not required | [5 empty] | Select | not required | 1 | 2 | other
92 | 7.29.3.1 | Remote racking device : | not required |  | not required | [5 empty] | Select | not required | integral | external
93 | 7.16, 7.29.8 | Circuit breaker test cabinet : | not required |  | not required | [5 empty] | Select | not required | required
94 | 7.21 | Ground and test device : | not required |  | not required | [5 empty] | Select | not required | required
95 | 7.31 | Grounding (earthing) switch : | not required |  | not required | [5 empty] | Select | required | not required | with a fault rating
96 |  | Shipping and preservation
97 | 9.2.3, 9.7.9.1 | Equipment preservation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | special
98 | 9.2.3, 9.7.9.2 | Provisions for energizing space heaters for storage : | not required |  | not required | [5 empty] | Select | not required | required
99 | 9.2.3, 9.3 | Desiccant bags installed for shipping : | every compartment |  | every compartment | [5 empty] | Select | not required | each vertical section | each MV breaker compartment | every compartment
100 | 9.2.1 | Impact sensors for shipping : | not required |  | not required | [5 empty] | Select | not required | shipping splits | MV breakers | splits and breakers | other
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the tag (e.g., process facility name, location within the facility).
Note on C7: Select the CAS level to be applied in IOGP S-743Q, Annex A. CAS D requires the fewest quality interventions and information requirements. The default selection of CAS level D is typically used for trusted manufacturers with whom the user has experience. Default value : D
Note on C9: Select the upper limit of ambient air temperature measured outside of the enclosure. The default value as per IEEE Std C37.20.2 is 40 °C. Default value : 40
Note on C10: Select the lower limit of ambient air temperature. The default values as per IEEE Std C37.20.2 are -5 °C for indoor and -30 °C for outdoor applications. Default value : -5
Note on C11: Select the MC switchgear installation altitude. IEEE Std C37.20.2 is based on the altitude not to exceed 1000 m (3300 ft). Derating information is provided in Table 8. If "other" is selected, specify the altitude in the "Additional notes" column. Default value: ≤ 1000
Note on C12: Select the humidity limit. As per IEEE Std C37.20.2, default value measured over 24 hours not to exceed 95% non-condensing. If "other" is selected, specify the humidity in the "Additional notes" column. Default value : < 95
Note on C13: Select whether the seismic design is required as per ASCE/SEI 7-16. Default value : not required
Note on C14: Specify the site physical address or latitude and longitude to determine the seismic acceleration values.
Note on C15: Select whether a third-party seismic certificate is required. Default value : not required
Note on C16: Select the installation environment of the MC switchgear. Default value : indoor climate controlled
Note on C17: Select the operating environment for MC switchgear. If "other" is selected, specify the operating environment in the "Additional notes" column.
Note on C18: Select the unusual environments or contaminant exposure to the MC switchgear. If "other or multiple" is selected, specify in the "Additional notes" column. Default value : none
Note on C19: Select the certification requirements in addition to NRTL or ACO. If "other" is selected, specify in the "Additional notes" column. Default value : not required
Note on C20: Select the required certification to IEEE Std C37.20.7:2017 for arc resistance testing. Default value : third-party certified
Note on C22: Select the nominal system voltage that the power system will operate. This will determine the VT ratio used in the assembly. If "other" is selected, specify the voltage (in kV) in the "Additional notes" column.
Note on C23: Select the nominal operating frequency. If "other"' is selected, specify in the "Additional notes" column. Default value : 60
Note on C24: Select the power system type. If "other" is selected, specify the phase in the "Additional notes" column. Default value : 3-phase 3-wire
Note on C25: Select the grounding system of the facility to which the MC switchgear will be connected.
Note on C26: Specify the available fault current (symmetrical) of the system at the MC switchgear point of connection (incomer) from the purchaser's power system study.
Note on C27: Specify the X/R ratio (system reactance / system resistance) at the MC switchgear point of connection (incomer). Higher X/R ratios can result in derating of short circuit ratings.
Note on C28: Select the system connection. If "other" is selected, specify the system connection in the "Additional notes" column. Default value : wye
Note on C30: Select whether the MC switchgear requires arc-resistant construction that is verified through testing for internal arcing faults. Arc-resistant Type 2B enclosures (as per IEEE Std C37.20.7) provide protection for personnel and improve electrical safety. Default value: Type 2B
Note on C31: Select whether an arc plenum is required. If so, specify if one plenum is needed for the complete assembly or if one is required for each main bus (e.g., secondary selective, multiple bus, double tie). A plenum may not be available from all manufacturers. Default value: not required
Note on C32: If a plenum is required, select the location of the arc plenum exhaust. Additional information is required for the arrangement or configuration of the room or space where the MC switchgear is located. Default value : not applicable
Note on C33: Select the enclosure paint color. If "other" is selected, specify the enclosure paint color in the "Additional notes" column. Default value : manufacturer's standard
Note on C34: Select whether vertical section space heaters are required. Default value : not required
Note on C35: If enclosure space heaters are required, specify the controls type. Default value : not applicable
Note on C36: If enclosure space heaters are required, specify the source for the power supply. If "internal" is selected, the manufacturer will supply the control power transformers (CPTs). Default value : external
Note on C37: Select whether a mimic bus is required to be installed on the front of the switchgear assembly. Default value : not required
Note on C38: Select whether a circuit breaker viewing window is required to be installed on the front of each circuit breaker compartment door. Default value : not required
Note on C40: Refer to IEEE Std C37.20.2, Table 1. If "other" is selected, specify the voltage (in kV) in the "Additional notes" column.
Note on C41: Select the main bus rating. For other main bus sizes, specify special bus requirements in the "Additional notes" column.
Note on C42: Select the short-circuit current rating. If "other" is selected, refer to IEEE Std C37.04-2018, Table 8 and specify the value in the "Additional notes" column.
Note on C43: Select the bus plating material. Tin is preferred over silver in corrosive gas environments. Default value : manufacturer's standard
Note on C44: Select whether the partial discharge test in accordance with 6.5.1 is to be performed on the assembly. Default value : not required
Note on C45: Select whether the insulation level for cable connections to the bus bar system is the manufacturer's standard or greater than or equal to the rated maximum voltage of the assembly. Default value : manufacturer's standard
Note on C47: Specify whether the MC switchgear is to be designated as the service disconnecting equipment. Refer to UL DLAH guide and NFPA 70 (NEC) for service entrance requirements. Default value : not required
Note on C48: Select whether cable entry is required. If required is selected, complete rows 49 to 53 of this procurement data sheet. Default value : required
Note on C49: If cable entry is specified, specify the conductor size needed for the incoming service.
Note on C50: If cable entry is specified, select the conductor material. Copper is typically used.
Note on C51: If cable entry is specified, select the number of conductors per phase. If "other" is selected, specify the number of conductors in the "Additional notes" column.
Note on C52: If cable entry is specified, specify the size of the incoming cable grounding conductor.
Note on C53: If cable entry is specified, select the number of the incoming cable grounding conductors. If "other" is selected, specify the number in the "Additional notes" column.
Note on C54: Select whether bus duct entry is specified. If "required" is selected, specify the details of the bus duct (ampacity, size, dimensions, number of bus bars, etc.) in the "Additional notes" column. Default value : not required
Note on C55: Select the incoming cable or bus entry location.
Note on C57: Select the outgoing cable or bus entry location.
Note on C58: Select the circuit breaker mechanism charging voltage. If "other" is selected, specify the voltage in the "Additional notes" column. Default value : 125 V dc
Note on C59: Select the circuit breaker trip coil voltage. If "other" is selected, specify the voltage in the "Additional notes" column. Default value : 125 V dc
Note on C60: Select the requirement to provide dual trip coils for each circuit breaker. If trip coil voltages differ, specify in the "Additional notes" column. If "breaker dependent" is selected, see project drawings for locations. Default value : not required
Note on C61: Select the circuit breaker close coil voltage. If "other" is selected, specify the voltage in the "Additional notes" column. Default value : 125 V dc
Note on C62: Select the control power source. The voltage level for the internal control power transformer (CPT) should be 120 V ac nominal. Default value : external
Note on C63: Select the requirements for the indicator lights. Additional status indicator lights can be specified on the project drawings or in the "Additional notes"' column, but this will reduce standardization. Default value : open-closed
Note on C64: Select whether circuit breaker trip coil monitoring on the door (device panel) is required. If monitoring is required, select whether protective relay (IEEE Dev. 94) or indicating light is to be provided. Default value : not required
Note on C65: Select whether a circuit breaker control switch (IEEE Dev. 52CS) is required on the compartment door (device panel) for each power circuit breaker. Default value : required
Note on C66: Select whether a physical lockout relay is required for circuit breaker control (IEEE Dev. 86). Devices to be installed for each individual power circuit breaker as indicated on the project drawings. Default value : not required
Note on C67: Select the requirement to install an emergency stop pushbutton on the door (instrument compartment) of each circuit breaker. See project drawings for locations if "breaker dependent" is selected. Default value : not required
Note on C68: Select the requirement to install surge arresters(s) on the load termination in the cable compartment of each circuit breaker. If "breaker dependent" is selected, see project drawings for locations. Default value : not required
Note on C69: Select the requirement to install surge capacitor(s) on the load termination in the cable compartment of each circuit breaker. If "breaker dependent" is selected, see project drawings for locations. Default value : not required
Note on C71: If incoming metering is required, select the required type. If analog metering is selected, voltmeter and ammeter switches will be provided. Use the "Additional notes" column to specify any specialty metering functions (e.g. PF, KW, KWH, harmonics). Default value : not required
Note on C72: Select whether panel-mounted metering for the feeder circuits is required. Specify details for type and quantity for feeder meeting in the "Additional notes" column. Default value : not required
Note on C73: Select whether test switches (FT1 type) are required for testing and calibration functions associated with metering and protective functions. Use the "Additional notes" column to specify which circuit functions will be rerouted through the test switch. Default value : not required
Note on C74: Select whether an arc flash detection system is required for MV compartments in the MC switchgear assembly. This may require additional software, hardware and control wiring to be provided. Default value : not required
Note on C75: Select whether a circuit breaker transfer scheme is required. The specific details are shown in the project drawings and functional description documents. Specify the reference documents in the "Additional notes" column. Default value : not required
Note on C76: Select whether a circuit breaker interlocking scheme is required. The specific details are shown in the project drawings and functional description documents. Use the "Additional notes" column to specify the reference documents. Default value : not required
Note on C77: Provisions for remote monitoring and control are available with protective relay multifunction meters that are equipped with communication capability. If required, select whether monitoring only or both monitoring and control are required. Default value : not required
Note on C78: Select the communication media. Depending on the selection, additional information regarding the physical layer may be required. If "multiple" or "other" is selected, specify in the "Additional notes" column and in the project drawings.
Note on C79: Select the network redundancy option. Depending on the selection, additional information regarding the physical layer may be required. If "multiple" or "other" is selected, specify in the "Additional notes" column and in the project drawings.
Note on C80: Select the communication protocol. Depending on the selection, additional information regarding the physical layer may be required. If "multiple" or "other" is selected, specify in the "Additional notes" column and in the project drawings.
Note on C81: Select the level of desired redundancy, including auxiliary power to the data switches and other miscellaneous communication equipment. If "external" is selected, it is to be supplied by others. Refer to project drawings for additional details.
Note on C83: Select whether a continuous thermal monitoring system is required. This may require additional hardware, software and control wiring to be installed. Default value : not required
Note on C84: Select whether a thermal monitoring analytical software is required. This includes any non-standard interface cables but excludes any computer hardware. Default value : not required
Note on C85: Select the requirement for thermal scanning inspection windows. Manufacturer to confirm the recommended locations. Default value : not required
Note on C86: Select whether a continuous partial discharge monitoring system is required. This may require additional hardware, software and control wiring to be installed. Use the "Additional notes" column to specify details for the system. Default value : not required
Note on C87: Select whether a motor condition monitoring system is required. This may require additional hardware, software and control wiring to be installed. If specific motors are to be monitored, refer to the detailed project drawings. Default value : not required
Note on C88: Select the number of portable lifting trucks. If "other" is selected, use the "Additional notes" column to specify the number. Default value : 1
Note on C89: Select the requirement for ventilation filters. Default value : not required
Note on C90: Select whether individual software packages for configuration, diagnostics, controls, protection and CBM data analytics are required. Provide specific requirements in the "Additional notes" column. This includes non-standard interface cables. Default value : not required
Note on C91: Select the number of remote handheld control stations needed to operate the MV circuit breakers. If "other" is selected, specify in the "Additional notes" column. Default value : not required
Note on C92: Select whether a motorized remote racking device is needed to insert or withdraw the MV circuit breakers. The "integral" selection is a factory-integrated system as part of the stationary mechanism. Default value : not required
Note on C93: Select whether a circuit breaker test cabinet for operating the circuit breaker outside of the assembly is required. Default value : not required
Note on C94: Select whether a ground and test device is necessary for the assembly. Specify in the "Additional notes" column the quantity, frame size, 3- or 6-pole and electrically or manually operated for each of the units required. Default value : not required
Note on C95: The grounding (earthing) switch provides a factory-integrated means to safely ground the load side terminals of the circuit breaker after the isolation switch is opened. If fault close rating is selected, provide details in the "Additional notes" column. Default value : not required
Note on C97: Select the equipment preservation requirement. Manufacturer's standard packaging is appropriate for domestic shipping (not offshore) and indoor storage. If "special" is selected, specify in the "Additional notes" column or "Supplement"' tab. Default value : manufacturer's standard
Note on C98: Select whether provisions for energizing the space heater for storage are required. If required, the preservation packaging allows for access to the space heater connections without compromising the preservation integrity. Default value : not required
Note on C99: Select the requirements for desiccant bags for shipping. Default value : every compartment
Note on C100: Select the requirements for impact sensors installed for shipping. If "other" is selected, specify additional instructions in the "Additional notes" column. Default value : not required

## Supplement
Row |  | IOGP S-743D (1.0) Procurement Data Sheet for Metal-Clad Switchgear (IEEE) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-743D (1.0) Procurement Data Sheet for
Metal-Clad Switchgear (IEEE)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-743 Supplementary Specification to IEEE Std C37.20.2 for Metal-Clad Switchgear.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data