## Front & Preliminaries
|  |  |  | SPECIFICATION | January 2025
|  |  |  | IOGP S-719D | Version 2.0
Procurement Data Sheet for
Water Mist Fire Protection Systems
(NFPA)
Revision history
| VERSION | DATE | PURPOSE
| 2 | January 2025 | Second Edition
| 1 | May 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-719D (2.0) Procurement Data Sheet for
Water Mist Fire Protection Systems (NFPA)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
This second edition cancels and replaces the first edition published in May 2020. Due to technical writing requirements leading to extensive changes, this second edition should be treated as a new document.
IOGP S-719D (2.0) Procurement Data Sheet for
Water Mist Fire Protection Systems (NFPA)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of water mist fire protection systems in accordance with IOGP S-719 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-719), information requirements specification (IOGP S-719L) and quality requirements specification (IOGP S-719Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)

## Procurement Data Sheet
Row | IOGP S-719D (2.0) Procurement Data Sheet for Water Mist Fire Protection Systems (NFPA) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Project country : | input data |  | input data
9 |  | Project region : | input data |  | input data
10 |  | Order status : | select |  | select | [5 empty] | select | for enquiry | for purchase
11 |  | Manufacturer : | input data |  | input data
12 |  | Safety integrity level (SIL) capability for assembly : | select |  | select | [5 empty] | select | SIL 1 | SIL 2 | SIL 3 | not applicable
13 |  | Site conditions
14 | 4.1.1.2,4.1.1.3, 17.4 | Limitations of use : | select |  | select | [5 empty] | select | contains water reactive materials | does not contain water reactive materials
15 | 8.5.6.6.2 | Location environment : | select |  | select | [5 empty] | select | indoor | onshore - coastal | onshore - desert | onshore - inland | offshore - fixed | offshore - floating | marine - ship | other
16 |  | Altitude : | 1000 m (3281 ft) or below |  | 1000 m (3281 ft) or below | [5 empty] | select | 1000 m (3281 ft) or below | other
17 | 6.10.3.4 | Maximum ambient air temperature : | select |  | select | [5 empty] | select | 40°C (104°F) | 45°C (113°F) | 50°C (122°F) | 54°C (129°F) | other
18 | 6.10.3.4 | Minimum ambient air temperature : | select |  | select | [5 empty] | select | 4°C (40°F) | 0°C (32°F) | -15°C (5°F) | -20°C (-4°F) | below -20°C (-4°F) | other
19 |  | Maximum relative humidity : | select | % | select | % |  |  |  |  | select | 100 | 95 | 90 | other | not applicable
20 |  | Transport and storage conditions : | within normal service conditions |  | within normal service conditions | [5 empty] | select | within normal service conditions | outside normal service conditions
21 |  | Extended periods of standstill : | no |  | no | [5 empty] | select | yes | no
22 | 12.5.1.1,12.5.1.2 | Water quality : | input data |  | input data
23 |  | Degree of ingress protection : | select |  | select | [5 empty] | select | IP23 | IP44 | IP54 | IP55 | IP56 | NEMA 3 | NEMA 3s | NEMA 4 | NEMA 4x | NEMA 5
24 |  | Protected spaces and objects
25 | 5.2.2,7.2,7.5, 18.4.4 | Water mist system type : | select |  | select | [5 empty] | select | deluge | wet pipe | preaction | dry pipe
26 | 4.1.1.1,7.2, 18.4.4 | Water mist performance objective : | select |  | select | [5 empty] | select | fire extinguishment | fire suppression | fire control | temperature control | exposure protection
27 | 7.2, 18.4.4 | Water mist system application type : | select |  | select | [5 empty] | select | local-application | total compartment application | zoned application | occupancy protection
28 | 5.2.2 | Water mist system protection sizing category : | select |  | select | [5 empty] | select | object | area | volume
29 | 6.6.1 | Sizing of protected object, area or volume : | input data | select | input data | select |  |  |  |  | select | m² | ft² | m³ | ft³
30 | 8.2.2 | Maximum height of protected object, area or volume : | input data | select | input data | select |  |  |  |  | select | m | ft
31 |  | Additional fire protection : | input data |  | input data
32 |  | Storage within or adjacent to protected space or object : | input data |  | input data
33 | 6.10.1.1 | Detection method for water mist system activation : | select |  | select | [5 empty] | select | heat detection | flame detection | smoke detection | manual activation | other
34 | 6.6.6.1 | Nozzle protection : | not required |  | not required | [5 empty] | select | frangible discs | blowoff caps | not required
35 |  | System approval/acceptance
36 | 5.2.2,5.1.1,5.1.2,5.1.3,6.1.1.1,6.6.1,7.2,7.2.4.2,9.1.5,16.1.2.1,16.1.2.2,17.1.1,17.2.1,18.2.1,18.2.2,18.2.3,18.4.1,18.6.1,18.6.2 | Water mist system approval type : | listed solution |  | listed solution | [5 empty] | select | listed solution | fire scenario-engineered solution
37 | 9.1.5,17.1.3,17.2.1,18.2.1,18.2.3,18.2.4,18.3,18.4.1,18.4.3 | Additional fire testing for fire scenario-engineered solution : | select |  | select | [5 empty] | select | required | not required | not applicable
38 | 16.2.11.3,17.1.3,17.2.1,18.2.1,18.3 | Authority having jurisdiction (AHJ) : | input data |  | input data
39 | 6.1.1.1,16.1.2.1,16.1.2.2,6.6.1,7.2.4.2 | System approval - body/organization : | input data |  | input data
40 |  | System approval - professional engineer (PE) : | not required |  | not required | [5 empty] | select | not required | required | not applicable
41 | 8.1.2,9.1.3,9.2.6.1,13.2.3,18.2.2,18.2.3 | System design responsibility : | input data |  | input data
42 | 8.1.5 | System installation responsibility : | input data |  | input data
43 | 14.1.6 | System commissioning responsibility : | input data |  | input data
44 |  | Pre-engineered systems for rotating equipment
45 | 12.3.1 | Rundown time of rotating equipment : | not applicable | minutes | not applicable | minutes
46 | 12.3.1 | Time to secure fuel lines to rotating equipment : | not applicable | minutes | not applicable | minutes
47 |  | Hazardous area information
48 | 8.5.4 | Blast protection : | select |  | select | [5 empty] | select | required | not required
49 | 6.2.2.1,6.5.7.1,8.3.7 | Seismic consideration : | select |  | select | [5 empty] | select | required | not required
50 | 6.1.3.1,6.6.4,6.6.5,8.1.3,8.5.4 | Chemicals and corrosives : | select |  | select | [5 empty] | select | applicable | not applicable
51 |  | Hazardous area certification standard : | select |  | select | [5 empty] | select | IEC 60079 (all parts) | NFPA 70 Article 500 | NFPA 70 Article 505 | not applicable
52 |  | Explosion hazard classification - IEC 60079 (all parts) or NFPA 70, Article 505 : | not applicable |  | not applicable | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | not applicable
53 |  | Explosion group - IEC 60079 (all parts) or NFPA 70, Article 505 : | not applicable |  | not applicable | [5 empty] | select | IIA | IIB | IIC | not applicable
54 |  | Explosion group - NFPA 70, Article 500 : | not applicable |  | not applicable | [5 empty] | select | Class I Group A | Class I Group B | Class I Group C | Class I Group D | not applicable
55 |  | Temperature class - IEC 60079-0 or NFPA 70, Article 505 : | not applicable |  | not applicable | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6 | not applicable
56 |  | Temperature class - NFPA 70, Article 500 : | not applicable |  | not applicable | [5 empty] | select | T1 | T2 | T2A | T2B | T2C | T2D | T3 | T3A | T3B | T3C | T4 | T4A | T5 | T6 | not applicable
57 |  | Explosion hazard classification - NFPA 70, Article 500 : | not applicable |  | not applicable | [5 empty] | select | non-hazardous | division 2 | division 1 | not applicable
58 |  | Compliant standards
59 | 6.5.2,8.3.2,8.3.6.2,8.3.7,8.4.2,16.2.15 | Compliance with NFPA 13 - installation of sprinkler systems : | select |  | select | [5 empty] | select | NFPA 13 | alternative international standard | not applicable
60 | 10.1.2.3,10.1.2.4 | Compliance with NFPA 14 - installation of standpipe and hose systems : | select |  | select | [5 empty] | select | NFPA 14 | alternative international standard | not applicable
61 | 10.3.1.9.2,6.9.1.2,6.9.1.7,6.9.2.1,6.9.3.1,8.8.3.1.9 | Compliance with NFPA 20 - installation of stationary pumps for fire protection : | select |  | select | [5 empty] | select | NFPA 20 | alternative international standard | not applicable
62 | 10.3.1.9.1,12.5.3.1 | Compliance with NFPA 22 - water tanks for private fire protection : | select |  | select | [5 empty] | select | NFPA 22 | alternative international standard | not applicable
63 | 15.1.1,8.6.5 | Compliance with NFPA 25 - inspection, testing, and maintenance of water-based fire protection systems : | select |  | select | [5 empty] | select | NFPA 25 | alternative international standard | not applicable
64 | 4.2.1.1,6.10.1.1,6.9.2.1,8.9.1.1,8.9.2.1 | Compliance with NFPA 70 - electrical code : | select |  | select | [5 empty] | select | NFPA 70 | alternative international standard | not applicable
65 | 6.10.1.1,6.10.2.1,6.10.4.1,8.9.1.2,8.9.1.3,8.9.2.1,8.9.2.2,8.9.3.1,10.3.2.3.2,10.3.2.5.6,14.2.4.2.5 | Compliance with NFPA 72 - fire alarm and signaling code : | select |  | select | [5 empty] | select | NFPA 72 | alternative international standard | not applicable
66 | 13.1.6 | Compliance with NFPA 170 - fire safety and emergency symbols : | select |  | select | [5 empty] | select | NFPA 170 | alternative international standard | not applicable
67 | 10.3.2.8.1.4 | Compliance with NFPA 220 - types of building construction : | select |  | select | [5 empty] | select | NFPA 220 | alternative international standard | not applicable
68 | 6.3.4.2,6.3.4.3,6.3.6.1,8.3.2,14.2.2.3.1 | Compliance with ASME B31.1 or BS EN 13480-3 - piping : | select |  | select | [5 empty] | select | ASME B31.1 | BS EN-13480-3 | alternative international standard | not applicable
69 | 6.2.2.2,6.4.3.5,8.5.6.1 | Compliance with ASME Boiler and Pressure Vessel Code, Section VIII or U.S. Department of Transportation, 49 CFR, 171-190, 178.36-178.37, or another approved international standard : | select |  | select | [5 empty] | select | ASME Boiler and Pressure Vessel Code Section VIII | U.S. DOT 49 CFR 171-190 and 178.36-178.37 | alternative international standard | not applicable
70 | 6.4.2.7,6.4.3.3 | Compliance with ANSI/ASME B1.20.1 - pipe threads : | select |  | select | [5 empty] | select | ANSI/ASME B1.20.1 | alternative international standard | not applicable
71 | 6.10.1.1,14.2.4.2.5 | Compliance with CAN/ULC S524-14 - installation of fire alarm systems (in Canada) : | select |  | select | [5 empty] | select | CAN/ULC S524-14 | alternative international standard | not applicable
72 | 6.10.1.1,14.2.4.2.5 | Compliance with CAN/ULC S529-16 - smoke detectors for fire alarm systems (in Canada) : | select |  | select | [5 empty] | select | CAN/ULC S524-16 | alternative international standard | not applicable
73 | 16.1.8 | Compliance with USCG NVIC 9-97, CH-1 - structural fire protection : | select |  | select | [5 empty] | select | USCG NVIC 9-97, CH-1 | alternative international standard | not applicable
74 |  | Ventilation and interlocks
75 | 6.10.3.7,9.1.4,9.2.3.2,9.4.1,9.4.1.2,9.4.1.2.2.1,9.4.1.2.2.2,10.3.2.8.1.4,17.3.1.1,17.3.1.2 | Ventilation : | input data |  | input data
76 | 9.4.1.2.1.1,9.4.1.2.1.2,17.3.1.1,17.3.1.2 | Natural ventilation : | input data |  | input data
77 | 17.3.1.1,17.3.1.2 | Forced ventilation : | input data |  | input data
78 | 13.1.5,13.42,A.16.5 | Interlocks : | input data |  | input data
79 |  | Designed system solution
80 | 6.2.1,6.9.1.1 | Water mist system supply type : | select |  | select | [5 empty] | select | cylinder based | electric pump | diesel pump | gas driven pump (pneumatic)
81 | 7.5 | System pressure type : | select |  | select | [5 empty] | select | low pressure | intermediate pressure | high pressure
82 | 6.1,7.5,8.8.4.4,11.1.1,11.4.1.1,12.1.3,12 | System fluid type : | single fluid |  | single fluid | [5 empty] | select | single fluid | twin fluid
83 | 8.6.1 | System flow rate : | input data | select | input data | select |  |  |  |  | select | L/min | gpm
84 | 10.3.1.10.2,16.2.11.2,16.2.11.4,16.2.11.5,9.1.4 | Maximum number of nozzles at designed system flow rate : | input data |  | input data
85 | 6.1.2.1,6.2.2.4,8.5.6.2 | Maximum system design pressure at nozzle : | input data | select | input data | select |  |  |  |  | select | bar | psi
86 | 6.1.2.1,6.2.2.4,8.5.6.2 | Minimum system design pressure at nozzle : | input data |  | input data
87 | 6.1.2.1,6.2.2.4,8.5.6.2 | System pressure at pump or cylinder : | input data | select | input data | select |  |  |  |  | select | bar | psi
88 |  | System weight - dry : | input data | select | input data | select |  |  |  |  | select | kg | lb
89 | 6.2.2.8.1 | System weight - filled : | input data | select | input data | select |  |  |  |  | select | kg | lb
90 | 6.10.3.4,6.2.2.4 | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
91 | 6.10.3.4,6.2.2.4 | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
92 | 10.1.2.1.1,12.3.1 | Discharge duration : | input data | minutes | input data | minutes
93 |  | Pump system
94 | 16.1.6,17.2.2.1,17.2.2.2 | Pump system redundancy : | select |  | select | [5 empty] | select | N+1 | 0 | 1 | 2 | other
95 |  | Cylinder system
96 |  | Cylinder system propellant : | select |  | select | [5 empty] | select | nitrogen | air | other
97 | 6.2.2.2,8.5.5.1 | Pressurized gas and water containers approval standard : | select |  | select | [5 empty] | select | ASME Boiler and Pressure Vessel Code Section VIII | U.S. Department of Transportation, 49 CFR 171–190, 178.36–178.37 | ISO 9809 | other
98 | 6.2.2.2,8.5.5.1 | Pressurized gas and water containers volume : | input data | select | input data | select |  |  |  |  | select | L | gal
99 | 6.2.2.3 | Shipping containers approval standard : | select |  | select | [5 empty] | select | U.S. Department of Transportation | Transport Canada | other
100 | 6.2.2.3 | Shipping container size : | input data | select | input data | select |  |  |  |  | select | L | gal
101 |  | Cylinder system redundancy : | select |  | select | [5 empty] | select | 0 | 2 | 1 | other
102 |  | Electrical operating conditions
103 |  | Low-voltage motors for pump system : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-703 | IOGP S-733D | not applicable
104 |  | Motor power supply AC voltage - electric pump system : | select | V | select | V |  |  |  |  | select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | other
105 |  | Motor power supply frequency - electric pump system : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
106 |  | Motor starting method - electric pump system : | direct-on-line |  | direct-on-line | [5 empty] | select | direct-on-line | star delta | VSD
107 |  | Rated motor in-rush current - electric pump system : | input data | A | input data | A
108 |  | Rated motor power - electric pump system : | input data | select | input data | select |  |  |  |  | select | kW | HP
109 |  | Electrical requirement running - diesel pump system : | input data |  | input data
110 |  | DC power supply voltage - cylinder system : | input data | V | input data | V
111 |  | Maximum DC current demand - cylinder system : | input data | A | input data | A
112 |  | Water supply
113 | 10.3.1.9.1 | Water supply tank size : | input data | select | input data | select |  |  |  |  | select | L | gal
114 | 12.4.1 | Additional connections to water supply : | input data |  | input data
115 | 12.3.1 | Water supply tank spray time : | input data | minutes | input data | minutes
116 | 12.5.1.1,12.5.1.7 | Water type of primary water supply : | potable |  | potable | [5 empty] | select | potable | seawater | demineralized | filtered | desalinated
117 | 12.5.1.1 | Water type of backup water supply : | select |  | select | [5 empty] | select | potable | seawater | demineralized | filtered | none | other
118 | 6.2.2.6.1,6.7.2,7.6,12.2 | Water additives : | none |  | none | [5 empty] | select | enhanced fire performance | microbiologic growth inhibitors | corrosion inhibitors | freeze protection | not applicable | none
119 | 6.10.3.4 | Water supply freezing protection : | input data |  | input data
120 |  | Section control valves
121 | 7.4.1.1,8.8.1.8.2,8.8.2.1,8.8.2.2 | Section control valve : | select |  | select | [5 empty] | select | normally open (NO) - hydraulic - wet pipe system | normally closed (NC) - electrical - dry pipe system
122 |  | Instrumentation
123 | 6.2.2.9 | Pressure gauge : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-718 | not applicable
124 |  | Pressure switch : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other | not applicable
125 |  | Pressure transmitter : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-718 | not applicable
126 |  | Flow indicator : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-718 | not applicable
127 |  | Water level indicator : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-718 | not applicable
128 |  | Valve position indicator : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-718 | not applicable
129 |  | Fire-fighting skid
130 | 8.1.3,8.1.4,8.3.7,8.5.4,12.5.4.3 | Enclosed fire-fighting skid : | select |  | select | [5 empty] | select | required | not required
131 | 8.5.4 | Fire-fighting skid enclosure type : | input data |  | input data
132 |  | Fire-fighting skid enclosure material : | select |  | select | [5 empty] | select | carbon steel | AISI 316L | other | not required
133 |  | Fire-fighting skid welding : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-705 | other
134 |  | Painting : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-715 | other
135 | 6.10.3.4,8.5.6.6.2,17.3.2.2 | Enclosure heating or cooling : | select |  | select | [5 empty] | select | heating | cooling - forced | cooling - naturally | not applicable
136 | 17.3.2.3 | Emergency lighting within enclosure : | required |  | required | [5 empty] | select | required | not required
137 |  | Water fill device : | select |  | select | [5 empty] | select | required | not required
138 | 6.10.3.5.1 | Emergency release device for enclosure : | select |  | select | [5 empty] | select | required - inside | required - outside | required - inside and outside | not required
139 | 16.1.7.1 | Manual pump start : | select |  | select | [5 empty] | select | required - control room | required - other location | not required
140 |  | Fire-fighting skid drain : | select |  | select | [5 empty] | select | required | not required
141 |  | Tubing and fittings
142 | 16.1.3.2 | Tubing and fittings : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-716
143 | 16.1.3.2,6.3.1.1 | Tubing and fitting material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | IOGP S-716
144 | 6.3.5.1,6.3.5.2 | Tubing and fittings manufacturer and type : | input data |  | input data
145 |  | Tubing and fittings measurement system : | metric |  | metric | [5 empty] | select | metric | U.S. customary
146 | 6.4.2.7 | Tubing and fittings thread sizes : | input data | select | input data | select |  |  |  |  | select | mm | in.
147 |  | Water mist system acceptance
148 | 11.4.1.3.2,14.2.6.1,14.2.6.2,14.2.6.3 | Full discharge test : | select |  | select | [5 empty] | select | factory acceptance test | site acceptance test | not applicable
149 | 14.2.6.2 | Test connection point : | not required |  | not required | [5 empty] | select | required | not required
150 |  | Nozzle details
151 | 7.3 | Nozzle type : | select |  | select | [5 empty] | select | automatic (heat responsive element) | nonautomatic (open) | multifunctional
152 | 6.6.1 | Nozzle identification : | input data |  | input data
153 | 6.6.1 | Nozzle operating pressure : | input data | select | input data | select |  |  |  |  | select | bar | psi
154 | 6.6.1 | Nozzle k-factor : | input data | k | input data | k
155 | 6.6.1 | Nozzle flow rate at operating pressure : | input data | select | input data | select |  |  |  |  | select | L/min | gpm
156 | 6.6 | Nozzle materials : | input data |  | input data
157 | 6.6.1,8.1.6.1,8.1.6.1.1,8.2.2 | Maximum installation height for nozzle : | input data | select | input data | select |  |  |  |  | select | m | ft
158 | 6.6.1,8.1.6.1,8.1.6.1.1,8.2.6 | Maximum installation distance below ceiling for nozzle : | input data | select | input data | select |  |  |  |  | select | m | ft
159 | 6.6.1,8.1.6.1,8.1.6.1.1,8.2.6 | Minimum installation distance below ceiling for nozzle : | input data | select | input data | select |  |  |  |  | select | m | ft
160 | 6.6.1,8.1.6.1,8.1.6.1.1,8.2.3 | Maximum installation spacing between nozzles : | input data | select | input data | select |  |  |  |  | select | m | ft
161 | 6.6.1,8.1.6.1,8.1.6.1.1,8.2.4 | Maximum nozzle installation distance to wall : | input data | select | input data | select |  |  |  |  | select | m | ft
162 | 8.1.6.1,8.1.6.1.1,8.2.2 | Maximum nozzle installation distance above hazard : | input data | select | input data | select |  |  |  |  | select | m | ft
163 | 6.6.1,8.1.6.1,8.1.6.1.1 | Minimum nozzle installation distance above hazard : | input data | select | input data | select |  |  |  |  | select | m | ft
164 | 6.6.1,8.1.6.1,8.1.6.1.1,8.2.5 | Minimum nozzle installation distance from obstruction : | input data | select | input data | select |  |  |  |  | select | m | ft
165 | 6.6.1,8.1.6.1,8.1.6.1.1 | Nozzle installation orientation : | select |  | select | [5 empty] | select | vertical | horizontal | angled
Note on C4: Specify the unique tag number for the water mist fire protection system based on the PID.
Note on C5: Specify the functional description of the equipment.
Note on C7: Select the CAS level to be applied in IOGP S-719Q, Annex A. CAS D requires the fewest quality interventions and information requirements. Default value : D
Note on C8: Specify the country in which the project is located, in accordance with ISO 3166-1.
Note on C9: Specify the geographic location, within the country, which will determine the applicability of local regulatory requirements.
Note on C10: Select the status of the order.
Note on C11: Specify the name of the water mist system manufacturer.
Note on C12: When the safety integrity level (SIL) is required, select the relevant SIL level required. When instrumentation not used in a safety loop, select "not applicable".
Note on C14: Specify whether the protected items/spaces include materials or applications as listed in sections 4.1.1.2 and 4.1.1.3.
Note on C15: Select the location where the water mist system is to be situated. If "other" is selected, specify in the "Additional notes" column.
Note on C16: This is the altitude above sea level. Section A.4.2.1.1 refers to 1000 m (3281 ft) for electrical clearance. Select "other" and specify the value in "Additional notes" only if the site altitude is higher than 1 000 m (3281 ft). Default value : 1000 m (3281 ft) or below
Note on C17: Select the maximum ambient air temperature that the water mist system can encounter. Temperatures outside of 4°C to 54°C (40°F to 130°F) may require additional design considerations.
Note on C18: Select the minimum ambient air temperature that the water mist system can encounter. Temperatures outside of 4°C to 54°C (40°F to 130°F) may require additional design considerations.
Note on C19: Select the maximum relative humidity at the maximum ambient air temperature in the area where the water mist system will be installed. If "other" is selected, specify the value in "Additional notes" column. Specify "not applicable" if it does not apply.
Note on C20: Select whether the transportation and storage conditions are outside with those detailed as site conditions. Specify the measures in the "Additional notes" column to ensure that they do not affect the integrity of the system. Default value : within normal service conditions
Note on C21: Select whether the water mist system is to be subject to standstill, storage or transport that exceed 6 months. Default value : no
Note on C22: Specify for the water mist system, the water quality available at final installation site.
Note on C23: Select the ingress protection value of the water mist system/components in accordance with IEC 60034-5.
Note on C25: Select the water mist system type. When there are more than one type on the project, specify the additional types in the "Additional notes" column.
Note on C26: Select the performance objective of the water mist system. The type approved for a specific application is to prevail over this point.
Note on C27: Select the system application as defined in Chapter 7.
Note on C28: Select the protection sizing category that is to be protected by water mist system.
Note on C29: Specify the dimensions of what is to be protected by the water mist system. For protected items and volumes, specify the length, width and height. For protected areas, specify the length and width.
Note on C30: Specify the maximum height of the protected object or space.
Note on C31: Specify whether an active fire suppression system provides additional protection (e.g. sprinklers, fixed gas extinguisher system).
Note on C32: Specify whether the protected space or object has storage within or adjacent to it including details of the materials and any packaging of the stored items along with the size of the room and other contents. If none, specify "No storage".
Note on C33: Select the method of detection used to activate the system. If there are multiple or alternative methods, specify in the "Additional notes" column.
Note on C34: Select whether frangible discs or blowoff caps are required to prevent clogging by external, foreign materials as defined in section 6.6.6. Typically, these would not be required in the oil and gas industry, therefore the default is not required. Default value : not required
Note on C36: Select the type of water mist system that is offered. Default value : listed solution
Note on C37: For fire scenario-engineered solutions, select whether further fire testing may be required and specify details in the "Additional notes" column.
Note on C38: Specify the AHJ for the approval of the water mist system.
Note on C39: For listed systems, specify the approval body or organization (e.g. IMO, FM approvals, UL, VDS). For fire scenario-engineered solution, specify the third party and the fire test laboratory.
Note on C40: Select whether a PE is required for system approval. This may be required in certain countries only. If it does not apply, select "not applicable". Default value : not required
Note on C41: Specify who is responsible for the design of the water mist system. This can be the water mist manufacture or a local distributor.
Note on C42: Specify who is responsible for the installation of the water mist system. This can be the water mist manufacture or a local distributor.
Note on C43: Specify who is responsible for the commissioning of the water mist system. This can be the water mist manufacture or a local distributor.
Note on C45: Specify the rundown time of the rotating equipment. Where rotating equipment is not included, specify "not applicable". Default value : not applicable
Note on C46: Specify the time necessary to secure the fuel lines to the rotating equipment. Where rotating equipment is not included, specify "not applicable". Default value : not applicable
Note on C48: Specify whether any part of the fire-fighting system is subject to blast protection requirements. Specify the blast withstand parameters (e.g. as severity, over pressure, duration and rating) in the "Additional notes" column.
Note on C49: Specify whether geographical location is subject to seismic activity. Specify the severity and rating in the "Additional notes" column.
Note on C50: Specify the chemicals and corrosives that may be present in the location environment (e.g. H2S). Specify the elements in the "Additional notes" column.
Note on C51: Select the certification type required for the end user location. Select which certification is acceptable for motors to be located in a hazardous area. If "other" is selected, specify the certification in the "Additional notes" column.
Note on C52: Select the area classification from the hazardous area classification drawing for the location where the water mist system water delivery system is to be installed. This is not the protected area. Default value : not applicable
Note on C53: Select the explosion group classification of the physical object in accordance with IEC 60079 (all parts) or NFPA 70, Article 505. Default value : not applicable
Note on C54: Select, for purposes of testing, approval, and area classification, various air mixtures (not oxygen-enriched) grouped in accordance with NFPA 70, Article 500.6(A) and (B). Default value : not applicable
Note on C55: Select the temperature class for which the motor is rated for in accordance with IEC 60079-0 or NFPA 70, Article 505. Default value : not applicable
Note on C56: Select the temperature classification of the physical object in accordance with NFPA 70, Article 500. Default value : not applicable
Note on C57: Select the area classification from the hazardous area classification drawing for the location where the water mist system water delivery system is to be installed. This is not the protected area. Default value : not applicable
Note on C59: Select whether sprinkler systems are to comply with NFPA 13 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C60: Select whether standpipe and hose systems are to comply with NFPA 14 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C61: Select whether stationary pumps are to comply with NFPA 20 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C62: Select whether water tanks are to comply with NFPA 22 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C63: Select whether inspection, testing and maintenance are to comply with NFPA 25 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C64: Select whether the electrical code is to comply with NFPA 70 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C65: Select whether alarm and signaling are to comply with NFPA 72 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C66: Select whether safety and emergency symbols are to comply with NFPA 170 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C67: Select whether building construction is to comply with NFPA 220 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C68: Select whether piping code is to comply with ASME B31.1, BS EN 13480-3 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C69: Select whether gas and water containers are to comply with section 6.2.2.2 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C70: Select whether pipe threads are to comply with ANSI/ASME B1.20.1 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C71: Select whether installation of alarm systems is to comply with 6.10.1.1 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C72: Select whether smoke detectors are to comply with CAN/ULC S529-16 or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C73: Select whether structural fire protection is to comply with section 16.1.8, C or, when permitted by the AHJ, with an alternative international standard. If “alternative international standard” is selected, specify details in the “Additional notes” column.
Note on C75: Specify the details of ventilation systems, including smoke ventilation, that are present in water mist protected rooms or compartments. Where ventilation is not included, specify "not applicable".
Note on C76: Specify details of doors, windows, shutters and other openings. Specify details about the manual and automatic controls to open and close these openings in the "Additional notes". Where natural ventilation is not included, specify "not applicable".
Note on C77: Specify details of forced ventilation and controls upon their use. Where forced ventilation is not included, specify "not applicable".
Note on C78: Specify details of interlocks for the protected object, area or volume that can impact the ability for the water mist system to perform optimally (e.g. fuel supply, power to equipment, process fluids).
Note on C80: Select the method for delivering water mist to the protected items or spaces.
Note on C81: Select the pressure type of the water mist system as defined in sections 6.4.2 and 6.4.3.
Note on C82: Select the media type of the water mist system as defined in section 7.5. Default value : single fluid
Note on C83: Specify the system flow rate for the assumed maximum area of operation (AMAO) or the section(s) that require(s) the greatest demand.
Note on C84: Specify the maximum number of nozzles which will discharge water during operation in the event of a fire.
Note on C85: Specify the maximum design working pressure at the most remote or most demanding nozzle.
Note on C86: Specify the minimum design working pressure at the most remote or most demanding nozzle.
Note on C87: Specify the designed operating range for the pump/cylinder system.
Note on C88: Specify the dry weight of the system (pump or cylinder system).
Note on C89: Specify the filled weight of the system (pump or cylinder system).
Note on C90: Specify the maximum design temperature for the water mist system location. If heating and cooling may need to be installed, specify so in the "Additional notes" column.
Note on C91: Specify the minimum design temperature for the water mist system location. If heating and cooling may need to be installed, specify so in the "Additional notes" column.
Note on C92: Specify the discharge duration. If the water mist system protects multiple items, specify the maximum discharge duration in the "Additional notes" column.
Note on C94: Specify the amount of pump redundancy that is required. Typically, this will be N+1 where N is the number of pumps. The number will be dependent on the system sizing and application.
Note on C96: Select the pressurized gas type to be used as a propellant in the water mist system. If "other" is selected, specify details of the propellant gas in the "Additional notes" notes.
Note on C97: Select the approved international standard system that the pressurized gas and water containers are in accordance with. If other, use the "Additional notes" column to give details.
Note on C98: Specify the volume of the pressurized gas and water containers. If the system consists of different sized containers, specify details in the "Additional notes" column.
Note on C99: Select the approved international standard system with which the shipping containers are in accordance.
Note on C100: Specify the size of the shipping container. Specify the length, width and height in the "Additional notes" column.
Note on C101: Specify the amount of cylinder redundancy that is required. There is not a typical amount of redundancy. The number will be dependent on system sizing, application and listing.
Note on C103: When applicable, select the low-voltage motor type. Select IOGP S-703 or S-733D for hazardous areas only. For cylinder- and diesel- driven systems, where electric motors are not included, select "not applicable". Default value : manufacturer's standard
Note on C104: Select the supply voltage for which the system is to be rated. For cylinder-based systems, where electric motors are not included, select "not applicable".
Note on C105: Select the supply frequency for which system is to be rated. For cylinder-based systems, where electric motors are not included, select "not applicable".
Note on C106: When applicable, select the motor starting method. Default value : direct-on-line
Note on C107: Specify the maximum electrical power (Amps) required for the water mist system (electric pump system only) for full system design (start up). For cylinder based and diesel pump systems, where electric motors are not included, specify "not applicable".
Note on C108: Specify the maximum electrical power required for the water mist system (electric pump system only) for full system design (start up). For cylinder based and diesel pump systems, where electric motors are not included, specify "not applicable".
Note on C109: Specify the electrical requirements for diesel pump system. For cylinder-based and electric pump systems, specify "not applicable".
Note on C110: Specify the electrical voltage required for the water mist system (cylinder system only) for full system actuation. Typically, this voltage is 24VDC. For electric and diesel pump systems, specify "not applicable".
Note on C111: For cylinder-based systems only, specify the electrical current demand required for the water mist system for system actuation.
Note on C113: For pumped systems only, specify the minimum effective capacity​ of the main water supply tank.
Note on C114: Specify whether there are any additional water supply connections, other than for fire protection purposes, that may draw water from the supply.
Note on C115: For pumped systems only, specify the main water tank spray time duration.
Note on C116: Select the water type of the primary water supply. Potable water is the default, as most manufacturers have moved away from demineralized water. Default value : potable
Note on C117: For pumped systems only, select the water type of the backup water supply. For marine and offshore, this could be seawater.
Note on C118: Select any additives required for the water mist system to operate. If multiple additives are required specify in the "Additional notes" column. Default value : none
Note on C119: Specify whether freezing conditions may occur and what is the mitigation to be used (e.g. lagging or heat tracing).
Note on C121: Select the type of section control valve for the water mist system. When more than one type is to be used, specify in the "additional notes" column.
Note on C123: Select whether the manufacturers standard is required or to adopt IOGP S-718. Specify the make and series of pressure gauge in the "Additional notes". Manufacturer's listed standard would need to be checked for hazardous area applications. Default value : manufacturer's standard
Note on C124: Select whether the manufacturers standard is not required. As IOGP S-718 does not apply. Specify the make and series of pressure switch in the "Additional notes". Manufacturer's listed standard would need to be checked for hazardous area applications. Default value : manufacturer's standard
Note on C125: Select whether the manufacturers standard is required or to adopt IOGP S-718. Specify the make and series of pressure transmitter in the "Additional notes". Manufacturer's listed standard would need to be checked for hazardous area applications. Default value : manufacturer's standard
Note on C126: Select whether the manufacturers standard is required or to adopt IOGP S-718. Specify the make and series of flow indicator in the "Additional notes". Manufacturer's listed standard would need to be checked for hazardous area applications. Default value : manufacturer's standard
Note on C127: Select whether the manufacturers standard is required or to adopt IOGP S-718. Specify the make and series of indicator in the "Additional notes". Manufacturer's listed standard would need to be checked for hazardous area applications. Default value : manufacturer's standard
Note on C128: Select whether the manufacturers standard is required or to adopt IOGP S-718. Specify the make and series of indictor in the "Additional notes". Manufacturer's listed standard would need to be checked for hazardous area applications. Default value : manufacturer's standard
Note on C130: Select whether the water mist system is to be protected by an enclosure. Specify the protection criteria from (e.g. severe weather conditions, mechanical, chemical or blast protection) in the “Additional notes” column.
Note on C131: Specify the type of protective enclosure for the water mist delivery system (e.g. blast protected, offshore, open, rack system, heated, vented). Applicable to pumped and cylinder-based systems.
Note on C132: When required, select the material of the protective enclosure of the water mist deliver system.
Note on C133: Select the welding process or system for items such as the enclosure for the fire-fighting skid, pump frame-set or cylinder retaining system (when required). May clarify position on welder qualification in "Additional notes". Default value : manufacturer's standard
Note on C134: Select the painting process. Use the "Additional notes" column to clarify what is painted and what is not painted. Default value : manufacturer's standard
Note on C135: When required, select the cooling or heating method for the enclosure space.
Note on C136: Select whether emergency lighting is required inside the fire-fighting skid enclosure. Default value : required
Note on C137: Select whether manual water filling (e.g. manual hand pump) is required. Typically for cylinder-based systems.
Note on C138: Select whether a manual emergency release is required on the fire-fighting skid enclosure. Typically required for cylinder-based systems.
Note on C139: Select, for offshore applications only, the location for manual pump start. NFPA 750 addresses this for onshore applications. Marine applications are addressed in 16.1.7.1.
Note on C140: Select whether a provision for drainage is required on the skid. Typically for enclosed fore fighting skids. May be hole or valve and pipework in floor. Specify in the "Additional notes" column whether any freezing drainage is to be considered.
Note on C142: Select if the tubing and fittings are to be manufacturer's standards or IOGP S-716. Specify the type in the "Additional notes" column. Default value : manufacturer's standard
Note on C143: Select if the piping and tubing material is to be manufacturer's standard or IOGP S-716. Specify the type and grade of material in the "Additional notes" column. Default value : manufacturer's standard
Note on C144: Specify the manufacturer of the tubing and fittings used in the water mist system.
Note on C145: Select the units of measure for the tubing and fittings within the water mist system. Default value : metric
Note on C146: Specify the thread sizes and type used for the tubing and fittings within the water mist system.
Note on C148: If required, select when the full discharge test is to be performed.
Note on C149: Select if a test connection for alternate test media (e.g. smoke) to prove free passage of pipe and nozzles is required. This allows for distribution piping to be checked for blockage without discharge of water into protected area. Default value : not required
Note on C151: Select the nozzle type. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C152: Specify the nozzle identity. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C153: Specify the nozzle operating pressure. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C154: Specify the nozzle k-factor. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C155: Specify the nozzle flow rate at operating pressure. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C156: Specify the material details of components within the nozzle. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C157: Specify the maximum nozzle installation height from floor. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C158: Specify the maximum nozzle distance below the ceiling for the nozzle. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C159: Specify the minimum distance below the ceiling for the nozzle. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C160: Specify the maximum spacing between nozzles. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C161: Specify the maximum nozzle installation distance to wall or bulkhead. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C162: Specify the maximum nozzle installation distance above hazard. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C163: Specify the minimum nozzle installation distance above the hazard. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C164: Specify the minimum installation distance from obstruction to the nozzle. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.
Note on C165: Specify the nozzle installation orientation along the center line of the flow path. For water mist systems that use more than one nozzle type, duplicate this section for each type of nozzle.

## Supplement
Row |  | IOGP S-719D (2.0) Procurement Data Sheet for Water Mist Fire Protection Systems (NFPA) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-719D (2.0) Procurement Data Sheet for
Water Mist Fire Protection Systems (NFPA)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-719 Supplementary Specification to NFPA 750 for Water Mist Fire Protection Systems.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data