## Addendum 1
Date of issue:
March 2025
Affected publication:
IOGP S-727D, Procurement Data Sheet for Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear (IEEE Std C37.20.1), First Edition, September 2021
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in September 2021.
List of updates
| Row | Column | Update
| 38 | All | New data sheet item "Provisions for padlocking ancillary circuits"
| 39 | All | New data sheet item "Mimic bus"
| 40 | All | New data sheet item "Enclosure design for roller installation"
| 83 * | All | Data sheet item "Provisions for remote monitoring and control" deleted
| 84 * | All | Data sheet item "Communication protocol" deleted
| 86 | All | New section "Interface with control systems"
| 87 | All | New data sheet item "IED brand"
| 88 | All | New data sheet item "Process control interface (ICSS/DCS) media"
| 89 | All | New data sheet item "Process control interface (ICSS/DCS) protocol"
| 90 | All | New data sheet item "Process control interface (ICSS/DCS) network redundancy"
| 91 | All | New data sheet item "Electrical control interface (ECMS) media"
| 92 | All | New data sheet item "Electrical control interface (ECMS) protocol"
| 93 | All | New data sheet item "Electrical control interface (ECMS) network redundancy"
| 94 | All | New data sheet item "IED remote configuration via ECMS"
| 95 | All | Data sheet item "Communication system power supply" moved from section "Metering and control" to new section "Interface with control systems"
| 104 | Description | Amended to "Ventilation opening accessories"
|  | Purchaser requirement / supplier offered value - options | Third option amended to "filter required" New option "mesh screen required" New option "filter with mesh screen required"
* Row number from Edition 1.0.

## Front & Preliminaries
[5 empty] | SPECIFICATION | March 2025
[5 empty] | IOGP S-727D | Version 1.01
ADDENDUM 1 TO FIRST EDITION (SEPTEMBER 2021)
Procurement Data Sheet for
Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear (IEEE Std C37.20.1)
Revision history
| VERSION | DATE | PURPOSE
| 1.01 | March 2025 | Addendum 1
| 1 | September 2021 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-727D (1.01) Procurement Data Sheet for
Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear
(IEEE Std C37.20.1)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-727D (1.01) Procurement Data Sheet for
Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear
(IEEE Std C37.20.1)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of metal-enclosed low-voltage power circuit breaker switchgear in accordance with IOGP S-727 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-727), information requirements specification (IOGP S-727L) and quality requirements specification (IOGP S-727Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)

## Procurement Data Sheet
Row | IOGP S-727D (1.01) Procurement Data Sheet for Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear (IEEE Std C37.20.1) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
5 |  | Site conditions
6 | 5.5.4 | Ambient air temperature - upper limit : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50
7 | 5.5.4 | Ambient air temperature - lower limit : | -5 | °C | -5 | °C |  |  |  |  | select | 0 | -5 | -20 | -30 | -40
8 | 4 b) | Altitude of installation : | ≤ 2000 | m | ≤ 2000 | m |  |  |  |  | select | ≤ 2000 | other
9 | 4 e) | Humidity limit : | < 95 | % | < 95 | % |  |  |  |  | select | < 95 | other
10 | 4.1 | Seismic design : | not required |  | not required | [5 empty] | select | not required | required
11 | 4.1 | Site location : | input data |  | input data
12 | 4.1 | Risk category : | N/A |  | N/A | [5 empty] | select | N/A | I | II | III | IV
13 | 4.1 | Component importance factor (Ip) : | N/A |  | N/A | [5 empty] | select | N/A | 1 | 1.25 | 1.5
14 | 4.1 | Site class : | N/A |  | N/A | [5 empty] | select | N/A | A | B | C | D | E | F
15 | 4.1 | Seismic certificate : | not required |  | not required | [5 empty] | select | not required | required
16 | 4 g) | Location installation : | indoors climate controlled |  | indoors climate controlled | [5 empty] | select | indoors climate controlled | indoor ventilated | outdoor
17 | 4.2 | Application/operating environment : | onshore |  | onshore | [5 empty] | select | onshore | offshore – fixed | offshore – floating | marine (ship) | other
18 | 4.2 | Environmental contamination : | none |  | none | [5 empty] | select | none | salt-laden | H₂S | salt-laden and H₂S | severe dust | other
19 | 7.1.6.2 | Certification (additional) : | not required |  | not required | [5 empty] | select | not required | USCG/ABS | other
20 | 7.1.5.7 | Arc-resistant certification : | 3rd party certified |  | 3rd party certified | [5 empty] | select | 3rd party certified | self-declared | N/A
21 |  | Electrical power system parameters
22 | 5.2, 7.4.4 | Voltage : | 480 | V | 480 | V |  |  |  |  | select | 208 | 480 | 600 | other
23 | 5.3 | Frequency : | 60 | Hz | 60 | Hz |  |  |  |  | select | 50 | 60 | other
24 | 7.1.1.1 a) | Phase/wire : | 3 phase 3-wire |  | 3 phase 3-wire | [5 empty] | select | 3 phase 3-wire | 3-phase 4-wire | 1-phase 2-wire | other
25 | 7.1.2.1, 7.1.2.2 | System grounding : | high resistance |  | high resistance | [5 empty] | select | high resistance | solid | ungrounded
26 | 5.4.5 | Available fault current (symmetrical) : | input data | kA | input data | kA
27 | 5.4.5 | System X/R ratio : | input data |  | input data
28 | 5.2.2 | System connection : | wye |  | wye | [5 empty] | select | wye | delta | other
29 |  | Enclosure construction
30 | 7.1.5.7 | Arc resistant construction : | Type 2B |  | Type 2B | [5 empty] | select | Type 2 | Type 2B | not required
31 | 7.1.5.2, 7.1.5.3, 7.1.5.4 | Arc plenum : | not required |  | not required | [5 empty] | select | not required | plenum interior exhaust | plenum exterior exhaust
32 | 7.7.1 | NEMA enclosure rating : | Type 1 |  | Type 1 | [5 empty] | select | Type 1 | Type 1 w/ gasket | Type 12 | Type 3R (non walk-in) | Type 3R and Type 12 | other
33 | 7.2.2 | Enclosure paint color : | manufacturer standard |  | manufacturer standard | [5 empty] | select | manufacturer standard | ANSI 61
34 | 7.5 | Accessibility : | rear access |  | rear access | [5 empty] | select | rear access | front access only
35 | 7.18 | Space heater : | not required |  | not required | [5 empty] | select | not required | required
36 | 7.18 | Space heater control : | N/A |  | N/A | [5 empty] | select | N/A | fixed (constant ON) | thermostat | hygrostat
37 | 7.18 | Space heater power supply : | external |  | external | [5 empty] | select | external | internal
38 | 7.15.14, 7.16.1.3, 7.16.1.4, 7.16.2.5, 7.16.2.6, 7.17.13, 7.17.14, 7.18.5.1 | Provisions for padlocking ancillary circuits : | manufacturer standard |  | manufacturer standard | [5 empty] | select | manufacturer standard | required
39 | 7.19.9 | Mimic bus : | not required |  | not required | [5 empty] | select | not required | required
40 | Annex C | Enclosure design for roller installation : | not required |  | not required | [5 empty] | select | not required | required
41 |  | Bus
42 | 5.4.3 | Horizontal bus rating : | select | A | select | A |  |  |  |  | select | 1600 | 2000 | 3000 | 3200 | 4000 | 5000 | other
43 | 5.4.5 | Short circuit current rating : | 65 | kA | 65 | kA |  |  |  |  | select | 42 | 65 | 85 | 100 | 200 | other
44 | 4.2.2, 7.1.1, 7.4 | Power bus plating material : | tin |  | tin | [5 empty] | select | tin | silver
45 | 7.4 | Insulated main horizontal bus : | not required |  | not required | [5 empty] | select | not required | required
46 | 7.1.1.1, 7.1.1.8 | Neutral bus rating : | not required |  | not required | [5 empty] | select | not required | full | half
47 | 7.1.1.1 | Neutral bus load termination point (location) : | N/A |  | N/A | [5 empty] | select | N/A | all sections | incoming section only
48 | 6.3.2.1, 7.1.2.2.6 | Ground ball studs : | not required |  | not required | [5 empty] | select | not required | incomers | select feeders | main buses | main buses and incomers
49 |  | Incoming section
50 |  | Service entrance application : | no |  | no | [5 empty] | select | no | yes
51 | 7.1.1.12 | Incoming line termination : | circuit breaker |  | circuit breaker | [5 empty] | select | circuit breaker | main lugs only | fusible disconnect | bus connection
52 | 7.1.1.3.2, 7.1.1.3.5, 7.12 | Cable entry : | required |  | required | [5 empty] | select | not required | required
53 | 7.1.1.3.4, 7.1.1.3.5, 7.12 | Conductor size : | input data | AWG | input data | AWG
54 | 7.1.1.3.5 | Conductor material : | select |  | select | [5 empty] | select | copper | aluminum
55 | 7.1.1.3.4, 7.1.1.3.5, 7.12 | Number of conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
56 | 7.1.1.3.4, 7.1.1.3.5, 7.12 | Incoming cable grounding conductor size : | input data | AWG | input data | AWG
57 | 7.1.1.3.4, 7.1.1.3.5, 7.12 | Number of incoming cable grounding conductors : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
58 | 6.3.2.2, 7.1.1.3.3, 7.1.1.3.5 | Cable lugs : | not required |  | not required | [5 empty] | select | not required | required
59 | 7.1.1.12 | Bus duct entry : | not required |  | not required | [5 empty] | select | not required | required
60 | 7.1.1.12 | Cable bus entry : | not required |  | not required | [5 empty] | select | not required | required
61 |  | Power circuit breakers
62 | 7.1.1.3 | Incoming cable/bus entry location : | top |  | top | [5 empty] | select | top | bottom
63 | 7.1.1.3 | Feeder cable entry location : | top |  | top | [5 empty] | select | top | bottom
64 | 7.6 | Circuit breaker operation : | electrically operated |  | electrically operated | [5 empty] | select | manual operated | electrically operated
65 | 7.11.2 c), 7.16.2.1.2 | Mechanism charging voltage : | 120 VAC |  | 120 VAC | [5 empty] | select | 120 VAC | 125 VDC | other | N/A
66 |  | Trip coil voltage : | 125 VDC |  | 125 VDC | [5 empty] | select | 120 VAC | 125 VDC | 24 VDC | other
67 |  | Close coil voltage : | 125 VDC |  | 125 VDC | [5 empty] | select | 120 VAC | 125 VDC | 24 VDC | other | N/A
68 | 7.17.11, 7.15.4 | Protection type
69 | 7.15.4 | Incomer/main breaker : | trip unit-LSI |  | trip unit-LSI | [5 empty] | select | external protection relay | trip unit-LSI | trip unit-LSIG | trip unit-LI | trip unit-LS | trip unit-LIG | N/A
70 | 7.15.4 | Tie breaker : | trip unit-LSI |  | trip unit-LSI | [5 empty] | select | external protection relay | trip unit-LSI | trip unit-LSIG | trip unit-LI | trip unit-LS | trip unit-LIG | N/A
71 | 7.15.4 | Feeder breaker : | trip unit-LSI |  | trip unit-LSI | [5 empty] | select | External protection relay | trip unit-LSI | trip unit-LSIG | trip unit-LI | trip unit LS | trip unit-LIG | N/A
72 | 7.15.12 | Arc reducing maintenance function : | not required |  | not required | [5 empty] | select | not required | local switch | remote switch | communication | multiple
73 | 7.16.2.8, 7.17.14 | Control power source : | internal CPT |  | internal CPT | [5 empty] | select | internal CPT | external | N/A
74 | 7.17.2.1, 7.17.2.4 | Status indicator lights : | open-closed |  | open-closed | [5 empty] | select | not required | open-closed | open-closed-trip
75 |  | Trip coil monitoring : | not required |  | not required | [5 empty] | select | not required | indicating light | protective relay
76 | 7.17.6 | Circuit breaker control device : | required |  | required | [5 empty] | select | not required | required
77 | 7.17.11, 7.17.12 | Lockout relay : | not required |  | not required | [5 empty] | select | not required | required
78 |  | Metering and control
79 | 7.17.1, 7.17.3 | Incoming metering : | not required |  | not required | [5 empty] | select | not required | power quality meter | microprocessor | digital meters | analog meters
80 | 7.17.1, 7.17.3 | Feeder metering : | not required |  | not required | [5 empty] | select | not required | required
81 | 7.17.9 | Test switches : | not required |  | not required | [5 empty] | select | not required | required
82 | 7.15.15, 7.15.16 | Zone selective interlock : | not required |  | not required | [5 empty] | select | not required | required
83 | 7.19.4 | Arc flash detection system : | not required |  | not required | [5 empty] | select | not required | required
84 | 7.1.2.5.4 | Auto transfer scheme : | not required |  | not required | [5 empty] | select | not required | required
85 | 7.1.2.5.4, 7.11.8.4 | Breaker interlocking scheme : | not required |  | not required | [5 empty] | select | not required | required
86 |  | Interface with control systems
87 | 7.1.3.3.5 | Intelligent electronic device (IED) brand : | manufacturer standard |  | manufacturer standard | [5 empty] | select | manufacturer standard | other
88 | 7.1.3.3.5 | Process control interface (ICSS/DCS) media : | manufacturer standard |  | manufacturer standard | [5 empty] | select | manufacturer standard | not required | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fibre) | multiple | other
89 | 7.1.3.3.5 | Process control interface (ICSS/DCS) protocol : | select |  | select | [5 empty] | select | not required | volt free contact/4-20mA | DeviceNet | EtherNet/IP | IEC 61850 | Modbus TCP/IP | Profinet | Profibus | multiple | other
90 | 7.1.3.3.5 | Process control interface (ICSS/DCS) network redundancy : | select |  | select | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
91 | 7.1.3.3.5 | Electrical control interface (ECMS) media : | not required |  | not required | [5 empty] | select | manufacturer standard | not required | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fibre) | other
92 | 7.1.3.3.5 | Electrical control interface (ECMS) protocol : | not required |  | not required | [5 empty] | select | not required | volt free contact/4-20mA | DeviceNet | EtherNet/IP | IEC 61850 | Modbus TCP/IP | Profinet | Profibus | other
93 | 7.1.3.3.5 | Electrical control interface (ECMS) network redundancy : | not applicable |  | not applicable | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
94 | 7.1.3.3.5 | Intelligent electronic device (IED) remote configuration via ECMS : | not applicable |  | not applicable | [5 empty] | select | not applicable | not required (local at IED only) | required | other
95 | 7.1.3.3.5 | Communication system power supply : | not applicable |  | not applicable | [5 empty] | select | not applicable | internal simplex | internal redundant | external simplex | external redundant
96 |  | Accessories
97 | 7.1.2.5 | High resistance grounding system : | not required |  | not required | [5 empty] | select | not required | external | in switchgear
98 | 7.19.4 | Continuous thermal monitoring : | not required |  | not required | [5 empty] | select | not required | required
99 | 7.19.4 | Thermal monitoring analytical software : | not required |  | not required | [5 empty] | select | not required | required
100 | 7.19.5 | Thermal scanning inspection windows : | not required |  | not required | [5 empty] | select | not required | required
101 | 7.19.6 | Absence of voltage tester : | not required |  | not required | [5 empty] | select | not required | incoming/main | each feeder | incoming/main and each feeder
102 |  | Test kit for trip unit : | not required |  | not required | [5 empty] | select | not required | required
103 | 7.1.5.7 | Arc resistant blank unit (quantity per compartment size) : | 1 |  | 1 | [5 empty] | select | not required | 1 | 2 | other
104 | 7.3 | Ventilation opening accessories : | not required |  | not required | [5 empty] | select | not required | filter | mesh screen | filter with mesh screen
105 | 7.17, 7.19.4 | Application software : | required |  | required | [5 empty] | select | not required | required
106 | 7.19.8 | Handheld control station : | not required |  | not required | [5 empty] | select | not required | 1 | 2 | other
107 | 7.19.3 | Remote racking device : | not required |  | not required | [5 empty] | select | not required | required
108 | 7.19.7 | Circuit breaker test cabinet : | not required |  | not required | [5 empty] | select | not required | required
109 |  | Shipping and preservation
110 | 7.20.6, 7.20.7, 7.20.8 | Equipment preservation : | manufacturer standard |  | manufacturer standard | [5 empty] | select | manufacturer standard | special
111 | 7.18, 7.20.6, annex C | Provisions for energizing space heaters for storage : | not required |  | not required | [5 empty] | select | not required | required
112 | 7.20.7 | Desiccant bags installed for shipping : | each compartment |  | each compartment | [5 empty] | select | not required | incoming only | each compartment
Note on C4: Select the conformity assessment level of this equipment. The default selection of CAS level D is typically used for trusted manufacturers that the purchaser has experience with. For CAS level selection guidance, refer to IOGP S-727Q.
Note on C6: Select the upper limit ambient air temperature measured outside of the enclosure. Default value as per IEEE C37.20.1 is 40 °C.
Note on C7: Select the lower limit ambient air temperature. Default value as per IEEE C37.20.1 is -5 °C.
Note on C8: Select the LV switchgear installation altitude. IEEE C37.20.1 is based on the altitude not to exceed 2 000 m (6 600 ft). If 'other' is selected, enter the altitude in the 'Additional notes' column.
Note on C9: Select the humidity limit. As per IEEE C37.20.1, the default value measured over 24 hours not to exceed 95% non-condensing. If 'other' is selected, enter the humidity in the 'Additional notes' column.
Note on C10: Select seismic design requirement as per ASCE/SEI 7-16.
Note on C11: Provide site physical address or latitude and longitude to determine seismic acceleration values.
Note on C12: Provide risk category as per ASCE/SEI 7-16 (risk category of buildings and other structures for flood, wind, snow, earthquake, and Ice loads). Typical oil and gas category is IV.
Note on C13: Provide component importance factor of buildings and other structures for snow, ice and earthquake loads. Typical oil and gas importance factor is 1.5.
Note on C14: Provide site class as per ASCE/SEI 7-16 (Chapter 20). Site class D is to be specified if detailed soil properties are not known.
Note on C15: Provide seismic certificate by third party, only if selected in data sheet.
Note on C16: Select the installation location of the LV switchgear.
Note on C17: Select the operating environment for LV switchgear. If 'other' is selected, enter the operating environment in the 'Additional notes' column.
Note on C18: Select any contaminant exposure to the LV switchgear. If 'other' is selected, enter the contaminant (multiple) exposures in the 'Additional notes' column.
Note on C19: Select the certification requirements (in addition to NRTL or ACO). If 'other' is selected, enter the additional certification in the 'Additional notes' column.
Note on C20: Select the required certification to IEEE C37.20.7 (2017) for arc resistance testing.
Note on C22: Reference IEEE C37.20.1, Table 1. If 'other' is selected, enter the voltage in the 'Additional notes' column.
Note on C23: Indicate the nominal operating frequency. If 'other' is selected, enter the frequency in the 'Additional notes' column.
Note on C24: Indicate the power system type. If 'other' is selected, enter the phase in the 'Additional notes' column.
Note on C25: Select the power system grounding type that the LV switchgear will be connected to.
Note on C26: Specify the available fault current (symmetrical) of the power system at the LV switchgear incomer(s).
Note on C27: Specify the X/R Ratio (system reactance / system resistance). Higher X/R ratios can result in de-rating of short circuit ratings.
Note on C28: Select the system connection. If 'other' is selected, enter the system connection in the 'Additional notes' column.
Note on C30: Select if LV switchgear requires arc resistant construction that is verified through testing for internal arcing faults. Arc resistant Type 2B enclosures provide protection for personnel and improve electrical safety.
Note on C31: Select if an arc plenum for exhaust is required due to the arrangement or configuration of the room or space where the LV switchgear is located. A plenum design may not be available from all manufacturers.
Note on C32: Select the NEMA enclosure rating. If 'other' is selected, enter the required NEMA rating in the 'Additional notes' column.
Note on C33: Select the enclosure paint color.
Note on C34: Select if 'front access' only for feeder cable access is required, otherwise the manufacturers' standard is rear access for feeder cables.
Note on C35: Select if enclosure space heaters are required.
Note on C36: If enclosure space heaters are required, specify controls type.
Note on C37: If enclosure space heaters are required, specify the source for the power supply. If internal is selected, the manufacturer will supply the CPT and necessary distribution.
Note on C38: Select whether provisions for padlocking open trip and close circuits, metering and relaying power supply circuits, control circuits leaving the switchgear, space heater circuits, CPT, VT, and primary and secondary side circuits are required.
Note on C39: Select whether a mimic bus representation is required to be installed on the front of the switchgear assembly.
Note on C40: Select whether the LV switchgear assembly is to be designed for roller installation.
Note on C42: Select the main bus rating. For other main bus sizes, indicate special bus requirements in the 'Additional notes' column.
Note on C43: Select the short-circuit current rating. For 'other' ratings, reference IEEE C37.13, Table 2 and indicate the value in the 'Additional notes' column.
Note on C44: Select the bus plating material. Tin is preferred over silver in corrosive gas applications.
Note on C45: Select the main bus insulation requirement. Insulated main horizontal bus with insulated shipping split connections provides a higher degree of electrical safety and ingress protection.
Note on C46: Select the neutral bus rating. When a neutral bus is required, a full size neutral is recommended.
Note on C47: Select the location(s) where the neutral from outgoing load feeder cables will be connected in the assembly. The selection of "incoming section" will require the load neutral feeder wire to be routed to the incoming section for connection.
Note on C48: Indicate if grounding ball studs are required. Use the "additional notes" column to provide specific details for the grounding ball stud diameter and any specific feeder requirements.
Note on C50: Indicate if the LV switchgear will be designated as the service disconnecting equipment. Reference UL1558 and NFPA 70 (NEC) for service entrance requirements.
Note on C51: Select the incoming line termination type. A power circuit breaker is the most common incoming section design.
Note on C52: Select if cable entry is specified. If required, complete the five lines below.
Note on C53: If cable entry is specified, enter the conductor size needed for the incoming service.
Note on C54: If cable entry is specified, enter the conductor material. Copper is typically used.
Note on C55: If cable entry is specified, enter the number of conductors per phase. If 'other' is selected, enter the number of conductors in the 'Additional notes' column.
Note on C56: If cable entry is specified, enter the size of the incoming cable grounding conductor size.
Note on C57: If cable entry is specified, enter the number of the incoming cable grounding conductors.
Note on C58: Indicate if the manufacturer will supply the cable lugs for the incoming cable connections.
Note on C59: Select if bus duct entry is specified. If required, the manufacturer of the LV switchgear will need to be provided the details of the bus duct (ampacity, size, dimensions, number of bus bars, etc.).
Note on C60: Select if cable bus entry is specified. If required, the manufacturer of the LV switchgear will need to be provided the details of the cable duct (ampacity, size, dimensions, number of cables, etc.).
Note on C62: Select incoming cable or bus entry location.
Note on C63: Select feeder cable entry location.
Note on C64: Select if circuit breakers are electrically or manually operated
Note on C65: Select the circuit breaker mechanism charging voltage. For other voltages, indicated the voltage in the 'Additional notes' column. Select "N/A" for manually operated circuit breakers.
Note on C66: Select the circuit breaker trip coil voltage. For other trip coil voltages, indicate the voltage in the 'Additional notes' column.
Note on C67: Select the circuit breaker close coil voltage. For other close coil voltages, indicate the voltage in the 'Additional notes' column.
Note on C69: Select the protection type. LSI (long time, short time and instantaneous) is the typical protection type for the incomer. Select external protection relay for door mounted type relays.
Note on C70: Select the protection type. LSI (long time, short time and instantaneous) is the typical protection type for the tie. Select external protection relay for door mounted type relays.
Note on C71: Select the protection type. LSI (long time, short time and instantaneous) is the typical protection type for feeders. Select external protection relay for door mounted type relays.
Note on C72: Available only with a circuit breaker that is equipped with an integral trip unit. If required, indicate the method for activation. If multiple is selected, use 'Additional notes' column to specify all activation types.
Note on C73: Select the control power source. The voltage level for "internal CPT" should be 120 V nominal. Select "N/A" for manually operated breakers.
Note on C74: Select the indicator lights requirements. Additional status indicator lights can be specified on the project drawings or in the "Additional notes" column, but, will reduce standardization.
Note on C75: Select the requirement to add circuit breaker trip coil monitoring on the door (device panel). If required, Indicate if protective relay (IEEE Dev. 94) or indicating light is to be provided.
Note on C76: Select if a circuit breaker control switch (IEEE Dev. 52) is to be provided on the compartment door (device panel) for each power circuit breaker.
Note on C77: Select if a lockout relay is required for circuit breaker control (IEEE Dev. 86) is to be provided on the compartment door (device panel) for each power circuit breaker as indicated on the project drawings.
Note on C79: If incoming metering is required, indicate type necessary. If analog metering is selected, voltmeter and ammeter switches will be provided. Use the 'Additional notes' column to specify any specialty metering functions (PF, KW, KWH, etc.).
Note on C80: Select if a panel mounted metering for the feeder circuits is required. Indicate the specific details for type and quantity for feeder meeting in the 'Additional notes' column.
Note on C81: Indicate if test switches (FT1 type) are required for testing and calibration functions associated with metering and protective functions. Use the 'Additional notes' column advise which specific circuit functions will be rerouted through the test switch.
Note on C82: Indicate the zone selective interlocking protection feature is required for all power circuit breakers (this may require additional software, hardware and control wiring to be provided). Indicate which protective function or combination is to be included.
Note on C83: Indicate if an arc flash detection system is required for all vertical sections in the LV switchgear assembly (this may require additional software, hardware and control wiring to be provided).
Note on C84: Select if a circuit breaker transfer scheme is required. The specific details are shown in the project drawings and functional description documents. Use the 'Additional notes' column to indicate the reference documents
Note on C85: Select if a circuit breaker interlocking scheme is required. The specific details are shown in the project drawings and functional description documents. Use the 'Additional notes' column to indicate the reference documents
Note on C87: Select "other" if the operating company or the site has a default IED brand for operational and/or system integration commonality at that location. If "other" is selected, specify the IED manufacturer/IED range in the "Additional notes" column.
Note on C88: Select the communication media within the assembly for interface to the process control system. If "multiple" or "other" is selected, specify details in the "Additional notes" column and in the project drawings.
Note on C89: Select the communication protocol within the assembly for the stated media interface to the process control system. If "multiple" or "other" is selected, specify details in the "Additional note" column and in the project drawing.
Note on C90: PRP or HSR (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. If “other” is selected, specify the redundancy protocol in the “Additional note” column.
Note on C91: If required, select the communication media within the assembly for interface to the electrical control and management system. If "other" is selected, specify details in the "Additional notes" column.
Note on C92: If required, select the communication protocol within the assembly for the stated media interface to the electrical control and management system. If "other" is selected, specify details in the "Additional notes" column.
Note on C93: PRP or HSR (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. If “other” is selected, specify the redundancy protocol in the “Additional note” column.
Note on C94: Not applicable if an ECMS is not specified. Where required, this is an optional facility provided by the electrical control system / power management system to remotely edit IED protection and logic settings by a user with the correct system privileges.
Note on C95: Select the level of desired redundancy including aux power to the breaker trip units. If "internal" is selected, the power supply is provided with the assembly. Refer to project drawings for additional details.
Note on C97: Select if a high resistance grounding (HRG) system is required. Indicate if it is to be installed integral to the switchgear or externally in a separate free standing enclosure.
Note on C98: Select if continuous thermal monitoring system is required. This may require additional hardware, software and control wiring to be installed.
Note on C99: Select if a thermal monitoring analytical software is required. This includes any nonstandard interface cables but does not include any computer hardware.
Note on C100: Select the requirement for thermal scanning inspection windows. Manufacturer to indicate recommended locations.
Note on C101: Select the requirement and location for absence of voltage tester devices. The installation of these devices in each unit can be used to establish an electrically safe work condition and assist with LOTO procedures. Refer to the requirements in NFPA 70E.
Note on C102: Select if a test kit for the circuit breaker trip unit is required. If more than one is required, indicate the number in the 'Additional notes' column.
Note on C103: Select the number of blanks per compartment size. If 'other' is selected, use the 'Additional notes' column for details. The blank unit is used to maintain the arc resistant rating when a circuit breaker is removed for maintenance.
Note on C104: Select the requirement for ventilation opening accessories. Mesh screens are typically less than or equal to 1/8 in. (3 mm) and used to prevent vermin entry to the assembly.
Note on C105: Select if the application software for monitoring, control, and configuration of digital programmable devices is required including any nonstandard interface cables. Provide specific requirements in the "Additional notes" column.
Note on C106: Indicate if a remote handheld control station is needed to operate the power circuit breakers. If so, indicate the number of units needed. If other is selected, indicate details in the "additional notes" column.
Note on C107: Indicate if a remote racking device (motorized) is needed to insert or withdraw the power circuit breakers from the stationary element. Use the 'Additional notes' column to indicate the number of units needed.
Note on C108: Select if a circuit breaker test cabinet for operating the circuit breaker outside of the assembly is required.
Note on C110: Select the equipment preservation requirement. Manufacturer standard packaging is appropriate for domestic shipping (not offshore) and indoor storage. If "special" is selected, use the 'Additional note' column or 'Supplement' tab for additional details.
Note on C111: Select the requirement for energizing space heater for storage. If required, the preservation packaging will allow for access to the space heater connections without compromising the preservation integrity.
Note on C112: Select the requirements for desiccant bags for shipping.

## Supplement
Row |  | IOGP S-727D (1.01) Procurement Data Sheet for Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear (IEEE Std C37.20.1) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
9
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-727D (1.01) Procurement Data Sheet for
Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear
(IEEE Std C37.20.1)
Guidance on the use of this procurement data sheet
To be used in conjunction with :
IOGP S-727 Supplementary Specification to IEEE Std C37.20.1 Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data