## Addendum 1
Date of issue:
May 2025
Affected publication:
IOGP S-742D, Procurement Data Sheet for Medium-Voltage AC Contactors, Controllers, and Control Centers (UL 347), First Edition, September 2022
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in September 2022.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Row | Column | Update
| 6 | Supplier offered value - options | Spurious error correction (default value amended from "N/A" * to"'D" to match the "Purchaser requirement" column)
| 37 | All | New data sheet item "Enclosure design for roller installation"
| 38 to 76 | All | Rows 37 * to 75 * renumbered to 38 to 76
| 76 * through 78 * | All | Section "Remote monitoring and control" * deleted including data sheet items ""Network provisions" * and "Communications protocol" *
| 77 | All | New section heading "Interface with control systems"
| 78 | All | New data sheet item "Intelligent electronic device (IED) brand"
| 79 | All | New data sheet item "Process control interface (ICSS/DCS) media"
| 80 | All | New data sheet item "Process control interface (ICSS/DCS) protocol"
| 81 | All | New data sheet item "Process control interface (ICSS/DCS) network redundancy"
| 82 | All | New data sheet item "Electrical control interface (ECMS) media"
| 83 | All | New data sheet item "Electrical control interface (ECMS) protocol"
| 84 | All | New data sheet item "Electrical control interface (ECMS) network redundancy"
| 85 | All | New data sheet item "Intelligent electronic device (IED) remote configuration via ECMS"
| 86 | All | New data sheet item "Communication system power supply"
| 87 through 100 | All | Rows 79 * to 92 * renumbered to 87 through 100
| 88 | Purchaser requirement / Supplier offered value - options | Option "required" moved before option "not required"
| 90 | Purchaser requirement / Supplier offered value - options | Options added ("not required", "required")
| 94 | Description | Description amended to "Ventilation opening accessories" Embedded guidance note amended
|  | Purchaser requirement / Supplier offered value - options | Option "required" * deleted Options "filter", "mesh screen" and "filter with mesh screen" added
| Various | Ref. Clause | List of references amended
* Data from Edition 1.0.

## Front & Preliminaries
|  |  |  | SPECIFICATION | May 2025
|  |  |  | IOGP S-742D | Version 1.01
ADDENDUM 1 TO FIRST EDITION (SEPTEMBER 2022)
Procurement Data Sheet for Medium-Voltage AC Contactors, Controllers, and Control Centers (UL 347)
Revision history
VERSION | DATE | PURPOSE
1.01 | May 2025 | Addendum 1
1 | September 2022 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-742D (1.01) Procurement Data Sheet for Medium-Voltage AC Contactors, Controllers, and Control Centers (UL 347)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-742D (1.01) Procurement Data Sheet for Medium-Voltage AC Contactors, Controllers, and Control Centers (UL 347)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of medium-voltage AC contactors, controllers, and control centers in accordance with IOGP S-742 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-742), information requirements specification (IOGP S-742L) and quality requirements specification (IOGP S-742Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Procurement Data Sheet
Row | IOGP S-742D (1.01) Procurement Data Sheet for Medium-Voltage AC Contactors, Controllers, and Control Centers (UL 347) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | Select | A | B | C | D
7 |  | Site conditions
8 |  | Ambient air temperature - upper limit : | 40 | °C | 40 | °C |  |  |  |  | Select | 40 | 45 | 50
9 |  | Ambient air temperature - lower limit : | 0 | °C | 0 | °C |  |  |  |  | Select | 0 | -20 | -30 | -40
10 |  | Altitude of installation : | ≤ 1 000 | m | ≤ 1 000 | m |  |  |  |  | Select | ≤ 1 000 | other
11 |  | Humidity limit : | < 95 | % | < 95 | % |  |  |  |  | Select | < 95 | other
12 | 2.2.4 | Seismic design : | not required |  | not required | [5 empty] | Select | not required | required
13 | 2.2.4 | Site location : | input data |  | input data
14 | 2.2.4 | Seismic certificate : | not required |  | not required | [5 empty] | Select | not required | required
15 |  | Installation environment : | indoor climate controlled |  | indoor climate controlled | [5 empty] | Select | indoor climate controlled | indoor ventilated | outdoor
16 | 2.2.5, 2.2.6 | Application/operating environment : | onshore |  | onshore | [5 empty] | Select | onshore | offshore - fixed | offshore - floating | marine (ship) | other
17 | 2.2.5 | Environmental contamination : | none |  | none | [5 empty] | Select | none | salt-laden | H₂S | salt-laden and H₂S | severe dust | other
18 | 2.2.6 | Certification (additional) : | not required |  | not required | [5 empty] | Select | not required | USCG/ABS | other
19 | 5.103.3 | Arc-resistant certification : | 3rd-party certified |  | 3rd-party certified | [5 empty] | Select | 3rd-party certified | self-declared | N/A
20 |  | Electrical power parameters
21 | 2.1, 4.1.201 | System supply voltage : | select | kV | select | kV |  |  |  |  | Select | 2.4 | 4.16 | 6.9 | 12.47 | 13.8 | other
22 |  | Frequency : | 60 | Hz | 60 | Hz |  |  |  |  | Select | 50 | 60 | other
23 | 5.204.2.3 | Phase/wire : | 3-phase 3-wire |  | 3-phase 3-wire | [5 empty] | Select | 3-phase 3-wire | other
24 | 5.204.2.3 | System grounding : | low resistance |  | low resistance | [5 empty] | Select | high resistance | low resistance | solid | ungrounded
25 |  | Available fault current (symmetrical) : | input data | kA | input data | kA
26 |  | System X/R ratio : | input data |  | input data
27 |  | System connection : | wye |  | wye | [5 empty] | Select | delta | wye
28 |  | Enclosure
29 | 5.103.1, 5.103.2, 5.103.5, 5.103.8 | Arc resistant construction : | Type 2B |  | Type 2B | [5 empty] | Select | Type 2 | Type 2B | not required
30 | 5.103.6, 5.103.7, 5.103.8 | Arc plenum : | not required |  | not required | [5 empty] | Select | not required | plenum interior exhaust | plenum exterior exhaust
31 | 5.102.210, 5.201.210.4, 6.203.2 | NEMA enclosure rating : | Type 1 |  | Type 1 | [5 empty] | Select | Type 1 | Type 1 w/ gasket | Type 2 | Type 12 | Type 3R | other
32 |  | Enclosure paint color : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | ANSI 61
33 | 5.218 | Space heater : | not required |  | not required | [5 empty] | Select | not required | required
34 | 5.218 | Space heater control : | N/A |  | N/A | [5 empty] | Select | N/A | fixed (constant ON) | thermostat | hygrostat
35 |  | Outgoing cables : | select |  | select | [5 empty] | Select | top | bottom
36 |  | Access for maintenance : | front only |  | front only | [5 empty] | Select | front only | front and rear
37 | 5.102.202 | Enclosure design for roller installation : | not required |  | not required | [5 empty] | Select | not required | required
38 |  | Incoming section
39 |  | Cable/bus entry location : | select |  | select | [5 empty] | Select | top | bottom | transition section
40 | 5.204.2.2 | Service entrance application : | no |  | no | [5 empty] | Select | no | yes
41 | 5.102.202.8, 5.102.202.9, 7.1 | Incoming line type : | cable |  | cable | [5 empty] | Select | cable | non-segregated phase bus duct | cable bus | close-coupled to switchgear bus
42 |  | Protection device : | not required |  | not required | [5 empty] | Select | not required | fused disconnect switch | fixed mount vacuum circuit breaker | withdrawable vacuum circuit breaker | interrupter | other
43 | 5.216.1 | Metering : | not required |  | not required | [5 empty] | Select | not required | power quality meter | microprocessor | digital meters | analog meters
44 |  | Bus voltage transformers (VTs) : | open-delta |  | open-delta | [5 empty] | Select | not required | open-delta | wye-wye
45 | 5.216.2.2 | Test switch : | not required |  | not required | [5 empty] | Select | not required | protective relay only | protective relay and metering
46 |  | Incoming cable
47 |  | Conductor size : | input data | AWG | input data | AWG |  |  |  |  | Select | AWG | kcmil
48 |  | Conductor material : | copper |  | copper | [5 empty] | Select | copper | aluminum
49 |  | Number of conductors per phase : | select | no. | select | no. |  |  |  |  | Select | 1 | 2 | 3 | 4 | other
50 |  | Incoming cable grounding conductor size : | input data | AWG | input data | AWG
51 | 5.3.203.8 | Number of incoming cable ground conductors : | select | no. | select | no. |  |  |  |  | Select | 1 | 2 | 3 | 4 | other
52 |  | Power bus
53 | 2.1, 4.4.101, 4.4.201 | Continuous current rating : | select | A | select | A |  |  |  |  | Select | 1 000 | 1 200 | 2 000 | 3 000 | other
54 | 4.5, 4.7.2 | Rated short-time withstand current : | 50 | kA | 50 | kA |  |  |  |  | Select | 40 | 50 | other
55 | 4.7.2 | Rated short-circuit current duration : | 0.5 | sec | 0.5 | sec |  |  |  |  | Select | 0.167 | 0.5 | 1 | 2
56 | 2.2.5, 4.4.202.6 | Power bus plating material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | tin | silver
57 |  | Neutral bus : | not required |  | not required | [5 empty] | Select | not required | required
58 |  | Controller (general)
59 |  | Contactor type : | stationary |  | stationary | [5 empty] | Select | stationary | withdrawable
60 | 4.201.2 | Power fuse type : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | bolt-on | clip-on
61 |  | Control power source : | individual unit CPT |  | individual unit CPT | [5 empty] | Select | individual unit CPT | external 120 VAC | 125 VDC
62 | 5.216.2.4 | Protective relay power source : | same as control power |  | same as control power | [5 empty] | Select | same as control power | external 120 VAC | external 125 VDC
63 | 5.214.11 | Auxiliary contacts : | none |  | none | [5 empty] | Select | none | 1 NO and 1 NC | 2 NO and 2 NC
64 |  | Controller (motor starter)
65 | 5.216.3.1, 5.102.208 | Status indicator lights : | run-stopped |  | run-stopped | [5 empty] | Select | run-stopped-trip | run-stopped | not required
66 | 5.102.208 | Start/stop pushbuttons : | not required |  | not required | [5 empty] | Select | not required | required | required-start in test only
67 | 5.216.3.4, 5.102.208 | E- stop pushbutton : | required |  | required | [5 empty] | Select | not required | required | controller dependent
68 | 5.218.9.2, 5.219.4, 5.219.5, 5.219.6 | Motor space heater ammeter : | not required |  | not required | [5 empty] | Select | not required | required | required with push button
69 | 5.216.2.2 | Test switch : | not required |  | not required | [5 empty] | Select | not required | CTs and VTs only | CT/VT + DI/DO
70 | 5.216.2.5 | Lock out relay : | not required |  | not required | [5 empty] | Select | not required | required | controller dependent
71 |  | Controller (latched)
72 | 5.216.3.1 | Status indicator lights : | closed-open |  | closed-open | [5 empty] | Select | closed-open-trip | closed-open | not required
73 | 5.216.3.2 | Open/close pushbuttons : | not required |  | not required | [5 empty] | Select | not required | required
74 | 5.216.3.4 | E-stop pushbutton : | required |  | required | [5 empty] | Select | not required | required | controller dependent
75 | 5.216.2.2 | Test switch : | not required |  | not required | [5 empty] | Select | not required | CTs and VTs only | CT/VT + DI/DO
76 | 5.216.2.5 | Lock out relay : | not required |  | not required | [5 empty] | Select | not required | required | controller dependent
77 |  | Interface with control systems
78 | 5.205.1.8 | Intelligent electronic device (IED) brand : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | other
79 | 5.205.1.8 | Process control interface (ICSS/DCS) media : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | not required | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fiber) | multiple | other | to be provided later
80 | 5.205.1.8 | Process control interface (ICSS/DCS) protocol : | select |  | select | [5 empty] | Select | not required | volt-free contact / 4-20mA | DeviceNet | EtherNet/IP | IEC 61850 | Modbus TCP/IP | Profinet | Profibus | multiple | other | to be provided later
81 | 5.205.1.8 | Process control interface (ICSS/DCS) network redundancy : | select |  | select | [5 empty] | Select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other | to be provided later
82 | 5.205.1.8 | Electrical control interface (ECMS) media : | not required |  | not required | [5 empty] | Select | manufacturer's standard | not required | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fiber) | other | to be provided later
83 | 5.205.1.8 | Electrical control interface (ECMS) protocol : | not required |  | not required | [5 empty] | Select | not required | volt-free contact / 4-20mA | DeviceNet | EtherNet/IP | IEC 61850 | Modbus TCP/IP | Profinet | Profibus | other | to be provided later
84 | 5.205.1.8 | Electrical control interface (ECMS) network redundancy : | not applicable |  | not applicable | [5 empty] | Select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other | to be provided later
85 | 5.205.1.8 | Intelligent electronic device (IED) remote configuration via ECMS : | not applicable |  | not applicable | [5 empty] | Select | not applicable | not required (local at IED only) | required | other | to be provided later
86 | 5.205.1.8 | Communication system power supply : | not required |  | not required | [5 empty] | Select | not required | internal simplex | internal redundant | external simplex | external redundant
87 |  | Accessories
88 | 5.205.1.8 | Application software : | required |  | required | [5 empty] | Select | required | not required
89 | 5.217.6.1 | Continuous thermal monitoring : | not required |  | not required | [5 empty] | Select | not required | required
90 | 5.217.2 | Thermal scanning inspection windows : | not required |  | not required | [5 empty] | Select | not required | required
91 | 5.217.6.2, 5.217.6.3 | Motor condition monitoring : | not required |  | not required | [5 empty] | Select | not required | local (manual) | continuous
92 | 5.217.6.4 | Partial discharge monitoring : | not required |  | not required | [5 empty] | Select | not required | required
93 | 4.8.4 | Voltage loss ride-through : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | other
94 | 5.102.206, 6.208.4 | Ventilation opening accessories: | not required |  | not required | [5 empty] | Select | not required | filter | mesh screen | filter with mesh screen
95 | 5.217.1 | Handheld control station : | not required |  | not required | [5 empty] | Select | not required | 1 | 2 | other
96 | 5.221.1, 5.221.2 | Grounding (earthing) switch : | not required |  | not required | [5 empty] | Select | not required | required | required with fault close rating
97 |  | Shipping and preservation
98 |  | Equipment preservation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | special
99 | 8.5 | Provisions for energizing space heaters for storage : | not required |  | not required | [5 empty] | Select | not required | required
100 |  | Desiccant bags installed for shipping : | not required |  | not required | [5 empty] | Select | not required | each controller | each compartment | other
Note on C4: Indicate the unique tag number for the equipment.
Note on C5: Provide a functional description of the equipment as per the equipment list.
Note on C6: Select the conformity assessment level of this equipment. For CAS level selection guidance, refer to IOGP S-742Q, Annex A. Default value : D
Note on C8: Select the upper limit ambient air temperature measured outside of the enclosure. The default value as per UL 347 is 40 °C with the 24 h average not exceeding 35 °C. Default value : 40
Note on C9: Select the lower limit ambient air temperature. The default value as per UL 347 is 0 °C. Default value : 0
Note on C10: Select the MV MCC installation altitude. UL 347 is based on the altitude not to exceed 1 000 m (3 300 ft). If 'other' is selected, specify the altitude in the 'Additional notes' column. Default value : ≤ 1 000
Note on C11: Select the humidity limit. As per UL 347, default value measured over 24 hours not to exceed 95% non-condensing. If 'other' is selected, specify the humidity in the 'Additional notes' column. Default value : < 95
Note on C12: Select the seismic design requirement as per ASCE/SEI 7-16. Default value : not required
Note on C13: Specify the site physical address or latitude and longitude to determine the seismic acceleration values.
Note on C14: Specify the third-party seismic certificate, only if selected on this data sheet. Default value : not required
Note on C15: Select the installation environment of the MV MCC. Default value : indoor climate controlled
Note on C16: Select the operating environment for MV MCC. If 'other' is selected, enter the operating environment in the 'Additional notes' column. Default value : onshore
Note on C17: Select any contaminant exposure to the MV MCC. If 'other' is selected, enter the contaminant exposure in the 'Additional notes' column. Default value : none
Note on C18: Select the certification requirements (in addition to NRTL or ACO). If 'other' is selected, enter the additional certification in the 'Additional notes' column. Default value : not required
Note on C19: Select the required certification for arc resistance testing. Default value : 3rd-party certified
Note on C21: Select the nominal utilization voltage. If 'other' is selected, specify the voltage in the 'Additional notes' column.
Note on C22: If 'other' is selected, specify the frequency in the 'Additional notes' column. Default value : 60
Note on C23: If 'other' is selected, specify the configuration in the 'Additional notes' column. Default value : 3-phase 3-wire
Note on C24: Select the grounding system of the facility that the MV MCC will be connected to. Default value : low resistance
Note on C25: Specify the available fault current (symmetrical) of the system at the MV MCC point of connection from the purchaser's power system study.
Note on C26: Specify the X/R ratio (system reactance/system resistance). Higher X/R ratios can result in de-rating of short circuit ratings.
Note on C27: Select the system connection. Default value : wye
Note on C29: Select whether the MV MCC requires arc resistant construction that is verified through testing for internal arcing faults. Arc resistant Type 2B enclosures provide protection for personnel and improve electrical safety. Default value : Type 2B
Note on C30: Select whether an arc plenum for exhaust is required due to the arrangement or configuration of the room or space where the MV MCC is located. A plenum design may not be available from all manufacturers. Default value : not required
Note on C31: Select the NEMA enclosure rating. If 'other' is selected, enter the desired NEMA rating in the 'Additional notes' column. Default value : Type 1
Note on C32: Select the enclosure paint color. Default value : manufacturer's standard
Note on C33: Select whether vertical section space heaters are required. Default value : not required
Note on C34: If vertical section space heaters are required, specify the control type. Default value : N/A
Note on C35: Select the location of the outgoing cables.
Note on C36: Select if rear access is needed for maintenance. It may be necessary for access to incoming and outgoing cables or main bus shipping split connections. Default value : front only
Note on C37: Select whether the MV MCC assembly is to be designed for roller installation. Default value : not required
Note on C39: Select the incoming cable/bus entry location.
Note on C40: Select whether this MV MCC will be designated as service entrance equipment. Default value : no
Note on C41: Select the incoming line type. Default value : cable
Note on C42: Select the incoming line protection device type. 'not required' indicates that the protective device is elsewhere and not provided in this assembly. If 'other' is selected, specify the specific protection requirements in the 'Additional notes' column. Default value : not required
Note on C43: If incoming metering is required, select the type. If analog metering is selected, voltmeter and ammeter switches will be provided. Use the 'Additional notes' column to specify any specialty metering functions (e.g., PF, KW, KWH). Default value : not required
Note on C44: Select the arrangement for the bus VTs. Two VTs will be provided for 'open-delta' and three VTs will be provided for 'wye-wye'. The 'wye-wye' connection is needed for advanced monitoring and diagnostics. Default value : open-delta
Note on C45: Select whether test switches (FT type) are required for testing and calibration functions associated with metering and protective devices. Use the 'Additional notes' column to advise which specific functions are to be routed through the test switch. Default value : not required
Note on C47: If 'cable entry' is specified, specify the conductor size needed for the incoming service. Cables greater than 4/0 AWG are expressed in kcmil. Default value : AWG
Note on C48: If 'cable entry' is specified, specify the conductor material. Default value : copper
Note on C49: If 'cable entry' is specified, specify the number of conductors per phase. If 'other' is selected, specify the number of conductors in the 'Additional notes' column.
Note on C50: If 'cable entry' is specified, specify the size of the incoming cable grounding conductor size.
Note on C51: If 'cable entry' is specified, specify the number of the incoming cable grounding conductors. If 'other' is selected, specify the number of grounding conductors in the 'Additional notes' column.
Note on C53: Select the main bus rating. For other main bus sizes, specify the bus requirements in the 'Additional notes' column.
Note on C54: Select the maximum symmetrical rms value for the rated short-time withstand current (Ik) for the horizontal power bus. For 'other' ratings, specify the value in the 'Additional notes' column. Default value : 50
Note on C55: Select the value for the duration of the short-circuit current (tk) for the horizontal power bus. For close-coupled to switchgear applications, 2 seconds should be selected. Default value : 0.5
Note on C56: Select the bus plating material. Tin is preferred over silver in corrosive gas applications. Default value : manufacturer's standard
Note on C57: Select whether a neutral bus is required. If a neutral bus is required, specify the neutral bus details in the 'Additional notes' column. Default value : not required
Note on C59: Select the contactor mounting arrangement. The stationary type has bolted connections. The withdrawable type only requires the removal of retaining bolts to remove the contactor. Default value : stationary
Note on C60: Select the power fuse mounting type. If clip-on fuses are provided, a fuse pulling device should be provided. Default value : manufacturer's standard
Note on C61: Select the control power source. Default value : individual unit CPT
Note on C62: Select the protective relay power source. This may differ from the control power source in order to allow for controller status and communications capability when the controller is isolated. Default value : same as control power
Note on C63: Select the number of auxiliary contacts required for each controller (NO-normally open, NC-normally closed). Default value : none
Note on C65: Select the indicator lights requirements. Additional status indicator lights can be specified on the project drawings or in the 'Additional notes' column, but this will reduce standardization. Default value : run-stopped
Note on C66: Select the requirement to add start/stop pushbuttons installed on the door of each motor controller unit. The 'required-start in test only' is recommended for non-arc resistant motor controllers which limits operator exposure. 'Stop' is always active. Default value : not required
Note on C67: Select the requirement to add an emergency stop pushbutton installed on the door (instrument compartment) of each motor controller unit. See project drawings for locations if 'controller dependent' is selected. Default value : required
Note on C68: Select the options for the motor space heater circuit. A momentary pushbutton with the ammeter selection will bypass the 'M' contact and energize the space heater circuit. Default value : not required
Note on C69: Select whether test switches (FT type) are required for testing and calibration functions associated with protective devices. Use the 'Additional notes' column to specify which specific functions are to be routed through the test switch Default value : not required
Note on C70: Select the requirement to add a lockout relay for motor protection (IEEE device 86) on the door (instrument compartment) of each motor controller unit. See project drawings for the locations if 'controller dependent' is selected. Default value : not required
Note on C72: Select the indicator lights requirements. Additional status indicator lights can be specified on the project drawings or in the "additional notes" column, but will reduce standardization. Default value : closed-open
Note on C73: Select the requirement to add open/ close pushbuttons installed on the door (instrument compartment) of each controller unit. Default value : not required
Note on C74: Select the requirement to install an emergency stop pushbutton on the door (instrument compartment) of each latched controller unit. See project drawings for locations if 'controller dependent' is selected. Default value : required
Note on C75: Select whether test switches (FT type) are required for testing and calibration functions associated with protective functions. Use the 'Additional notes' column to advise which specific functions are to be routed through the test switch. Default value : not required
Note on C76: Select the requirement to install a lockout relay for motor protection (IEEE device 86) on the door (instrument compartment) of each motor controller unit. See project drawings for locations if 'controller dependent' is selected. Default value : not required
Note on C78: Select "other" if the operating company or the site has a default IED brand for operational and/or system integration commonality at that location. If "other" is selected, specify the IED manufacturer / IED range in the "Additional notes" column. Default value : manufacturer's standard
Note on C79: Select the communication media within the assembly for interface to the process control system. If "multiple" or "other" is selected, specify details in the "Additional notes" column and in the project drawings. Default value : manufacturer's standard
Note on C80: Select the communication protocol within the assembly for the stated media interface to the process control system. If "multiple" or "other" is selected, specify details in the "Additional notes" column and in the project drawings.
Note on C81: PRP or HSR (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. If “other” is selected, specify the redundancy protocol in the “Additional notes” column.
Note on C82: If required, select the communication media within the assembly for interface to the electrical control and management system. If "other" is selected, specify details in the "Additional notes" column. Default value : not required
Note on C83: If required, select the communication protocol within the assembly for the stated media interface to the electrical control and management system. If "other" is selected, specify details in the "Additional notes" column. Default value : not required
Note on C84: PRP or HSR (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. If “other” is selected, specify the redundancy protocol in the “Additional notes” column. Default value : not applicable
Note on C85: Not applicable if an ECMS is not specified. Where required, this is an optional facility provided by the electrical control system / power management system to remotely edit IED protection and logic settings by a user with the correct system privileges. Default value : not applicable
Note on C86: Select the level of desired redundancy, including auxiliary power to the data switches and other miscellaneous communication equipment. If "external" is selected, it is to be supplied by others. Refer to project drawings for additional details. Default value : not required
Note on C88: Select whether individual software packages for configuration, diagnostics, controls, protection, CBM data analytics are required. Provide specific requirements in the 'Additional notes' column. This includes nonstandard interface cables. Default value : required
Note on C89: Select whether a continuous thermal monitoring system is required. This may require additional hardware, software and control wiring to be installed. Use the 'Additional notes' column to specify details for the system. Default value : not required
Note on C90: Select the requirement for thermal scanning inspection windows. Manufacturer to indicate recommended locations. Default value : not required
Note on C91: Select whether a motor condition monitoring system is required. This may require additional hardware, software and control wiring to be installed. If specific motors are to be monitored, refer to the detailed project drawings. Default value : not required
Note on C92: Select whether a continuous partial discharge monitoring system is required. This may require additional hardware, software and control wiring to be installed. Use the 'Additional notes' column to specify details for the system. Default value : not required
Note on C93: Select whether a specific time is required for loss of voltage ride-through. Specify the minimum requirement in the 'Additional notes' column. Specifying a time greater than the manufacturer's standard may add additional components and cost. Default value : manufacturer's standard
Note on C94: Select the requirement for ventilation opening accessories. Mesh screens are typically less than or equal to 1/8 in. (3 mm) and used to prevent vermin entry to the assembly. Default value : not required
Note on C95: Select whether a remote handheld control station is needed to operate the controllers. If so, specify the number of units needed. If 'other' is selected, specify the quantity needed in the 'Additional notes' column. Default value : not required
Note on C96: The grounding switch provides a factory integrated means to safely ground the load side terminals of the controller after the isolation switch is opened. Default value : not required
Note on C98: Select the equipment preservation requirement. The manufacturer's standard shipping is appropriate for domestic shipping (not offshore) and indoor storage. If 'special' is selected, use the 'Additional notes' column or 'Supplement' tab for more details. Default value : manufacturer's standard
Note on C99: Select the requirement for energizing space heater for storage. If required, the preservation packaging will allow for access to the space heater connections without compromising the preservation integrity. Default value : not required
Note on C100: Select the requirements for desiccant bags for shipping. If 'other' is selected, use the 'Additional notes' column or 'Supplement' tab to specify alternate preservation methods, (e.g., vapor phase corrosion inhibitors). Default value : not required

## Supplement
Row |  | IOGP S-742D (1.01) Procurement Data Sheet for Medium-Voltage AC Contactors, Controllers, and Control Centers (UL 347) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-742D (1.01) Procurement Data Sheet for
Medium-Voltage AC Contactors, Controllers, and Control Centers
(UL 347)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-742 Supplementary Specification to UL 347 Medium-Voltage AC Contactors, Controllers, and Control Centers.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data