## Addendum 1
Date of issue:
June 2025
Affected publication:
IOGP S-620D, Procurement Data Sheet for High-voltage Switchgear and Controlgear (IEC), Second Edition, December 2022
ADDENDUM 1
This addendum (Version 2.01) replaces Edition 2.0 published in December 2022.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Row | Column | Update
| 10 | All | New data sheet item "Local language for information/caution/danger/warning labels"
| 17 * | All | Data sheet item "Site pollution severity (SPS) class" * deleted
| 21 | All | New data sheet item "Classification for condensation and pollution"
| 44 * and 45 * | All | Section "Ratings of the internal arc classification (IAC)" * including "Data sheet item "Accessibility type" * deleted
| 46 | Description | Description including embedded guidance note amended
|  | Purchaser requirement / Supplier offered value | Default value amended to "withdrawable"
| 47 | Purchaser requirement / Supplier offered value - options | New option "other"
| 74 | Description | Description including embedded guidance note amended
|  | Purchaser requirement / Supplier offered value | Default value amended to "manufacturer's standard"
| 76 | Purchaser requirement / Supplier offered value | Default value amended to "IP31"
|  | Purchaser requirement / Supplier offered value - options | List of options replaced with "IP31, other"
| 78 | All | New data sheet item "Minimum degree of protection against mechanical impacts"
| 80 | All | New data sheet item "Locking facilities - high-voltage compartments"
| 81 | Description | Description including embedded note amended
|  | Purchaser requirement / Supplier offered value - options | New option "handle without lock"
| 82 | Description | Description including embedded note amended
|  | Purchaser requirement / Supplier offered value | Default value "manufacturer's standard locking facility" added
| 86 | Purchaser requirement / Supplier offered value | Default value amended to "IPXXB"
|  | Purchaser requirement / Supplier offered value - options | List of options replaced with "IPXXB, other"
| 87 * | All | Data sheet item "Minimum degree of protection by enclosure with doors open - shutters" * deleted
| 91 | All | New data sheet item "Status colour of indicators and on human machine interface screens"
List of updates (continued)
| Row | Column | Update
| 107 and 108 | All | Data sheet item "Circuit-breaker mechanical endurance class" * replaced with data sheet item "Circuit-breaker mechanical endurance class for motor feeders" and data sheet item "Circuit-breaker mechanical endurance class for non-motor feeders"
| 110 | All | New data sheet item "Automatic spring discharge mechanism"
| 116 | Purchaser requirement / Supplier offered value - options | List of options amended to "manufacturer's standard, common withdrawable VT, common non-withdrawable VT, individual functional unit VT, defined on a circuit-by-circuit basis"
| 119 | All | New data sheet item "Voltage transformer for gas insulated switchgear"
| 125 | Description | Embedded guidance note amended
|  | Purchaser requirement / Supplier offered value - options | Second option amended to "pluggable cable connectors"
| 127 | Description | Embedded guidance note amended
|  | Purchaser requirement / Supplier offered value - options | Second option amended to "pluggable cable connectors"
| 129 | All | New data sheet item "Cable entry method"
| 178 | All | New data sheet item "Provision for moving shipping section to location"
| Several | Row | Numbering updated as per deletion of Edition 2.0 rows and addition of Version 2.01 new rows
* Data from Edition 2.0.

## Front & Preliminaries
[5 empty] | SPECIFICATION | June 2025
[5 empty] | IOGP S-620D | Version 2.01
ADDENDUM 1 TO SECOND EDITION (DECEMBER 2022)
Procurement Data Sheet for High-voltage Switchgear and Controlgear (IEC)
Revision history
| VERSION | DATE | PURPOSE
| 2.01 | June 2025 | Addendum 1
| 2 | December 2022 | Second Edition
| 1 | October 2018 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-620D (2.01) Procurement Data Sheet for High-voltage Switchgear and Controlgear (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
This second edition cancels and replaces the first edition published in October 2018. Due to technical writing requirements leading to extensive changes, this second edition should be treated as a new document.
IOGP S-620D (2.01) Procurement Data Sheet for High-voltage Switchgear and Controlgear (IEC)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of high-voltage switchgear and controlgear in accordance with IOGP S-620 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-620), information requirements specification (IOGP S-620L) and quality requirements specification (IOGP S-620Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Procurement Data Sheet
Row | IOGP S-620D (2.01) Procurement Data Sheet for High-voltage Switchgear and Controlgear (IEC) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Project country : | input data |  | input data
9 |  | Project region : | input data |  | input data
10 |  | Local language for information/caution/danger/warning labels : | input data |  | input data
11 |  | Location environment
12 | 6.101,9.5 | Location environment : | select |  | select | [5 empty] | select | onshore | offshore – fixed | offshore – floating | marine (ship)
13 |  | Ambient air temperature - upper limit : | 40 | °C | 40 | °C
14 |  | Ambient air temperature - daily average maximum : | 35 | °C | 35 | °C
15 |  | Ambient air temperature - lower limit : | -5 | °C | -5 | °C
16 |  | Altitude : | 1000 | m | 1000 | m
17 |  | Humidity conditions - 24 h average relative humidity : | 95 | % | 95 | %
18 |  | Seismic activity zone in accordance with IEC 60721-2-6 : | not applicable |  | not applicable | [5 empty] | select | not applicable | Zone 1 | Zone 2 | Zone 3 | Zone 4
19 | 6.101 | Maximum rolling of vessel in dynamic conditions : | input data |  | input data
20 | 6.101 | Maximum pitching of vessel in dynamic conditions : | input data |  | input data
21 |  | Classification for condensation and pollution : | Class 0 |  | Class 0 | [5 empty] | select | Class 0 | Class 1 | Class 2
22 |  | Rated voltage
23 | 5.2 | Nominal and rated system voltage (Ur) : | select | kV | select | kV |  |  |  |  | select | 3.3 (3.6) | 6.6 (7.2) | 11 (12) | 22 (24) | 33 (36) | 3 (3.6) | 6 (7.2) | 10 (12) | 20 (24) | 30 (36) | 35 (40.5) | 4.16 (4.4) | 12.47 (13.2) | 13.2 (13.97) | 13.8 (14.52) | 24.94 (26.4) | 34.5 (36.5) | 45 (52)
24 | 9.102 | Type of system earthing : | select |  | select | [5 empty] | select | solidly earthed neutral | impedance earthed neutral | isolated neutral
25 |  | Rated insulation level
26 | 5.3 | Rated short-duration power-frequency withstand voltage (Ud) : | select | kV | select | kV |  |  |  |  | select | 10 / 12 | 20 / 23 | 28 / 32 | 38 / 45 | 50 / 60 | 70 / 80 | 80 / 90 | 95 / 110 | 19 / 21 | 36 / 40 | 50 / 55 | 60 / 66 | 70 / 77 | 80 / 88 | 95 / 105 | 105 / 115 | 120 / 132
27 | 5.3 | Rated lightning impulse withstand voltage (Up) kV peak : | select | kV | select | kV |  |  |  |  | select | 20 / 23 | 40 / 46 | 60 / 70 | 75 / 85 | 95 / 110 | 125 / 145 | 145 / 165 | 170 / 195 | 185 / 215 | 250 / 290 | 19 / 21 | 36 / 40 | 50 / 55 | 60 / 66 | 70 / 77 | 80 / 88 | 95 / 105 | 105 / 115 | 120 / 132
28 |  | Rated frequency
29 | 5.4 | Rated frequency (fr) : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
30 |  | Rated continuous current
31 | 5.5,E.2.1 | Rated continuous current (Ir) : | select | A | select | A |  |  |  |  | select | 630 | 800 | 1000 | 1250 | 1600 | 2500 | 3150 | 4000 | 5000
32 |  | Rated short-time withstand current
33 | 5.6.102,5.6.101,6.106, E.2.2,E.4.2 | Rated short-time withstand current (Ik, Ike) : | select | kA | select | kA |  |  |  |  | select | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63
34 | 5.6.102 | Rated short-time phase-to-earth withstand current (Ike) : | select | kA | select | kA |  |  |  |  | select | 87 % of Ik | 100 % of Ik
35 |  | Rated peak withstand current
36 | 5.7.102 | Rated peak phase-to-earth withstand current (Ipe) : | select | kA | select | kA |  |  |  |  | select | 87 % of Ip | 100 % of Ip
37 |  | Rated duration of short circuit
38 | 5.8.101,E.2.4,E.4.2 | Rated duration of short-circuit (tk) : | 1 | s | 1 | s |  |  |  |  | select | 1 | 2 | 3
39 |  | Rated supply voltage of closing and opening devices and of auxiliary and control circuits
40 | 5.9 | Closing and tripping devices : | select |  | select | [5 empty] | select | 24 V DC | 48 V DC | 60 V DC | 110 V DC | 125 V DC | 220 V DC | 250 V DC | 120 V AC | 220 V AC | 230 V AC | 240 V AC
41 | 5.9 | Indication : | select |  | select | [5 empty] | select | 24 V DC | 48 V DC | 60 V DC | 110 V DC | 125 V DC | 220 V DC | 250 V DC | 120 V AC | 220 V AC | 230 V AC | 240 V AC
42 | 5.9 | Control : | select |  | select | [5 empty] | select | 24 V DC | 48 V DC | 60 V DC | 110 V DC | 125 V DC | 220 V DC | 250 V DC | 120 V AC | 220 V AC | 230 V AC | 240 V AC
43 | 6.108.2.3 | Circuit breaker spring charging motors : | select |  | select | [5 empty] | select | 24 V DC | 48 V DC | 60 V DC | 110 V DC | 125 V DC | 220 V DC | 250 V DC | 120 V AC | 220 V AC | 230 V AC | 240 V AC
44 | 6.4.1.2 | Auxiliary circuits (e.g. panel lighting) : | select | V AC | select | V AC |  |  |  |  | select | 110 | 120 | 220 | 230 | 240
45 |  | Design and construction
46 |  | Main device withdrawal requirements : | withdrawable |  | withdrawable | [5 empty] | select | withdrawable | non-withdrawable | manufacturer's standard
47 |  | Mounting arrangement : | select |  | select | [5 empty] | select | longitudinal channels flush with floor | directly bolted to concrete floor | mounted on elevated stanchions | other
48 | 6.101 | Back-to-wall switchgear configuration required : | select |  | select | [5 empty] | select | no | yes
49 | 6.101 | Cable termination chamber location : | select |  | select | [5 empty] | select | front access | rear access | manufacturer's standard
50 |  | Requirements for gases in switchgear and controlgear
51 | 6.1 | High-voltage compartment insulating medium : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | air | low GWP | SF6
52 |  | Earthing of the high-voltage conductive parts
53 | 5.101 | Classification of earthing switches for short-circuit making : | E1 |  | E1 | [5 empty] | select | E1 | E2
54 | 7.102.1 | Earthing switch mechanical endurance class : | M0 |  | M0 | [5 empty] | select | M0 | M1
55 |  | Earthing device operator location(s) : | select |  | select | [5 empty] | select | front of panel operation only | hand held umbilical device | adjacent control panel | remote operation
56 |  | Provision of earthing truck : | not required |  | not required | [5 empty] | select | not required | required
57 |  | Voltage detecting and indicating systems
58 | 6.3.107.1,6.3.107.2,6.3.107.3, 11.6.3 | VDIS provision: | select |  | select | [5 empty] | select | not required | manufacturer's standard | integrated VDIS | separable VDIS
59 |  | Heating elements
60 | 6.4.5.2.1,6.4.5.2.2,6.4.5.2.3,6.4.5.2.4,6.4.5.2.5,6.4.5.2.6 | Low-voltage auxiliary compartment space heater provision : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | not required | required
61 | 6.4.5.2.1,6.4.5.2.2,6.4.5.2.3,6.4.5.2.4,6.4.5.2.5,6.4.5.2.6 | High-voltage connection compartment space heater provision : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | not required | required
62 |  | Space heater rated voltage : | select | V AC | select | V AC |  |  |  |  | select | 110-120 | 200-240 | not applicable
63 |  | Space heater control method : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | thermostat | hygrostat | not applicable
64 |  | Remote motor space heater supply provision : | required |  | required | [5 empty] | select | required | not required
65 |  | Remote motor space heater supply voltage : | select | V AC | select | V AC |  |  |  |  | select | 110 | 230 | not applicable
66 |  | Low- and high-pressure interlocking and monitoring devices
67 | 6.1 | Method of local gas pressure indication/alarm : | select |  | select | [5 empty] | select | manufacturer's standard | sight gauge | via IED display
68 |  | Gas and vacuum tightness - General
69 | 6.16 | Circuit breaker switching medium : | manufacturer's standard (not air) |  | manufacturer's standard (not air) | [5 empty] | select | manufacturer's standard (not air) | vacuum | SF6 | low GWP | air
70 | 6.16 | Contactor switching medium : | manufacturer's standard (not air) |  | manufacturer's standard (not air) | [5 empty] | select | manufacturer's standard (not air) | vacuum | SF6 | low GWP
71 |  | Controlled pressure systems for gas
72 | 6.103.2.3 | Provision of controlled pressure systems : | not permitted |  | not permitted | [5 empty] | select | not permitted | permitted
73 |  | Fire hazard (flammability)
74 |  | Internal wiring insulation type : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | low smoke zero halogen | manufacturer's standard | PVC
75 |  | Enclosure - general
76 | 6.102.1,6.14.2 | Minimum degree of protection by enclosure with doors closed : | IP31 |  | IP31 | [5 empty] | select | IP31 | other
77 | 6.102.1 | Consideration of floor surface : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | floor is not part of enclosure | floor may be part of enclosure
78 |  | Minimum degree of protection against mechanical impacts : | IK07 |  | IK07 | [5 empty] | select | IK07 | other
79 |  | Locking facilities
80 |  | Locking facilities - high-voltage compartments : | manufacturer's standard locking facility |  | manufacturer's standard locking facility | [5 empty] | select | manufacturer's standard locking facility | padlockable | hasp and padlock | handle without locking
81 |  | Locking facilities - low-voltage compartments : | manufacturer's standard locking facility |  | manufacturer's standard locking facility | [5 empty] | select | manufacturer's standard locking facility | padlockable | hasp and padlock | handle without lock
82 |  | Locking facilities - safety shutters, disconnectors and switches : | manufacturer's standard locking facility |  | manufacturer's standard locking facility | [5 empty] | select | manufacturer's standard locking facility | padlockable | hasp and padlock
83 |  | Padlock provider : | select |  | select | [5 empty] | select | not applicable | user supplied | manufacturer supplied
84 |  | Partitions and shutters - general
85 | 10.2 | Partition class : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | PM | PI
86 |  | Minimum degree of protection by enclosure with doors open - partitions : | IPXXB |  | IPXXB | [5 empty] | select | IPXXB | other
87 |  | Removeable parts
88 | 6.104 | Facilities for remote testing of withdrawable units : | select |  | select | [5 empty] | select | not required | required
89 |  | Labelling and identification
90 | 6.103.3.2,6.107.1.2,6.107.1.3 | Main component, primary identification language : | English |  | English | [5 empty] | select | English | other
91 |  | Status colour of indicators and on human machine interface screens : | IOGP S-620 Table 105 |  | IOGP S-620 Table 105 | [5 empty] | select | IOGP S-620 Table 105 | user defined
92 |  | Supplementary colour marking of conductors
93 | Table 107 | Phase 1 : | not required |  | not required | [5 empty] | select | not required | brown | other
94 | Table 107 | Phase 2 : | not required |  | not required | [5 empty] | select | not required | black | other
95 | Table 107 | Phase 3 : | not required |  | not required | [5 empty] | select | not required | grey | other
96 | Table 107 | Neutral : | not required |  | not required | [5 empty] | select | not required | blue | other
97 | 6.107.3, Table 107 | Supplementary conductor colour marking for DC circuits. : | not required |  | not required | [5 empty] | select | not required | required
98 |  | Mimic diagrams
99 |  | Mimic (synoptic) diagrams : | required |  | required | [5 empty] | select | required | not required
100 |  | Isolating switching devices (disconnectors)
101 |  | Switch electrical endurance class : | select |  | select | [5 empty] | select | E1 | E2 | E3
102 | 7.102.1 | Switch mechanical endurance class : | select |  | select | [5 empty] | select | M1 | M2
103 |  | Capacitive breaking capability class of switches : | no classification |  | no classification | [5 empty] | select | no classification | C1 | C2
104 |  | Circuit-breakers
105 |  | Circuit-breaker electrical endurance class : | E2 |  | E2 | [5 empty] | select | E1 | E2
106 |  | Circuit-breaker restrike class : | C1 |  | C1 | [5 empty] | select | C1 | C2
107 | 7.102.1 | Circuit-breaker mechanical endurance class for motor feeders : | M1 |  | M1 | [5 empty] | select | M1 | M2
108 |  | Circuit-breaker mechanical endurance class for non-motor feeders : | M1 |  | M1 | [5 empty] | select | M1 | M2
109 |  | Circuit-breaker system class : | S1 |  | S1 | [5 empty] | select | S1 | S2
110 |  | Automatic spring discharge mechanism : | not required |  | not required | [5 empty] | select | required | not required
111 |  | Surge arrestors
112 | 6.111.1 | Provision of metal oxide surge arresters to IEC 60099-4 : | select |  | select | [5 empty] | select | not required | required
113 |  | Voltage transformers
114 |  | Incomer voltage transformer arrangement : | select |  | select | [5 empty] | select | manufacturer's standard | withdrawable | non-withdrawable | defined on a circuit-by-circuit basis
115 |  | Outgoing feeder voltage transformer arrangement : | select |  | select | [5 empty] | select | manufacturer's standard | withdrawable | non-withdrawable | defined on a circuit-by-circuit basis
116 |  | Motor starter voltage transformer arrangement : | select |  | select | [5 empty] | select | manufacturer's standard | common withdrawable VT | common non-withdrawable VT | individual functional unit VT | defined on a circuit-by-circuit basis
117 |  | Busbar voltage transformer arrangement : | select |  | select | [5 empty] | select | manufacturer's standard | withdrawable | non-withdrawable | defined on a circuit-by-circuit basis
118 | 6.109.7 | Energy tariff voltage transformer : | not required |  | not required | [5 empty] | select | not required | required
119 |  | Voltage transformer for gas insulated switchgear : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | bus connected with isolator | direct bus connected
120 |  | Digital instruments
121 |  | Multi-function digital measuring device accuracy : | select |  | select | [5 empty] | select | class 1 | 0 S | class 0 | 5 S
122 |  | Protection devices
123 | 6.113.1 | Protection relay type : | IED - manufacturer's standard |  | IED - manufacturer's standard | [5 empty] | select | IED - manufacturer's standard | IED - user defined provider and range
124 |  | Terminals for external conductors
125 | 6.114.1.4 | Incoming (supply) unit external conductor type : | select |  | select | [5 empty] | select | cable - bolted lugs | pluggable cable connectors | busbar trunking system
126 |  | Incoming cable entry direction. : | select |  | select | [5 empty] | select | top | bottom
127 | 6.114.1.4 | Outgoing (load) unit external conductor type : | select |  | select | [5 empty] | select | cable - bolted lugs | pluggable cable connectors
128 |  | Outgoing cable entry direction. : | select |  | select | [5 empty] | select | top | bottom
129 |  | Cable entry method : | undrilled removable gland-plate |  | undrilled removable gland-plate | [5 empty] | select | undrilled removable gland-plate | drilled removable gland-plate | multi-cable transit | other
130 |  | Terminals for control and auxiliaries
131 |  | Auxiliary cable entry direction : | select |  | select | [5 empty] | select | top | bottom
132 | 6.114.2.7 | Spare terminal provision for future use : | 10 % spare |  | 10 % spare | [5 empty] | select | none | 10 % spare | 20 % spare | other
133 |  | Condition monitoring
134 | 6.116.1 | Thermal monitoring : | not required |  | not required | [5 empty] | select | not required | required | priced option
135 | 6.116.1 | Partial discharge monitoring : | not required |  | not required | [5 empty] | select | not required | required | priced option
136 | 6.116.1 | Circuit breaker condition monitoring : | not required |  | not required | [5 empty] | select | not required | required | priced option
137 |  | Motor condition monitoring equipment : | not required. |  | not required. | [5 empty] | select | not required | required
138 |  | Additional data visualization : | not required |  | not required | [5 empty] | select | not required | required
139 |  | Condition monitoring to site system interface media : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | hardwired discrete | ethernet (Cu) | RS 485 | RS 232 | ethernet (fiber) | other
140 |  | Condition monitoring to site system interface protocol : | none |  | none | [5 empty] | select | none | potential free contact | modbus | profinet | IEC 61850 | other
141 |  | Interface with control systems
142 |  | IED brand : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
143 |  | Process control interface (ICSS/DCS) media : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | not required | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fibre) | multiple | other
144 |  | Process control interface (ICSS/DCS) protocol : | select |  | select | [5 empty] | select | not required | volt-free contact/4-20mA | DeviceNet | EtherNet/IP | IEC 61850 | Modbus TCP/IP | Profinet | Profibus | multiple | other
145 |  | Process control interface (ICSS/DCS) network redundancy : | select |  | select | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
146 | Figure F.1 | Electrical control interface (ECMS) media : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fibre) | other
147 | Figure F.1 | Electrical control interface (ECMS) protocol : | not required |  | not required | [5 empty] | select | not required | volt-free contact / 4-20mA | DeviceNet | EtherNet/IP | IEC 61850 | Modbus TCP/IP | Profinet | Profibus | other
148 | Figure F.1 | Electrical control interface (ECMS) network redundancy : | not applicable |  | not applicable | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
149 |  | IED remote configuration via the ECMS : | not applicable |  | not applicable | [5 empty] | select | not applicable | not required (local at IED only) | required | other
150 |  | Switchgear interlocking/intertripping interfaces
151 |  | Interlocking/intertripping interface media : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | none | hardwired discrete | ethernet (Cu) | RS 485 | RS 232 | ethernet (fibre) | other
152 |  | Interlocking/intertripping interface protocol : | hardwired |  | hardwired | [5 empty] | select | hardwired | not required | manufacturer's standard | IEC 61850 | other
153 |  | Power management system (PMS) interfaces
154 |  | IED to PMS interface media : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | via ECMS media | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fibre) | other
155 |  | IED to PMS interface protocol : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | volt-free contact / 4-20mA | via ECMS interface | IEC 61850 | other
156 |  | IED to PMS network redundancy : | not applicable |  | not applicable | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
157 |  | Generator control panel interfaces
158 |  | IED to generator control panel interface media : | not required |  | not required | [5 empty] | select | not required | hardwired | via ECMS media | other
159 |  | IED to generator control panel interface protocol : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | volt free contact/4-20mA | via ECMS interface | IEC 61850 | other
160 |  | Application of communication protocols to protective functions
161 |  | Conformance class : | select |  | select | [5 empty] | select | class a | class b | class c
162 |  | Availability class : | A2 |  | A2 | [5 empty] | select | A1 | A2 | A3
163 |  | Network redundancy protocol : | select |  | select | [5 empty] | select | not required | manufacturer's standard | parallel redundancy protocol (PRP) | high-availability seamless redundancy HSR)
164 |  | Routine tests
165 | 7.2.10 | Partial discharge measurement test : | select |  | select | [5 empty] | select | not required | required for GIS | required for GIS and AIS
166 |  | ECMS simulation test : | select |  | select | [5 empty] | select | not required | required
167 |  | Cyber security
168 | 6.4.5.1 | Security certification for industrial automation and control system components : | select |  | select | [5 empty] | select | not required | required | other
169 |  | Internal arc fault supplementary protective measures
170 | 9.103.3 | Integrated internal arc fault detection system : | select |  | select | [5 empty] | select | not required | required
171 |  | Information to be given with enquiries, tenders and orders
172 |  | Language used for all provided information : | English |  | English | [5 empty] | select | English | other
173 |  | Transport, storage, installation, operation and maintenance
174 | 11.2 | Transport and storage environmental conditions : | select |  | select | [5 empty] | select | within defined site conditions | outside defined site service conditions - see additional notes for details
175 |  | Equipment integration location : | select |  | select | [5 empty] | select | integration at user's site | integration not at end user's site | see user's integration specification
176 |  | Load certified hoist for components > 25 kg : | not required |  | not required | [5 empty] | select | not required | required
177 |  | Circuit breaker trolley : | not required |  | not required | [5 empty] | select | not required | required
178 |  | Provision for moving switchgear shipping section to location : | select |  | select | [5 empty] | select | rolled across floor on pipes | not applicable
Note on C4: Indicate the unique tag number for the equipment.
Note on C5: A functional description of the switchgear service.
Note on C7: Select the CAS level to be applied in IOGP S-620Q, Annex A. Default value : D
Note on C8: The name assigned by ISO to the country, in ISO 3166-1.
Note on C9: Geographic location of the project within a country which will determine the applicability of local regulatory requirements.
Note on C10: Specify any additional local/native language to be used for describing information/caution/danger/warning information on the equipment labels.
Note on C12: Select the location where the assembly is to be situated as per the options available.
Note on C13: Normal service conditions as described in IEC 62271-1:2021, 4.1.2 are applied unless special service conditions are specified here. Default value : + 40
Note on C14: Normal service conditions as described in IEC 62271-1:2021, 4.1.2 are applied unless special service conditions are specified here. Default value : + 35
Note on C15: Normal service conditions as described in IEC 62271-1:2021, 4.1.2 are applied unless special service conditions are specified here. Default value : - 5
Note on C16: Normal service conditions as described in IEC 62271-1:2021, 4.1.2 are applied unless special service conditions are specified here. Default value : 1000
Note on C17: Normal service conditions as described in IEC 62271-1:2021, 4.1.2 are applied unless special service conditions are specified here. Default value : 95
Note on C18: Where seismic certification in accordance with IEC 60068-3-3 is required, specify the seismic activity zone as defined in IEC 60721-2-6 for the location where the drive is used. Where seismic certification is "not required", select "not applicable". Default value : not applicable
Note on C19: Where a floating or marine location is specified, confirm the maximum rotation about fore-and-aft axis of the vessel under dynamic conditions defined in IEC 60092-101, e.g. ± 22° 30'. Specify "not applicable" where not applicable.
Note on C20: Where a floating or marine location is specified, confirm the maximum rotation about athwartship axis of the vessel under dynamic conditions defined in IEC 60092-101, e.g. ± 7° 30'. Specify "not applicable" where not applicable.
Note on C21: Specify the classification of enclosed switchgear and controlgear as per IEC TS 62271-304 for the condensation and pollution level. The pollution level of "very light", as per IEC 62271-1:2017, is already included. Default value : Class 0
Note on C23: Nominal system voltage in accordance with IEC 60038:2021, Table 3 and Table 4. rated voltage (Ur) in parentheses in accordance with IEC 62271-1:2021, 5.2.
Note on C24: Specify the type of system earthing for which the assembly will be installed.
Note on C26: Select from the Range I series I and Range I series II values in accordance with IEC 62271-1:2021, 5.3 and IEC 62271-1:2021, Table 1 or Table 2.
Note on C27: Select from the Range I series I and Range I series II values in accordance with IEC 62271-1:2021, 5.3 and IEC 62271-1:2021, Table 1 or Table 2.
Note on C29: Specify the frequency for which the assembly shall be rated.
Note on C31: Specify the rated continuous current in accordance with IEC 62271-1:2021, 5.5. VR10 numerical series of values specified in IEC 60059.
Note on C33: Specify the rated short-time withstand current from the R10 numerical series of values specified in IEC 60059.
Note on C34: Specify the value of rated short-time phase to earth withstand current (Ike).
Note on C36: Specify the rated peak phase to earth withstand current.
Note on C38: Specify the rated duration of short circuit in accordance with IEC 62271-1:2021, 5.8. Default value : 1
Note on C40: Specify the voltage selected from the values given in Table 6 and from row items 1 to 5 in Table 7 of IEC 62271-1:2021.
Note on C41: Specify the voltage selected from the values given in Table 6 and from row line items 1 to 5 in Table 7 of IEC 62271-1:2021.
Note on C42: Specify the voltage selected from the values given in Table 6 and from row items 1 to 5 in Table 7 of IEC 62271-1:2021.
Note on C43: Specify the circuit breaker spring charging motor rated voltage.
Note on C44: Specify the auxiliary circuit rated voltage.
Note on C46: Specify the main device withdrawal requirements in accordance with IEC 62271-200:2021, Table 4. Default value : withdrawable
Note on C47: Confirmation of the required mounting arrangement as per site infrastructure.
Note on C48: Specify whether the assembly will be situated in a "back-to-wall" configuration.
Note on C49: Specify the location of cable termination chamber.
Note on C51: Specify where a technical requirement with regards to insulation medium is apparent or the need to specify equipment with a medium to match the existing switchgear. Default value : manufacturer's standard
Note on C53: Specify the classification of earthing switches for short-circuit making in accordance with the procedures of IEC 62271-102:2022, 7.101.7 Default value : E1
Note on C54: Specify the earthing switch mechanical endurance class. Default value : M0
Note on C55: Specify the required earthing device operator location.
Note on C56: Specify where a dedicated assembly earthing truck is to be provided as part of the scope of supply. Default value : not required
Note on C58: Specify where a voltage detection and indication system is required. Integrated voltage detecting and indicating system will be in accordance with IEC 62271-213 and separable VDIS will be in accordance with IEC 62271-213 and IEC 62271-215
Note on C60: Specify when a space heater is required in the low-voltage auxiliary compartment. Default value : manufacturer's standard
Note on C61: Specify when a space heater is required in the high-voltage compartment. Default value : manufacturer's standard
Note on C62: Specify the supply voltage for which the space heater is to be rated. Where space heaters have not been specified, select "not applicable".
Note on C63: While a thermostat manages the heater according to the measured temperature, a hygrostat has the additional function of measuring the air humidity as well as the temperature. Default value : manufacturer's standard
Note on C64: Specify if the motor starter functional units should be fitted with auxiliary circuits to supply remote space heaters within the high-voltage motors. Default value : required
Note on C65: Specify the rated voltage of motor space heaters for which provision is made within the high-voltage motors.
Note on C67: For GIS assemblies where local and remote indication and alarm capability are required, specify the method of local pressure indication.
Note on C69: Specify the circuit breaker switching medium. Where SF6 is unsuitable due to its high (GWP) global warming potential, a low GWP medium can be specified. Default value : manufacturer's standard (not air)
Note on C70: Specify the circuit breaker switching medium. Where SF6 is unsuitable due to its high (GWP) global warming potential, a low GWP medium can be specified. Default value : manufacturer's standard (not air)
Note on C72: For GIS assemblies, confirm whether controlled pressures systems should be as per IEC 62271-1. Default value : not permitted
Note on C74: Select the auxiliary and control circuit wiring insulation. Low smoke, zero halogen is typically required in offshore installations and in high occupancy buildings. Default value : manufacturer's standard
Note on C76: Specify the ingress protection level of the enclosure with doors closed. Default value : IP31
Note on C77: Specify whether the floor surface below the installed assembly may be considered as part of the enclosure as per 6.102.1. Default value : manufacturer's standard
Note on C78: Select the minimum degree of protection against mechanical impacts. Default value : IK07
Note on C80: Select the means of access control for high-voltage compartments covers and doors. Default value : manufacturer's standard locking facility
Note on C81: Select the means of access control for low-voltage compartments covers and doors. Default value : manufacturer's standard locking facility
Note on C82: Select the means of locking facility for safety shutters, disconnectors and switches. Default value : manufacturer's standard locking facility
Note on C83: Where padlockable facilities are specified, the purchaser may request padlocks that are provided by the manufacturer. Where padlockable facilities are not specified, select "not applicable".
Note on C85: Select the partition class of assembly in accordance with 9.101.4. There are two types of defined partition class, Class PM (3.6.107) and Class PI (3.6.108). Default value : manufacturer's standard
Note on C86: Select the ingress protection level of the enclosure with doors open for assembly partitions. Default value : IPXXB
Note on C88: Specify where facilities for remote testing of withdrawable main circuit units are required by means of extension umbilicals or specific test modules.
Note on C90: Specify the language for which the labels should be written. Where the language is other than English, this can be confirmed in the "Additional notes" column. Default value : English
Note on C91: Select the status colour of indicators and on human machine interface screens. Specify details of user defined colours for indicators in the "Additional notes" column. Default value : IOGP S-620 Table 105
Note on C93: Specify where phase 1 conductor colour may vary to meet local statutory requirements. Default value : not required
Note on C94: Specify where phase 2 conductor colour may vary to meet local statutory requirements. Default value : not required
Note on C95: Specify where phase 3 conductor colour is required or dictated by local statutory requirements. Default value : not required
Note on C96: Specify where neutral conductor colour is required or dictated by local statutory requirements. Default value : not required
Note on C97: Specify where supplementary conductor colour marking is required for DC circuits as per Table 107 (positive = red, negative = white). Default value : not required
Note on C99: Specify when a mimic one-line (synoptic) diagram is to be provided on the front of the assembly, displaying the single line arrangement of busbars and the main circuit switching devices. Default value : required
Note on C101: Specify the electrical endurance class of isolating switching devices in accordance with IEC 62271-103:2021, 5.115.
Note on C102: Specify the mechanical endurance class of isolating switching devices in accordance with IEC 62271-103:2021, 5.114.
Note on C103: Specify the capacitive breaking capability class of switches in accordance with IEC 62271-103:2021, 5.116. Default value : no classification
Note on C105: Specify the electrical endurance class of circuit breakers in accordance with IEC 62271-100:2021, 6.107.5. Default value : E2
Note on C106: Specify the circuit-breaker restrike class as per IEC 62271-100:2021, 6.107.4. Default value : C1
Note on C107: Select the mechanical endurance class of circuit breakers for motor feeders as per IEC 62271-100:2021, 6.107.2. Default value : M1
Note on C108: Select the mechanical endurance class of circuit breakers for non-motor feeders as per IEC 62271-100:2021, 6.107.2. Default value : M1
Note on C109: Specify the circuit-breaker system class as per IEC 62271-100:2021, 6.107.3. Default value : S1
Note on C110: Select whether automatic spring discharge mechanism to circuit breaker is required to ensure that spring energy is discharged prior to withdrawal. The mechanism can be identified by another equivalent term by a different supplier. Default value : not required
Note on C112: Specify where metal oxide surge arresters to IEC 60099 4 should be installed on the circuit side of the main circuit switching device within an enclosure compartment.
Note on C114: Specify what type of incomer voltage transformers are required for the application. Where "defined on a circuit-by-circuit basis" is selected, this will be communicated external to this specification.
Note on C115: Specify what type of outgoing voltage transformers are required for the application. Where "defined on a circuit-by-circuit basis" is selected, this will be communicated external to this specification.
Note on C116: Specify what type of voltage transformers are required for the application. Where "defined on a circuit-by-circuit basis" is selected, this will be communicated external to this specification.
Note on C117: Specify what type of voltage transformers are required for the application. Where "defined on a circuit-by-circuit basis" is selected, this will be communicated external to this specification.
Note on C118: Specify where a voltage transformer with an accuracy class of 0,2 in accordance with IEC 61869-3 will be provided at the assembly incomer. Default value : not required
Note on C119: Select the connection arrangement of the voltage transformer in gas insulated switchgear. Default value : manufacturer's standard
Note on C121: Specify the multi-function digital measuring devices accuracy class in accordance with IEC 60051-1
Note on C123: Specify where the protection relay manufacturer/type should be defined by the user. Default value : IED - manufacturer's standard
Note on C125: Select the termination type for incoming supply conductors. If "cables", specify details (1Core / 3Cores, conductor cross section area, number of cable runs) to design cable chamber size, gland plate material selection, termination arrangement, etc.
Note on C126: Specify the required incoming cable entry direction. This will be dependent on site cable routing.
Note on C127: Specify the termination details for outgoing supply conductors. Specify the details (1Core / 3Cores, conductor cross section area, number of cable runs) to design cable chamber size, gland plate material selection, termination arrangement, etc.
Note on C128: Specify the required outgoing cable entry direction. This will be dependent on site cable routing.
Note on C129: Gland plates are typically undrilled as cable sizes and entry points are often not finalized until well into construction. Cable transits are often used on pre-fabricated switchrooms, on offshore module, or if a gas or water seal is required. Default value : undrilled removable gland-plate
Note on C131: Specify the required auxiliary cable entry direction. This will be dependent on site cable routing.
Note on C132: Specify the quantity of installed spare control and auxiliary terminals for future use to be provided. Default value : 10 % spare
Note on C134: Specify where an integrated thermal monitoring system is required. Where "priced option" is selected, a price for this facility will be provided prior to enable the purchaser to make the decision of whether it will be required. Default value : not required
Note on C135: Specify where an integrated partial discharge monitoring system is required. Where "priced option" is selected, a price for this facility will be provided prior to enable the purchaser to make the decision of whether it will be required. Default value : not required
Note on C136: Specify where an integrated circuit breaker condition monitoring system is required. Where "priced option" is selected, a price for this facility will be provided prior to enable the purchaser to make the decision of whether it will be required. Default value : not required
Note on C137: Specify where motor condition monitoring hardware is to be installed in motor starter functional units. Final details will be agreed outside this specification. This element is used to alert the supplier of this requirement. Default value : not required.
Note on C138: Specify where additional data visualization such as mobile device access and cloud hosting is required. Use 'additional notes' to provide specific details where necessary. Default value : not required
Note on C139: Specify the condition monitoring to site system media required. Default value : not required
Note on C140: Specify the condition monitoring to site system protocol. Where other is specified, provide details in "additional notes" column. Default value :none
Note on C142: Select "other" if the operating company or the site has a default IED brand for operational and/or system integration commonality at that location. If "other" is selected, specify the IED manufacturer / IED range in the "additional" notes column. Default value : manufacturer's standard
Note on C143: Specify the communication media within the switchgear assembly for interface to the process control or industrial control system. If "multiple" or "other" is selected, provide details in the "Additional note" column and in the project drawings. Default value : manufacturer's standard
Note on C144: Specify the communication protocol within the PSC-assembly for the stated media interface to the process control or industrial control system. If "multiple" or "other is selected, provide details in the "Additional note" column and in the project drawing.
Note on C145: Parallel redundancy protocol or high-availability seamless redundancy (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. Select "other" to specify other redundancy protocols.
Note on C146: If required, specify the communication media within the PSC-assembly for interface to the electrical control and management system. Where "other" media is selected, provide details in the "additional notes" column. Default value : not required
Note on C147: If required, specify the communication protocol within the PSC-assembly for the stated media interface to the electrical control and management system. Where "other" protocol is selected , provide details in the "additional notes" column. Default value : not required
Note on C148: PRP or HSR (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. Use "other" to specify other redundancy protocols. Default value : not applicable
Note on C149: Not applicable if ECMS is not specified. Where required, this is an optional facility provided by the electrical control system / power management system to remotely edit an IEDs protection and logic settings, by a user with the correct system privileges. Default value : not applicable
Note on C151: Specify the interlocking/intertripping interface media required between switchgear assemblies. Default value : manufacturer's standard
Note on C152: A default of '"hardwired" is presumed for discrete hardwired interlocking/intertripping from the switchgear assembly to upstream or downstream switchboards but may be IED-to-IED communication or via the ECMS station bus. Default value : hardwired
Note on C154: Specify the IED to electrical power management system interface media. Where other is specified provide details in the "Additional notes" column. Default value : not required
Note on C155: If required, specify the communication protocol from IEDs via the stated media interface to the power management system. Where "other" protocol is specified provide details in the "Additional notes" column. Default value : not required
Note on C156: PRP or HSR (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. Use "other" to specify other redundancy protocols. Default value : not applicable
Note on C158: If required, specify the communication media within the switchgear assembly for interface to the generator control panel. Where "other" media is specified provide details in the "Additional notes" column. Default value : not required
Note on C159: If required, specify the communication protocol from IEDs via the stated media interface to the generator control panel. Where "other" protocol is specified provide details in the "Additional notes" column. Default value : not required
Note on C161: Specify the conformance class in accordance with IEC 62271-3:2015, 5.2.
Note on C162: Specify the availability class in accordance with IEC 62271-3. Default value : A2
Note on C163: Specify the network redundancy protocol in accordance with the site architecture. These are defined in IEC 62439-3.
Note on C165: Specify where partial discharge testing of the assembly is required.
Note on C166: Select where a simulation test is to be performed by the supplier to validate the electrical control and management system (ECMS) interfaces between the remote HMI and IEDs on the assembly. Test details to be agreed outside of this specification.
Note on C168: Specify where certification confirming compliance with IEC 62243-4-2 for automation and control system components is required.
Note on C170: Specify when an integrated internal arc fault detection system in accordance with IEC TS 63107 is required.
Note on C172: Specify the language used for all information to be provided. Where the language is other than English, this can be confirmed in the "Additional notes" column. Default value : English
Note on C174: Purchaser to advise the supplier when transport and storage conditions are outside those specified as site conditions. This may result in the requirement of additional preservation provision at the supplier's discretion.
Note on C175: Where the equipment integration site differs from the end usage site, associated transport/logistic options and conditions at the integration site this should be identified.
Note on C176: Specify where a load certified hoist to facilitate the removal of functional units and associated components with a mass of 25 kg or greater is to be provided. Default value : not required
Note on C177: Specify where a trolley to facilitate the transportation of functional units and associated components is required. Default value : not required
Note on C178: Select the means of safely handling the switchgear shipping section without damage when an overhead lifting means is not available. The enclosure structure will be strengthened for rolling on floor without deformation of the enclosure base.

## Supplement
Row |  | IOGP S-620D (2.01) Procurement Data Sheet for High-voltage Switchgear and Controlgear (IEC) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-620D (2.01) Procurement Data Sheet for
High-voltage Switchgear and Controlgear (IEC)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-620 Supplementary Specification to IEC 62271-200 for High-voltage Switchgear and Controlgear.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data