## Addendum 1
Date of issue:
June 2025
Affected publication:
IOGP S-620L, Information Requirements for High-voltage Switchgear and Controlgear (IEC), Second Edition, December 2022
ADDENDUM 1
This addendum (Version 2.01) replaces Edition 2.0 published in December 2022.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Worksheet | IR ID | Column | Update
| Definitions | S620-IR-66 | C - Description | Description added
| Definitions | S620-IR-69 | F - CFIHOS Code | CFIHOS code CFIHOS-70000451 added
| Definitions | S620-IR-76 | C - Description | CFIHOS code CFIHOS-70000447 added
| Definitions | S620-IR-79 | C - Description | Description amended
| Definitions | S620-IR-81 | F - CFIHOS Code | CFIHOS code CFIHOS-70000449 added
| Definitions | S620-IR-82 | C - Description | Description amended
|  |  | F - CFIHOS Code | CFIHOS code CFIHOS-70000449 added
| Definitions | S620-IR-83 | F - CFIHOS Code | CFIHOS code CFIHOS-70000449 added
| Requirements | S620-IR-84 | D - Typical Deliverable | Typical deliverable amended
| Definitions |  | F - CFIHOS Code | CFIHOS code CFIHOS-70000203 added
| Definitions | S620-IR-85 | F - CFIHOS Code | CFIHOS code CFIHOS-70000441 added
| Definitions | S620-IR-128 | F - CFIHOS Code | CFIHOS code CFIHOS-70000153 added
| Definitions | S620-IR-94 | F - CFIHOS Code | CFIHOS code CFIHOS-70000012 added
| Definitions | S620-IR-95 | F - CFIHOS Code | CFIHOS code CFIHOS-70000012 added
| Definitions | S620-IR-124 | F - CFIHOS Code | CFIHOS code CFIHOS-70000454 added
| Definitions | S620-IR-104 | F - CFIHOS Code | CFIHOS code CFIHOS-70000245 added
| Requirements | S620-IR-127 | D - Typical Deliverable | Typical deliverable amended
| Definitions |  | F - CFIHOS Code | CFIHOS code CFIHOS-70000239 added
| Definitions | Various | D - Reference | List of references amended

## Front & Preliminaries
[5 empty] | SPECIFICATION | June 2025
[5 empty] | IOGP S-620L | Version 2.01
ADDENDUM 1 TO SECOND EDITION (DECEMBER 2022)
Information Requirements for High-voltage Switchgear and Controlgear (IEC)
Revision history
| VERSION | DATE | PURPOSE
| 2.01 | June 2025 | Addendum 1
| 2 | December 2022 | Second Edition
| 1 | October 2018 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-620L (2.01) Information Requirements for High-voltage Switchgear and Controlgear (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
This second edition cancels and replaces the first edition published in October 2018. Due to technical writing requirements leading to extensive changes, this second edition should be treated as a new document.
IOGP S-620L (2.01) Information Requirements for High-voltage Switchgear and Controlgear (IEC)
Introduction
The purpose of this information requirements specification (IRS) is to define information requirements for the procurement of high-voltage switchgear and controlgear in accordance with IOGP S-620 for application in the petroleum and natural gas industries. The IRS defines the information requirements, including format, timing and purpose, for information to be provided by the supplier. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the specification (IOGP S-620), procurement data sheet (IOGP S-620D) and quality requirements specification (IOGP S-620Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification

## Instructions
IOGP S-620L (2.01) Information Requirements for
High-voltage Switchgear and Controlgear (IEC)
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS Structure Contents
| 1 | 'Front & Preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes / No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information Submission Abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS .
Column K — 'Translation Required' (Yes / No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable Formats
Column F — 'CFIHOS Document Type Code' relates to the CFIHOS document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3 below. Metadata listed below are as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The document master to which this revision is related |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification |  |  | The Export Control Rule that is applicable for the document revision (e.g., ECCN, EAR). |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
| Security classification |  |  | Indicates internal Owner-Operator access restriction applicable for the document |  |  | TBA
Table 3 — Supplier Deliverable Metadata

## Requirements
IOGP S-620L (2.01) Information Requirements for High-voltage Switchgear and Controlgear (IEC)
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Information Deliverable Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S620-IR-66 | Supplier master information schedule |  | Information deliverables list | No | For Information |  | - | - |  | -
S620-IR-67 | Delivery schedule |  | Delivery/production schedule | Yes | For Information |  | - | - |  | - | Preliminary with proposal
S620-IR-68 | Progress report |  | Progress report | No | For Information |  | - | - |  | -
S620-IR-69 | Quality plan | Required for CAS A, CAS B | Quality plan | - | - |  | - | - |  | - | Preliminary with proposal
S620-IR-71 | Sub-supplier delivery schedule |  | Delivery/production schedule | Yes | For Information |  | - | - |  | - | Preliminary with proposal
S620-IR-72 | Inspection and test plan (ITP) |  | Inspection and test plan (ITP) | Yes | For Acceptance |  | - | - |  | - | Preliminary with proposal
S620-IR-73 | Handling, shipping and storage procedure |  | Handling, shipping and storage procedure | No | For Acceptance |  | - | - |  | -
S620-IR-74 | Non-conformance records |  | Non-conformance records | No | For Information |  | - | - |  | -
S620-IR-75 | Concession request |  | Concession request | No | For Acceptance |  | - | - |  | -
S620-IR-76 | Obsolescence management plan |  | Obsolescence management plan | Yes | For Information |  | - | - |  | - | Preliminary with proposal
S620-IR-77 | IED configuration responsibilities | Where IEDs are included in scope | Authority matrix | Yes | For Information |  | - | - |  | - | Preliminary with proposal
Technical Information Deliverables
S620-IR-78 | Functional design specification |  | Functional design specification | Yes | For Information |  | - | - |  | -
S620-IR-79 | General arrangement details |  | General arrangement diagram | Yes | For Acceptance |  | - | - |  | - | Preliminary with proposal
S620-IR-80 | Foundation and Installation details |  | Installation diagram | No | For Information |  | - | - |  | -
S620-IR-81 | Current transformer sizing calculations |  | Curves and tables calculations | No | For Information |  | - | - |  | -
S620-IR-82 | Current transformer characteristics |  | Curves and tables calculations | No | For Information |  | - | - |  | -
S620-IR-83 | High-voltage protective devices characteristics and ratings |  | Curves and tables calculations | No | For Information |  | - | - |  | -
S620-IR-84 | Utility load schedule |  | Load list | No | For Information |  | - | - |  | -
S620-IR-85 | Heat dissipation calculation and loads |  | Heat dissipation calculation and loads | No | For Information |  | - | - |  | -
S620-IR-86 | Connection diagram |  | Connection diagram | No | For Information |  | - | - |  | -
S620-IR-87 | Switchgear I/O schedule | Where IEDs included in scope | Input, output list | No | For Information |  | - | - |  | -
S620-IR-88 | Functional logic diagram |  | Logic diagram | No | For Acceptance |  | - | - |  | -
S620-IR-89 | Switchgear single line diagram |  | Single line diagram | No | For Acceptance |  | - | - |  | -
S620-IR-126 | Gas compartment diagram | Where GIS switchgear is provided | Single line diagram | No | For Acceptance |  | - | - |  | -
S620-IR-128 | Arc duct or gas duct arrangement drawing |  | Arrangement drawing | No | For Acceptance |  | - | - |  | -
S620-IR-90 | Circuit and wiring diagram |  | Wiring diagram | No | For Acceptance |  | - | - |  | -
S620-IR-91 | Inter-panel wiring diagram |  | Connection diagram | No | For Information |  | - | - |  | -
S620-IR-125 | Inter-panel logic diagram |  | Logic diagram | No | For Acceptance |  | - | - |  | -
S620-IR-92 | Probability of failure on demand reliability data | Where SIL performance requirements are included in scope | Reliability, availability, safety integrity level calculation | No | For Information |  | - | - |  | -
S620-IR-93 | IED interrogation and programming software | Where IEDs included in scope | Application software | No | For Information |  | - | - |  | -
S620-IR-94 | Relay IED configuration files | Where IEDs included in scope | Configuration file | No | For Information |  | - | - |  | -
S620-IR-95 | IEC 61850 configuration files | Where IEDs included in scope with IEC 61850 interface to remote systems | Configuration file | No | For Information |  | - | - |  | -
S620-IR-123 | Manufacturer data sheet |  | Manufacturer data sheet | Yes | For Acceptance |  | - | - |  | -
S620-IR-96 | Installation manual |  | Installation manual | No | For Information |  | - | - |  | -
S620-IR-110 | Maintenance manual |  | Maintenance manual | No | For Information |  | - | - |  | -
S620-IR-111 | Operating manual |  | Operating manual | No | For Information |  | - | - |  | -
S620-IR-97 | Recommended spare part list (RSPL) |  | Spare part list | No | For Information |  | - | - |  | -
S620-IR-124 | Special tools list |  | Special tools list | No | For Information |  | - | - |  | -
S620-IR-98 | Chemical inventory and material safety data sheets |  | Manufacturer data sheet | No | For Information |  | - | - |  | -
S620-IR-99 | Bill of materials |  | Bill of materials | No | For Information |  | - | - |  | -
S620-IR-100 | Type test certificate |  | General certificate | No | For Information |  | - | - |  | -
S620-IR-101 | Lifting equipment test certificate | If lifting equipment included in scope | Lifting equipment test certificate | No | For Information |  | - | - |  | -
S620-IR-102 | Weight data sheet |  | Weight report | No | For Information |  | - | - |  | -
S620-IR-103 | ECMS simulation test procedure | If ECMS simulation included in scope | Test procedure | No | For Acceptance |  | - | - |  | -
S620-IR-104 | ECMS simulation test report | Where IEDs included in scope | Test report | No | For Information |  | - | - |  | -
S620-IR-105 | Routine verification test (FAT) procedure |  | Factory acceptance test (FAT) procedure | No | For Acceptance |  | - | - |  | -
S620-IR-106 | Routine verification test (FAT) results |  | Factory acceptance test (FAT) records | No | For Acceptance |  | - | - |  | -
S620-IR-108 | Site acceptance test (SAT) procedure |  | Site acceptance test (SAT) procedure | No | For Acceptance |  | - | - |  | - | To incorporate site interfaces
S620-IR-109 | Site acceptance test (SAT) report |  | Site acceptance test (SAT) records | No | For Acceptance |  | - | - |  | -
S620-IR-127 | Cyber security certification | Where specified | General certificate | No | For Information |  | - | - |  | -
S620-IR-107 | Certificate of conformity | Where class or regional certification is included in scope | Certificate of conformance | No | For Information |  | - | - |  | - | Marine class approval from an independent verification body
Purchase Order Specific Information Requirements

## Definitions
IOGP S-620L (2.01) Information Requirements for High-voltage Switchgear and Controlgear (IEC)
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Document Type Code — CFIHOS document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Deliverables
S620-IR-66 | Supplier master information schedule | Schedule of specific information deliverables developed by the manufacturer and accepted by the user to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines: a) information deliverable type, title/description b) unique identification (code/number) in the manufacturer's format unless agreed otherwise in the contract c) planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with the contractual agreements. | 10.1 | PDF | CFIHOS-70000099
S620-IR-67 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by manufacturer/suppliers. Schedule details typically** include;. a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Once agreed , changes to planned dates are subject to agreement by user. Progress against planned dates is measured and the schedule updated and reported to the user in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the manufacturer's standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S620-IR-68 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S620-IR-69 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the manufacturer, and when applicable sub-suppliers, to deliver the services or procured item(s) in conformance with the agreed requirements. ISO9001 Clause 8.1 and ISO10005 may be used to inform the development of quality plans for specific applications, processes or products.. |  | PDF | CFIHOS-70000451
S620-IR-71 | Sub-supplier delivery schedule | Definition of processes, products or services that will be externally provided and the controls to be applied by the [supplier] to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . Note: ISO9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. |  | PDF | CFIHOS-70000298
S620-IR-72 | Inspection and test plan (ITP) | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria, records and associated manufacturer, user and independent conformity assessment activities. ISO9001 Clause 8.1 and ISO10005 may be used to inform the development of inspection and test plans for specific processes and products. |  | PDF | CFIHOS-70000180
S620-IR-73 | Handling, shipping and storage procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a) Packaging requirements; contents, identification, size, weight and number of packages/container (s), b) special packing/unpacking/handling requirements c) storage location and requirements, d) preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. |  | PDF | CFIHOS-70000154
S620-IR-74 | Non-conformance records | Details of non-conformances raised by or to the manufacturer/sub suppliers against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the manufacturer in accordance with ISO9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a nonconforming condition are subject to agreement by the user in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S620-IR-75 | Concession request | Formal submission seeking user agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, user directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000389
S620-IR-76 | Obsolescence management plan | Plan defining the manufacturer's co-ordinated activities to direct and control the strategies for the identification and mitigation of the effects of obsolescence to the user, through all stages of the life of all components within the high-voltage switchgear and controlgear assembly. An example of the principles of this plan is defined within IEC 62402, Obsolescence management – Application guide. |  | PDF | CFIHOS-70000447
S620-IR-77 | IED configuration responsibilities | Responsibility matrix or flow chart detailing device configuration and set-point responsibilities including protection relay, IED generic configuration and IED functional logic files for the purpose of interface control between user and manufacturer during the development of the switchgear and controlgear assembly. | 6.113.1 | PDF | CFIHOS-70000023
Technical Information Deliverables
S620-IR-78 | Functional design specification | A document containing specific design data and performance requirements for the equipment. This document covers the design, available functionality and the hardware included in the scope. This document can also include images of hardware, topology sketches and extracts from general arrangement drawings in addition to text to provide a common understanding of the assemblies. To include motor starter and contactor feeder number of on-load operating cycles. Details to include integration with site systems and equipment interlocking/intertripping functionality. | E.3.1.7 | PDF | CFIHOS-70000244
S620-IR-79 | General arrangement details | The manufacturer's standard general arrangement drawing shall include, but not be limited to, the following information a. dimensions - main, overall and critical interface dimensions, clearances, b. internal arrangement - front, top, side, rear and internal/cross-section views, arc chute details, busbar arrangement, c. installation - lifting arrangement, mounting and base frame details, withdrawal and maintenance space, d. layout - elevation view with component deposition layout (external and internal), cable chamber/termination details (cable entry plate/MCT arrangement, cable routing and termination layout and clearances, etc.) e. interface - connections details, f. identification - tag/label/rating plate details, g. transport - shipping split details, weight, centre of gravity, h. reference - specifications, standards, project documents, supplier's support documents | 5.5, 6.103.2.4, 6.3.102, 6.4.5.2.6, 6.110.7, 6.116.1.1, 8.6.1, E.3.1.4 | PDF | CFIHOS-70000153
S620-IR-80 | Foundation and Installation details | The manufacturer's standard installation drawing showing; • Critical interface dimensions • Interface connections • Weight of assemblies, equipment and components • Centre of gravity • Withdrawal/installation and maintenance space. • Installation and mounting details • Lifting arrangement The drawing to reference to main specifications and standards. | 11.3 | PDF | CFIHOS-70000119
S620-IR-81 | Current transformer sizing calculations | Calculations to size the CT's, e.g. burden and accuracy class. | 6.110.1, 6.110.2, 6.110.3 | PDF | CFIHOS-70000449
S620-IR-82 | Current transformer characteristics | Characteristic curves for the current transformers show the relationship between the secondary excitation current and the secondary excitation voltage to identify the saturation voltage. | 6.110.1, 6.110.2, 6.110.3 | PDF | CFIHOS-70000449
S620-IR-83 | High-voltage protective devices characteristics and ratings | Time-current characteristics of high-voltage protection devices provided with the switchgear and controlgear assembly, e.g. motor-starter fuse and protection relay curves. | 6.113.5 | PDF | CFIHOS-70000449
S620-IR-84 | Utility load schedule | Summarises the normal and transient DC and AC utility loads of the switchgear for the purpose of sizing external power provision. | 11.1 | PDF | CFIHOS-70000203
S620-IR-85 | Heat dissipation calculation and loads | This document contains the calculation by the manufacturer to arrive at the heat load produced by the switchgear to enable HVAC sizing and includes load factors and type of load provided to the manufacturer to produce accurate calculation | 11.1 | PDF | CFIHOS-70000441
S620-IR-86 | Connection diagram | Drawing providing information about the external physical connections per functional unit including hydraulic, pneumatic and electrical connections. | 6.114.2.1 | PDF | CFIHOS-70000055
S620-IR-87 | Switchgear I/O schedule | Schedule of tags identifying IED programmable addresses and hardwired signal interfaces for all functional units within the switchgear and control gear assembly. | 11.1 | PDF | CFIHOS-70000179
S620-IR-88 | Functional logic diagram | Control logic embedded in IEDs (e.g. protection relays) that is developed by the manufacturer to implement the requirements of the user diagrams and associated protection relay settings. | 6.115.2.2, 6.116.1.5, E.3.1.1, E.3.1.2, E.3.3.1, E.3.3.2, E.3.3.5, E.3.3.6 | PDF | CFIHOS-70000248
S620-IR-89 | Switchgear single line diagram | Drawing detailing major items of equipment, including protection devices per functional unit using IEC 60617 standard symbols and/or ANSI C37.2 device function numbers per switchgear and controlgear assembly. | 11.1 | PDF | CFIHOS-70000371
S620-IR-126 | Gas compartment diagram | A pictorial representation of the main elements and functions of the gas system illustrating compartmentalization, locations of pressure relief discs/ rupture disc, location of the valves, SF6 gauges, etc. | 6.103.2.2 | - | CFIHOS-70000371
S620-IR-128 | Arc duct or gas duct arrangement drawing | An overall representation of the switchgear ducting arrangement, showing how ionized gasses are safely evacuated. | 7.105.6 | - | CFIHOS-70000153
S620-IR-90 | Circuit and wiring diagram | Drawing detailing in schematic form the functional unit in respect of electrical and instrument circuit connections based on the principles in IEC 61082-1, Preparation of documents used in electrotechnology – Part 1: Rules. The circuit(s) to be shown to the extent necessary for the understanding of the circuit(s) functions and how the components are interconnected. The drawing includes details of all device hardwired connections within the functional unit and external interfaces to terminal blocks. Hardwired connections internal to the functional unit, devices and external interface terminal blocks are to be identified as per manufacturers standard. | 5.9, 6.4.1.4, 6.3.101, 6.10, 6.108.2.15, 6.109.11, 6.109.15, 6.109.16, 6.110.5, 6.110.6, 6.112.2.4, 6.112.4, 6.114.2.7, 8.6.3, 8.6.4, E.3.1.6 | PDF | CFIHOS-70000268
S620-IR-91 | Inter-panel wiring diagram | Wiring diagram detailing the control and auxiliary interfaces between functional units within the switchgear and controlgear assembly. The wiring diagram identifies functional unit inter-connection and field run connections to be made during assembly of transport units. | 11.1 | PDF | CFIHOS-70000055
S620-IR-125 | Inter-panel logic diagram | A representation of circuit breaker, disconnector, and switch relationships, with respect to interlocking, intertripping and blocking actions, taking into account switchgear status and monitoring (such as gas level). Where an executive action is taken by the internal switchgear control system, without a command from an external system, this will be included. This can be provided in the form of a matrix. | 6.3.105.3 | PDF | CFIHOS-70000248
S620-IR-92 | Probability of failure on demand reliability data | Identifies reliability input data for functional unit and protection relay probability of failure on demand (PFD) to enable user to perform functional safety requirements assessments to IEC 61511-1. | 6.115.1 | PDF | CFIHOS-70000312
S620-IR-93 | IED interrogation and programming software | Software and special communication media required to access and program the relays and programmable devices in the high-voltage switchgear. | 6.113.1 | Native | CFIHOS-70000012
S620-IR-94 | Relay IED configuration files | Relay and programmable configuration devices files (native files and PDF) | 6.113.1 | Native | CFIHOS-70000012
S620-IR-95 | IEC 61850 configuration files | Substation Configuration Description (SCD) or Configured IED Description (CID) files | 6.113.1 | Native | CFIHOS-70000012
S620-IR-123 | Manufacturer data sheet | To include confirmation of compliance with S-620D by providing actual values of switchgear specification and all other information in accordance with IEC 62271-1:2021, 10, and IEC 62271-200:2021,10. | 10.3 | PDF | CFIHOS-70000416
S620-IR-96 | Installation manual | The manufacturer's standard information manual. This document includes sufficient information to install the equipment. It is acknowledged this may be provided as part of an overall IOM manual. | 11.3 | PDF | CFIHOS-70000181
S620-IR-110 | Maintenance manual | The manufacturer's standard maintenance manual. This document includes sufficient information to maintain the equipment. It is acknowledged this may be provided as part of an overall IOM manual. If required a supplementary sheet can be added identifying components that are not suitable for 5 years continuous operation without inspection or replacement under the user specified service conditions. This will include maintenance of assembly subcomponents. | 6.116.1.3 | - | CFIHOS-70000206
S620-IR-111 | Operating manual | The manufacturer's standard operating manual. This document includes information to operate the assembly and subcomponents. This document includes sufficient information for troubleshooting. It is acknowledged this may be provided as part of an overall IOM manual. | 6.109.12, 6.109.13, 6.109.14, 6.116.4, E.3.1.5 | - | CFIHOS-70000228
S620-IR-97 | Recommended spare part list (RSPL) | Identified products which may require replacement are listed in a spare parts list identified and described so that the necessary spare, the whole item or parts can be obtained. The spare parts list includes: - reference to project documentation (e.g. drawing number and position number); - the manufacturer's catalogue/unique and unambiguous parts number; - for standardized parts: the real manufacturer's name and catalogue/unique and unambiguous parts number. - reference to tag (where applicable) The list includes equipment manufacturer's recommendation for commissioning and two years operational spares. | 11.1 | PDF | CFIHOS-70000374
S620-IR-124 | Special tools list | The special tools list identifies special tool and equipment necessary for handling, installation, dismantling, operation and maintenance of the switchgear, including circuit breaker operating handles, earthing switch operating handles and software interrogation cables, earthing truck (where specified), lifting hoist (where specified) and circuit breaker trolley (where specified). | 11.6.1 | PDF | CFIHOS-70000454
S620-IR-98 | Chemical inventory and material safety data sheets | A structured form containing information on the safety, health and environmental protection aspects of the chemical, including protective measures and emergency actions. Safety Data Sheets (SDS) to be in accordance with local/national regulations and in the official operating language of the plant, or in English if accepted by local authorities. A collection of SDS to be delivered to User for chemicals delivered as part of equipment, as first fill or used for preservation before operation. Exceptions are • grease • fat • surface preservatives • coatings • oils in volume per equipment below 10 litres. The report includes one SDS per unique chemical trade name. The report to include a cross reference table with each unique chemical trade name, equipment tag number(s) and SDS file name. | 13 | PDF | CFIHOS-70000416
S620-IR-99 | Bill of materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and references to specifications including sub-suppliers and associated purchase orders. To include OEM part numbers for components not manufactured by the supplier. | 11.6.1, 11.6.3, E.4.1.1 | PDF | CFIHOS-70000028
S620-IR-100 | Type test certificate | A document providing objective evidence that the equipment is compliant to relevant standards. To include equipment designation, manufacturer, testing authority name and address, specific year and edition of the IEC used to perform verification and a summary of the proving tests performed. | 6.16, 6.108.2.1, 6.108.4.2, 6.108.4.3, 6.110.4 | PDF | CFIHOS-70000239
S620-IR-101 | Lifting equipment test certificate | Lifting equipment test certificate in relation switchgear load certified hoist | 11.3 | PDF | CFIHOS-70000432
S620-IR-102 | Weight data sheet | Document with weight of individual shipping sections | 11.3 | PDF | CFIHOS-70000359
S620-IR-103 | ECMS simulation test procedure | User-agreed functional test procedure of the ECMS or its parts using the parameter set for the planned application including communication interfaces with integrated control and safety systems. | Figure F.1 | PDF | CFIHOS-70000332
S620-IR-104 | ECMS simulation test report | Results from the execution of ECMS simulation test procedure including communication interfaces with integrated control and safety systems. | Figure F.1 | PDF | CFIHOS-70000245
S620-IR-105 | Routine verification test (FAT) procedure | Procedure documenting the manufacturers recommended testing activities and acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Procedure to define test set-up and test equipment. | 8.102, 8.6.1, 8.6.2, 8.6.3, 8.6.4, E.3.1.3, E.3.4 | PDF | CFIHOS-70000427
S620-IR-106 | Routine verification test (FAT) results | This document records and documents all results from the activities performed in accordance with the FAT procedure. Include any observation rework or retesting. | 8.102, 8.6.1, 8.6.2, 8.6.3, 8.6.4, E.3.1.3, E.3.4 | PDF | CFIHOS-70000429
S620-IR-108 | Site acceptance test (SAT) procedure | Procedure documenting the manufacturers recommended site tests including discrete functional unit and overall assembly, electrical, mechanical, protection relay and IEDs. | 8.104 | PDF | CFIHOS-70000428
S620-IR-109 | Site acceptance test (SAT) report | Site acceptance test report including discrete functional unit and overall assembly, electrical, mechanical, protection relay and IED tests. | 8.104 | PDF | CFIHOS-70000430
S620-IR-127 | Cyber security certification | Certification confirming compliance with IEC 62243-4-2 for industrial automation and control system components. | 6.4.5.1 | - | CFIHOS-70000239
S620-IR-107 | Certificate of conformity | The manufacture's or other party's confirmation that the product is designed, manufactured and tested as specified. To be delivered according to applicable authorities requirements. An example is marine class approval of the switchgear | 6.4.3.4.2, 6.4.4.3, 6.101, 6.106, 6.108.4.1, 6.108.4.4, 6.108.4.5, 6.109.1, 6.109.2, 6.109.3, 6.109.4, 6.109.5, 6.109.6, 6.110.1, 6.110.2, 6.110.3, 6.110.9, 6.111.1, 6.112.1.1, 6.112.2.3, 6.112.2.6, 6.112.2.8, 6.112.3, 6.112.4.1, 6.113.1, 6.113.5, 6.114.2.9, 6.115.1, 6.115.2.1 | PDF | CFIHOS-70000013
Purchase Order Specific Information Requirements

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
-