## Addendum 1
Date of issue:
June 2025
Affected publication:
IOGP S-720D, Data Sheet for Transformers, First Edition, December 2020
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in December 2020.
Due to the extent of updates, this addendum should be treated as a new document.

## Front & preliminaries
[5 empty] | SPECIFICATION | June 2025
[5 empty] | IOGP S-720D | Version 1.01
ADDENDUM 1 TO FIRST EDITION (DECEMBER 2020)
Data Sheet for Transformers
Revision history
| VERSION | DATE | PURPOSE
| 1.01 | June 2025 | Addendum 1
| 1 | December 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-720D (1.01) Data Sheet for Transformers
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-720D (1.01) Data Sheet for Transformers
Introduction
The purpose of this equipment data sheet is to define purchaser specific requirements for the procurement of transformers in accordance with IOGP S-720 for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification (IOGP S-720), information requirements specification (IOGP S-720L) and quality requirements specification (IOGP S-720Q) which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet

## Liquid Immersed Transformers
Row | IOGP S-720D (1.01) Data Sheet for Transformers Liquid Immersed Transformers |  |  |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | 1. General
6 |  | Equipment identifier : | input data
7 |  | Quantity : | input data
8 | 9.3 | Type of liquid preservation system : | freely breathing conservator type |  |  |  | select | freely breathing conservator type | conservator with bladder or diaphragm type | inert gas pressure type | sealed type with gas cushion | completely sealed type
9 | 4.1,5.7.1,** | Service : | select |  |  |  | select | power transformer | lighting and small power transformer | unit transformer | generator transformer | auto-transformer | reactor | earthing transformer | mobile service transformer.
10 |  | Conformity assessment system : | D |  |  |  | select | A | B | C | D
11 |  | 2. Environmental conditions
12 | 5.5(Para,** | Altitude (if more than 1000m or 3280ft) : | input data | select |  |  | select | m | ft
13 | 4.2,** | Minimum ambient temperature : | input data | select |  |  | select | °C | °F
14 | 4.2,** | Maximum ambient temperature : | input data | select |  |  | select | °C | °F
15 | 4.2,** | Yearly average ambient temperature : | input data | select |  |  | select | °C | °F
16 | 5.5(Para,** | Design ambient temperature (if more than 40 °C or 104 °F ) : | input data | select |  |  | select | °C | °F
17 | 4.2,** | Relative humidity at maximum operating temperature (if more than 90 %) : | input data | %
18 | 4.2 | Climatic conditions (K) for liquid immersed transformer : | 4K23 |  |  |  | select | 4K23 | 4K24 | 4K25 | 4K26 | 4K27
19 | 4.2 | Special climatic conditions (Z) for liquid immersed transformer : | input data
20 | 4.2 | Biological conditions (B) for liquid immersed transformer : | 4B1 |  |  |  | select | 4B1 | 4B2 | 4B3
21 | 4.2 | Chemically active substances (C) for liquid immersed transformer : | 4C5 |  |  |  | select | 4C1 | 4C2 | 4C3 | 4C4 | 4C5 | 4CX
22 | 4.2 | Mechanically active substances (S) for liquid immersed transformer : | 4S13 |  |  |  | select | 4S10 | 4S11 | 4S12 | 4S13
23 | 4.2 | Mechanical conditions (M) for liquid immersed transformer : | 4M11 |  |  |  | select | 4M10 | 4M11 | 4M12
24 | 9.6.18.1,9.6.18.3 | Corrosion class : | C3 |  |  |  | select | C3 | C4 | C5 | CX
25 | ** | Seismic zone as per IEC 60721-2-6, figure 5 : | Zone 2 |  |  |  | select | zone 2 | zone 3 | zone 4
26 | 4.2,5.7.4.2(Para,** | Location : | select |  |  |  | select | indoor | outdoor | offshore fixed | offshore mobile
27 | ** | Unusual service conditions : | No |  |  |  | select | Yes | No
28 | 5.7.3 | Sound power level : | input data | dB(A)
29 |  | 3. Hazardous area classification
30 | 4.2,** | Hazardous area classification zone : | non hazardous |  |  |  | select | non hazardous | zone 1 | zone 2
31 | 4.2,** | Hazardous area classification gas group : | select |  |  |  | select | IIA | IIB | IIC
32 | 4.2,** | Hazardous area classification temperature class : | input data
33 |  | 4. Technical data
34 |  | 4.1 Electrical system data
35 | 5.4.1(Para,** | Rated voltage (HV) : | input data | kV
36 | 5.4.1(Para | Rated voltage (LV) : | input data | kV
37 | 5.4.1(Para | Rated voltage (tertiary) : | input data | kV
38 | 5.4.2(Para,** | Rated frequency : | 50 | Hz |  |  | select | 50 | 60
39 | **,A.1.2(a | System short circuit apparent power : | input data | MVA
40 | 6.4.3.e | Minimum full load power factor : | input data
41 | **,A.1.2(a | Supply voltage harmonic content : | input data | %
42 |  | 4.2 Transformer/reactor data
43 |  | 4.2.1 General
44 |  | Power frequency withstand voltage
45 | ** | Power frequency withstand voltage - HV winding : | input data | kV
46 | ** | Power frequency withstand voltage - LV winding : | input data | kV
47 | ** | Power frequency withstand voltage - tertiary winding : | input data | kV
48 | ** | Power frequency withstand voltage - neutral terminal : | input data | kV
49 |  | Lightning impulse withstand voltage
50 | ** | Lightning impulse withstand voltage - HV winding : | input data | kV
51 | ** | Lightning impulse withstand voltage - LV winding : | input data | kV
52 | ** | Lightning impulse withstand voltage - tertiary winding : | input data | kV
53 | ** | Lightning impulse withstand voltage - neutral terminal : | input data | kV
54 | 5.7.2(Para,7.1.1,** | Number of phases : | 3 |  |  |  | select | 1 | 2 | 3
55 | 6.4.3.a,** | Direction of power flow : | step-down |  |  |  | select | step-up | step-down | bi-directional
56 | 7.1.5,5.7.2(Para,7.1.1,** | Connection and phase displacement symbol (vector group) : | input data
57 | **,A.1.2(a,B.4(Para | Percentage impedance on air natural rating at principal tap : | input data | %
58 | 5.7.2(Para | High limit for zero sequence impedance : | input data | ohms/ph
59 | 5.7.2(Para | Low limit for zero sequence impedance : | input data | Ohms/ph
60 | 5.1.1,** | Rated power in air natural mode (HV) : | input data | kVA
61 | 5.1.1,** | Rated power in air natural mode (LV) : | input data | kVA
62 | 5.1.1,** | Rated power in air natural mode (tertiary) : | input data | kVA
63 | 5.1.1,5.1.3(Para,** | Rated power in forced cooling mode (HV) : | input data | kVA
64 | 5.1.1,5.1.3(Para,** | Rated power in forced cooling mode (LV) : | input data | kVA
65 | 5.1.1,5.1.3(Para,** | Rated power in forced cooling mode (tertiary) : | input data | kVA
66 | 5.4.3(Para | Variation in V/Hz ratio from no load to rated load when exceeding 105 % : | input data | %
67 | **,A.1.2(a,A.2 | Parallel operation : | select |  |  |  | select | Yes | No
68 | 5.1.1 | Requirement of 1.8 times overloading for transformer feeding a group of motors : | select |  |  |  | select | Yes | No
69 | 5.8,** | Insulating liquid : | Fully inhibited high grade mineral oil |  |  |  | select | mineral oil | fully inhibited high grade mineral oil | synthetic ester | natural ester | silicon oil
70 | **,A.1.2(a,Table 1 | Tolerance on total losses when not in accordance with IEC 60076-1 : | input data | %
71 | 6.5(Para,**,A.1.2(a,Table 1 | Tolerance on impedance value when not in accordance with IEC 60076-1 : | input data | %
72 |  | 4.2.2 Neutral terminal
73 | 9.4(Para | Level of DC current in neutral : | input data | %
74 | ** | Transformer neutral earthing for HV winding : | select |  |  |  | select | solid | ungrounded | resistance grounded | earthing transformer
75 | ** | Transformer neutral earthing for LV winding : | select |  |  |  | select | solid | ungrounded | resistance grounded | earthing transformer
76 | ** | Transformer neutral earthing for tertiary winding : | select |  |  |  | select | solid | ungrounded | resistance grounded | earthing transformer
77 | 9.2 | Sizing of the low voltage neutral terminal : | input data | %
78 |  | 4.2.3 Winding
79 | ** | Winding conductor material : | select |  |  |  | select | aluminum | copper
80 | 5.7.2(Para | Requirement of delta connected stabilizing winding : | select |  |  |  | select | Yes | No
81 | 5.7.2(Para | Method of earthing of delta connected stabilizing winding : | Solidly grounded |  |  |  | select | solidly grounded | ungrounded
82 | ** | Winding class of insulation : | A |  |  |  | select | A | B | F | H
83 | ** | Non-uniform (graded) insulation : | select |  |  |  | select | Yes | No
84 | ** | High temperature insulation : | select |  |  |  | select | Yes | No
85 | A.1.2(a | Thermally upgraded paper : | select |  |  |  | select | Yes | No
86 |  | 4.2.4 Termination
87 | **,A.1.2(a | Main external termination details (HV) : | select |  |  |  | select | exposed bushings | busduct | gas insulated busduct | cable bus | cable box | plug-in connection
88 | **,A.1.2(a | Main external termination details (LV) : | select |  |  |  | select | exposed bushings | busduct | gas insulated busduct | cable bus | cable box | plug-in connection
89 | **,A.1.2(a | Main external termination details (tertiary) : | select |  |  |  | select | exposed bushings | busduct | gas insulated busduct | cable bus | cable box | plug-in connection
90 | **,A.1.2(a | Main external termination details (neutral) : | select |  |  |  | select | exposed bushings | busduct | gas insulated busduct | cable bus | cable box | plug-in connection
91 | **,A.1.2(a | Cable box type : | select |  |  |  | select | air insulated | liquid insulated | gas insulated
92 |  | Direction of cable entry (HV) : | bottom entry |  |  |  | select | top entry | bottom entry | side entry
93 |  | Direction of cable entry (LV) : | bottom entry |  |  |  | select | top entry | bottom entry | side entry
94 | ** | Main cable box design : | select |  |  |  | select | Phase segregated | insulated busbar | supplier standard
95 | ** | Cable type : | select |  |  |  | select | bare conductor | insulated
96 | ** | Number of cables (HV) : | input data
97 | ** | Number of cables (LV) : | input data
98 | ** | Number of cables (tertiary) : | input data
99 | 9.6.11.1.4,** | Cable conductor size (HV) : | input data | select |  |  | select | mm² | in²
100 | 9.6.11.1.4 | Cable conductor size (LV) : | input data | select |  |  | select | mm² | in²
101 | 9.6.11.1.4 | Cable conductor size (tertiary) : | input data | select |  |  | select | mm² | in²
102 | 9.6.11.1.4,** | Number of cores per cable (HV) : | input data
103 | 9.6.11.1.4 | Number of cores per cable (LV) : | input data
104 | 9.6.11.1.4 | Number of cores per cable (tertiary) : | input data
105 | 9.6.11.1.4,** | Number of cables per phase (HV) : | input data
106 | 9.6.11.1.4 | Number of cables per phase (LV) : | input data
107 | 9.6.11.1.4 | Number of cables per phase (tertiary) : | input data
108 | 5.6(Para,** | Separate neutral terminal box : | select |  |  |  | select | Yes | No
109 | 9.6.9.5,** | Canopy required for cable box : | select |  |  |  | select | Yes | No
110 | ** | Busduct type : | select |  |  |  | select | air insulated | gas insulated | sandwich type | cast resin
111 | ** | Bushings
112 | ** | Type of bushings (HV) : | select |  |  |  | select | polymer | porcelain | other
113 | ** | Type of bushings (LV) : | select |  |  |  | select | polymer | porcelain | other
114 | ** | Type of bushings (tertiary) : | select |  |  |  | select | polymer | porcelain | other
115 | ** | Type of bushings (neutral) : | select |  |  |  | select | polymer | porcelain | other
116 |  | 4.2.5 Tap changer
117 | 6.1(Para,6.4.1(Para,** | Tap changer required and type : | select |  |  |  | select | No | OLTC | DETC | bolted links
118 | 6.4.2.a,6.4.3.c | Voltage variation required on: : | select |  |  |  | select | HV | LV
119 | ** | Type of de-energized tap changer (DETC) : | hand operated |  |  |  | select | hand operated | motor operated
120 | 9.6.17.2.2 | Tap changer switching medium : | select |  |  |  | select | vacuum | liquid
121 | 6.2.a,6.2.b,6.2.c | Category of voltage variation : | CFVV |  |  |  | select | CFVV | VFVV | CbVV
122 | 6.4.1(Para,6.4.2.b,6.4.3.b,6.4.3.c,**,B.4(Para | Tapping range : | input data | %
123 | 6.4.1(Para,6.4.2.b,6.4.3.b,6.4.3.c,** | Number of tapping positions : | input data
124 | 6.4.3.b | Principal tapping position : | select |  |  |  | select | symmetrical | asymmetrical
125 | 6.3 | Maximum current tapping position : | input data
126 | 9.6.17.3.4 | Remote tap-changer cabinet for OLTC : | select |  |  |  | select | Yes | No
127 |  | 4.2.6 Cooling
128 | 5.2,5.1.3(Para,** | Type of cooling : | select |  |  |  | select | ONAN | ONAF | OFAF | OFWF | ODAF | ODWF | KNAN | KNAF | KFAF | KFWF | KDAF | KDWF
129 | 5.1.3(Para,9.3,A.1.2(a | Temperature rise of insulating liquid when not in accordance with IEC 60076-2 : | input data | select |  |  | select | °C | °F
130 | 5.1.3(Para,A.1.2(a | Temperature rise of winding when not in accordance with IEC 60076-2 or IEC 60076-11 : | input data | select |  |  | select | °C | °F
131 | 4.2 | Cooling water inlet temperature when not in accordance with IEC 60076-2 and IEC 60076-11 : | input data | select |  |  | select | °C | °F
132 | 5.2 | Provision for mounting of cooling fans : | No |  |  |  | select | Yes | No
133 | ** | AF fan motor cabinet : | on transformer body |  |  |  | select | on transformer body | self standing
134 |  | 4.2.7 Miscellaneous requirements
135 |  | a. Construction
136 | ** | Type of cover for liquid immersed transformer and reactor : | select |  |  |  | select | bolted | welded
137 | ** | Surface finish of tank and radiators : | select |  |  |  | select | hot dip galvanized | zinc coated
138 | 9.6.18.1 | Painting class required : | M |  |  |  | select | L | M | H | VH
139 | ** | Paint shade : | select |  |  |  | select | Supplier default | Other
140 |  | b. Interface
141 | ** | Auxiliary supply voltage details for cooling fans : | input data | V
142 | ** | Auxiliary supply voltage details for RTCC : | input data | V
143 | 8.3 | Requirement of current transformer in neutral terminal box : | select |  |  |  | select | Yes | No
144 | ** | Current transformer ratio : | input data | A
145 | ** | Current transformer accuracy class : | select |  |  |  | select | 0.5 | 1 | 1.5 | other
146 | ** | Current transformer burden : | input data | VA
147 |  | c. Transport
148 | 5.7.4.1,A.1.2(a | Limiting transportation dimensions (height) : | input data | select |  |  | select | mm | in.
149 | 5.7.4.1,A.1.2(a | Limiting transportation dimensions (width) : | input data | select |  |  | select | mm | in.
150 | 5.7.4.1,A.1.2(a | Limiting transportation dimensions (depth) : | input data | select |  |  | select | mm | in.
151 | 5.7.4.1,A.1.2(a | Limiting transportation weight : | input data | select |  |  | select | kg | lb
152 | ** | Impact recorder requirement during transportation : | select |  |  |  | select | Yes | No
153 | 5.7.4.2(Para | Acceleration in excess of 1 g during transportation : | select |  |  |  | select | Yes | No
154 |  | 4.3 Reactor specific requirements
155 | ** | Application : | select |  |  |  | select | shunt reactor | current limiting reactor | neutral earthing transformer | arc suppression reactor | discharge reactor
156 | ** | Rated current : | input data | A
157 | ** | Rated short circuit current : | input data | A
158 | ** | Time to withstand rated short circuit current : | input data | s
159 | 6.5(Para,** | Impedance at rated voltage and current : | input data | Ohms
160 |  | 5. Accessories
161 | 9.1.2,** | Lifting lugs : | select |  |  |  | select | Yes | No
162 | 9.3,** | Silica gel breather for main tank : | select |  |  |  | select | Yes | No
163 | ** | Type of silica gel breather : | select |  |  |  | select | manual | self regenerating
164 | **,Annex F(Para 1,Table F.1 | Liquid level indicator : | select |  |  |  | select | Yes | No
165 | **,Annex F(Para 1,Table F.1 | Liquid level gauge with alarm and trip contacts : | Yes |  |  |  | select | Yes | No
166 | 9.6.3.4,9.6.3.5,**,Annex F(Para 1,Table F.1 | Buchholz relay with alarm and trip contacts : | select |  |  |  | select | Yes | No
167 | 9.6.1.1 | Pressure relief device for OLTC : | select |  |  |  | select | Yes | No
168 | 9.6.10.3.2 | Pressure relief device for liquid filled cable box : | select |  |  |  | select | Yes | No
169 | 9.6.1.3 | Facility for directing emissions of liquid from the relief device in the direction specified : | select |  |  |  | select | Yes | No
170 | ** | Sudden pressure relay : | No |  |  |  | select | Yes | No
171 | **,Annex F(Para 1,Table F.1 | Liquid temperature Indicator with alarm and trip contacts : | select |  |  |  | select | Yes | No
172 | **,Annex F(Para 1,Table F.1 | Winding temperature indicator with alarm and trip contacts : | select |  |  |  | select | Yes | No
173 | **,Annex F(Para 1,Table F.1 | Winding temperature measurement type : | PTC thermistor |  |  |  | select | Not required | PTC thermistor | PT100 RTD
174 | ** | Cooling fans : | select |  |  |  | select | Yes | No
175 | ** | Redundancy of cooling system : | select |  |  |  | select | Yes | No
176 | **,Annex F(Para 1,Table F.1 | Control panel for fan starters (for AF type transformer) : | select |  |  |  | select | Yes | No
177 | ** | HV cable box : | select |  |  |  | select | Yes | No
178 | ** | LV cable box : | select |  |  |  | select | Yes | No
179 | ** | Tertiary cable box : | select |  |  |  | select | Yes | No
180 | 9.6.13,** | Surge arrester requirement : | select |  |  |  | select | Yes | No
181 | 9.6.13 | Surge arrester class : | select |  |  |  | select | Station class | Distribuition class
182 | Annex F(Para 1 | Requirement of online dissolved gas analysis (DGA) : | select |  |  |  | select | Yes | No
183 | Annex F(Para 1 | Requirement of fiber optic temperature sensing : | select |  |  |  | select | Yes | No
184 | Annex F(Para 1 | Number of channels of fiber optic temperature sensor : | input data
185 | 9.6.6.2 | Core earthing terminals at accessible location. : | select |  |  |  | select | Yes | No
186 | 9.6.6.3,** | Earthing cable lug size : | input data | mm
187 | A.1.2(a | Provision for connection of portable earthing device to the air insulated terminals for voltages above 1 kV : | select |  |  |  | select | Yes | No
188 | A.1.2(a | Infra red-inspection window for cable box for dry type transformer/reactor : | select |  |  |  | select | Yes | No
189 | 9.3 | Alarm contact for diaphragm failure for transformer with diaphragm in conservator : | No |  |  |  | select | Yes | No
190 | ** | Bi-directional rollers : | select |  |  |  | select | Yes | No
191 | 4.2 | Anti-condensation heater for cable box : | select |  |  |  | select | Yes | No
192 | 9.6.17.3.5 | Anti-condensation heater for remote tap-changer cabinet : | select |  |  |  | select | Yes | No
193 | 9.1.2. | Requirement of ladder : | select |  |  |  | select | Yes | No
194 | Table F.1 | Partial discharge monitoring : | not required |  |  |  | select | not required | required
195 | Table F.1 | Insulating liquid temperature monitoring : | not required |  |  |  | select | not required | required
196 | Table F.1 | Winding temperature monitoring : | not required |  |  |  | select | not required | required
197 | Table F.1 | Cable termination thermal monitoring : | not required |  |  |  | select | not required | required
198 | Table F.1 | Moisture in oil monitoring : | not required |  |  |  | select | not required | required
199 |  | Portable earthing device for plug in bushings : | not required |  |  |  | select | required | not required
200 |  | 6. Testing requirements
201 | 11.1.3.a | Temperature rise test : | select |  |  |  | select | Yes | No
202 | 6.6.b | Temperature rise test at tapping other than the maximum current tapping : | select |  |  |  | select | Yes | No
203 | 11.1.3.d | Power consumption of fans and liquid pump motors : | select |  |  |  | select | Yes | No
204 | 11.1.3.b,A.1.2(a | Dielectric type tests (lightning impulse) : | No |  |  |  | select | Yes | No
205 | 11.1.3.c | Sound level test : | select |  |  |  | select | Yes | No
206 | 11.1.3.e | Measurement of no-load loss and current at 90 % and 110 % of rated voltage : | select |  |  |  | select | Yes | No
207 | 11.1.4.a,A.1.2(a | Dielectric special tests (see table 1, IEC 60076-3) : | No |  |  |  | select | Yes | No
208 | 11.1.4.b,A.1.2(a | Winding hot-spot temperature-rise measurements : | select |  |  |  | select | Yes | No
209 | 11.1.4.c,A.1.2(a | Determination of capacitances windings-to-earth and between windings : | select |  |  |  | select | Yes | No
210 | 11.1.4.e,A.1.2(a | Determination of transient voltage transfer characteristics : | select |  |  |  | select | Yes | No
211 | 11.1.4.f,A.1.2(a | Measurement of zero-sequence impedance : | select |  |  |  | select | Yes | No
212 | 11.1.4.g,A.1.2(a | Short-circuit withstand test : | select |  |  |  | select | Yes | No
213 | 11.1.4.i,A.1.2(a | Vacuum deflection test : | select |  |  |  | select | Yes | No
214 | 11.1.4.j,A.1.2(a | Pressure deflection test : | select |  |  |  | select | Yes | No
215 | 11.1.4 | Pressure deflection test for OLTC tank : | select |  |  |  | select | Yes | No
216 | 11.1.4.k,A.1.2(a | Vacuum tightness test : | select |  |  |  | select | Yes | No
217 | 11.1.4 | Vacuum tightness test for OLTC tank : | select |  |  |  | select | Yes | No
218 | 11.1.4.l,A.1.2(a | Measurement of frequency response : | select |  |  |  | select | Yes | No
219 | 11.1.4.m,A.1.2(a | Check of external coating : | select |  |  |  | select | Yes | No
220 | A.1.2(a | Measurement of dissolved gasses before and after dielectric tests : | select |  |  |  | select | Yes | No
221 | 11.1.4.o,A.1.2(a | Mechanical test : | select |  |  |  | select | Yes | No
222 | 11.1.4 | Simulated transformer/motor on load start test for unit transformer : | select |  |  |  | select | Yes | No
223 | 11.1.4 | Routine test for Ex 'P' type transformer in accordance with IEC 60079-13 : | select |  |  |  | select | Yes | No
224 | 11.1.4 | Routine tests for Ex 'O' type transformer in accordance with IEC 60079-6 : | select |  |  |  | select | Yes | No
Note on C6: Specify equipment tag number
Note on C7: Specify quantity of transformers
Note on C8: Select type of liquid preservation system in accordance with 60076-1, 9.3. Default value : freely breathing conservator type
Note on C9: Select transformer service as per the load fed by the transformer. Unit transformer refers to transformer feeding a single motor.
Note on C10: Select CAS level as applied in S-720Q, Annex A Default value : D
Note on C12: Specify altitude, if more than 1 000 m or 3 280 ft
Note on C13: Specify minimum ambient temperature (°C or °F)
Note on C14: Specify maximum ambient temperature (°C or °F)
Note on C15: Specify yearly average ambient temperature (°C or °F)
Note on C16: Specify design ambient temperature (if more than 40 °C or 104 °F )
Note on C17: IOGP default is maximum 90 %. Specify relative humidity at maximum operating temperature if more than 90 %.
Note on C18: Select climatic conditions for liquid immersed transformer as per IEC 60721-3-4 Default value : 4K23
Note on C19: Specify special climatic conditions for liquid immersed transformer as per IEC 60721-3-4
Note on C20: Specify biological conditions for liquid immersed transformer as per IEC 60721-3-4 Default value : 4B1
Note on C21: Specify chemically active substances for liquid immersed transformer as per IEC 60721-3-4 Default value : 4C5
Note on C22: Specify mechanically active substances for liquid immersed transformers as per IEC 60721-3-4 Default value : 4S13
Note on C23: Specify mechanical conditions for liquid immersed transformer as per IEC 60721-3-4 Default value : 4M11
Note on C24: IOGP default is "C3" in accordance with ISO 12944-2. Higher corrosion class may be specified for coastal (C4/C5) and offshore, outdoor (CX) environment. Default value : C3
Note on C25: IOGP default is Zone 2. Specify higher seismic zone where exceeding zone 2 as per IEC 60721-2-6 Default value : Zone 2
Note on C26: Specify type of location in accordance with installation area
Note on C27: If "Yes", specify unusual service conditions in the supplement in accordance with IEC 60076-1, 5.5. Default value : No
Note on C28: Purchaser to specify maximum allowable A weighted sound power level in accordance with IEC 60076-10.
Note on C30: Specify hazardous area classification as non-hazardous, zone 1 or zone 2 Default value : non hazardous
Note on C31: Specify hazardous area classification gas group (IIA, IIB, IIC)
Note on C32: Specify hazardous area classification temperature class. T3 is typically applicable to oil and gas applications.
Note on C35: Specify rated voltage in kV for HV winding for transformer/reactor as applicable
Note on C36: Specify rated voltage in kV for LV winding for transformer/reactor as applicable.
Note on C37: Specify rated voltage in kV for tertiary winding
Note on C38: Specify rated frequency in Hz for transformer/reactor as applicable. Default value : 50
Note on C39: Specify system short circuit apparent power in MVA
Note on C40: Purchaser to specify the minimum full load power factor as this affects the voltage drop of the transformer
Note on C41: Specify supply voltage harmonic content in % if more than 5 %
Note on C45: Power frequency withstand voltage to be specified in accordance with IEC 60076-3
Note on C46: Power frequency withstand voltage to be specified in accordance with IEC 60076-3
Note on C47: Power frequency withstand voltage to be specified in accordance with IEC 60076-3
Note on C48: Power frequency withstand voltage to be specified in accordance with IEC 60076-3
Note on C50: Specify lightning impulse withstand voltage in accordance with IEC 60076-3
Note on C51: Specify lightning impulse withstand voltage in accordance with IEC 60076-3
Note on C52: Specify lightning impulse withstand voltage in accordance with IEC 60076-3
Note on C53: Specify lightning impulse withstand voltage in accordance with IEC 60076-3
Note on C54: Select number of phases for transformer/reactor as applicable. Default value : 3
Note on C55: Added to indicate direction of power flow across the transformer Default value : step-down
Note on C56: Specify vector group in accordance with IEC 60076-1, 7.1.1 for transformer/reactor as applicable.
Note on C57: Specify percentage impedance on air natural rating at principal tap in %. For reactor indicate in reactor specific requirements.
Note on C58: Specify the high limit for zero sequence impedance. This is required to decide the requirement of a stabilizing winding.
Note on C59: Specify the low limit for zero sequence impedance. This is required for deciding the requirement of a stabilizing winding.
Note on C60: Specify rated power in kVA in air natural cooling mode for HV winding
Note on C61: Specify rated power in kVA in air natural cooling mode for LV winding
Note on C62: Specify rated power in kVA in air natural cooling mode for tertiary winding in case of 3 winding transformers
Note on C63: Indicate rated power in forced cooling mode (HV)
Note on C64: Indicate rated power in forced cooling mode (LV)
Note on C65: Indicate rated power in forced cooling mode (tertiary)
Note on C66: Specify variation in V/Hz ratio from no load to rated load when in excess of 105 % as indicated in IEC 60076-1, 5.4.3.
Note on C67: Select whether parallel operation is required
Note on C68: Select whether 1.8 times overloading capability of transformer is required for restarting of a group of motors
Note on C69: Select type of insulating liquid Default value : Fully inhibited high grade mineral oil
Note on C70: Specify tolerance on total losses in % when exceeding IEC 60076-1, Table 1.
Note on C71: Specify tolerance on impedance value in % when exceeding IEC 60076-1, Table 1.
Note on C73: Specify level of DC current expected to flow in the transformer neutral in accordance with IEC 60076-1, 9.4
Note on C74: Select type of transformer neutral earthing for HV winding
Note on C75: Select type of transformer neutral earthing for secondary winding
Note on C76: Select type of transformer neutral earthing for tertiary winding
Note on C77: Sizing of low voltage neutral terminal to be specified where more than 50 % of the phase terminal in case of liquid immersed transformers.
Note on C79: Select winding conductor material
Note on C80: Specify whether delta connected stabilizing winding is required
Note on C81: Specify the type of earthing for the stabilizing winding. IOGP default is "solidly grounded". Default value : Solidly grounded
Note on C82: Specify winding class of insulation (A, B for liquid immersed transformers) in accordance with IEC 60085. Default value : A
Note on C83: Specify whether non-uniform (graded) insulation is required in accordance with cl.no.3.6 of IEC 60076-3
Note on C84: Specify whether high temperature insulation is required in accordance with IEC 60076-14
Note on C85: Specify whether thermally upgraded paper is required in accordance with IEC 60076-7, Table A.2.
Note on C87: Select type of cable termination (HV)
Note on C88: Select type of cable termination (LV)
Note on C89: Select type of cable termination (tertiary)
Note on C90: Select type of cable termination (neutral)
Note on C91: Specify cable box type
Note on C92: Select the direction of cable entry into the HV connection box. Default value : bottom entry
Note on C93: Select the direction of cable entry into the HV connection box. Default value : bottom entry
Note on C94: Specify the type of main terminal box. Phase segregated is preferred above 33 kV.
Note on C95: Select cable type
Note on C96: Specify number of cables to be terminated on the HV side
Note on C97: Specify number of cables to be terminated on the LV side
Note on C98: Specify number of cables to be terminated on the tertiary side
Note on C99: Specify cable conductor size for HV terminals
Note on C100: Specify cable conductor size for LV terminals
Note on C101: Specify cable conductor size for tertiary terminals
Note on C102: Specify number of cores per cable for HV terminals
Note on C103: Specify number of cores per cable for LV terminals
Note on C104: Specify number of cores per cable for tertiary terminals
Note on C105: Specify number of cables per phase for HV terminals
Note on C106: Specify number of cables per phase for LV terminals
Note on C107: Specify number of cables per phase for tertiary terminal
Note on C108: Select whether separate neutral terminal box is required
Note on C109: Select Yes, No
Note on C110: Select type of busduct
Note on C112: Specify type of bushing required for HV terminals in accordance with IEC 60137
Note on C113: Specify type of bushing required for LV terminals in accordance with IEC 60137.
Note on C114: Specify type of bushing required for tertiary terminals in accordance with IEC 60137.
Note on C115: Specify type of bushing required for neutral terminal in accordance with IEC 60137.
Note on C117: Select whether tap changer is required and the type
Note on C118: Purchaser to specify whether voltage variation is required on HV or LV side
Note on C119: Select type of de-energized tap changer (DETC) required Default value : hand operated
Note on C120: The switching medium whether vacuum or insulating liquid to be specified.
Note on C121: Specify the category of voltage variation for the tap changer in accordance with IEC 60076-1, 6.2. Default value : CFVV
Note on C122: Specify tapping range in %
Note on C123: Specify number of steps for tapping
Note on C124: Specify whether the principal tapping is symmetrical, asymmetrical
Note on C125: Specify the maximum current tapping position for tapping range wider than +/-5 %.
Note on C126: Remote tap-changer cabinet can be selected in accordance with purchaser's operation philosophy.
Note on C128: Select type of cooling required for transformer/reactor as applicable.
Note on C129: Select allowable temperature rise for insulating liquid when not in accordance with IEC 60076-2
Note on C130: Select temperature rise of winding when not in accordance with IEC 60076-2 or IEC 60076-11
Note on C131: Cooling water inlet temperature to be specified when not in accordance with IEC 60076-2 and IEC 60076-11
Note on C132: Provision for mounting of cooling fans in future to be specified. IOGP default is "No" as this is not a standard requirement. Default value : No
Note on C133: Select required location of cooling fan cabinet- on transformer body, self standing Default value : on transformer body
Note on C136: Select whether bolted or welded cover is required
Note on C137: Specify type of surface finish for the transformer tank and radiators
Note on C138: IOGP default is "M" in accordance with ISO 12944-1. Higher painting class may be selected for coastal(H) and offshore, outdoor(VH) environment. Default value : M
Note on C139: Select the paint shade from either supplier default or "other" (preferred by purchaser).
Note on C141: Specify auxiliary supply voltage details in volts for cooling fans
Note on C142: Specify auxiliary supply voltage details in volts for remote tap changer cabinet (RTCC)
Note on C143: Specify whether current transformer in neutral is required.
Note on C144: Specify current transformer ratio
Note on C145: Specify current transformer accuracy class
Note on C146: Specify current transformer burden
Note on C148: Purchaser to indicate limiting transportation dimensions (height)
Note on C149: Purchaser to indicate limiting transportation dimensions (width)
Note on C150: Purchaser to indicate limiting transportation dimensions (depth)
Note on C151: Purchaser to indicate limiting transportation weight
Note on C152: Select impact recorder requirement
Note on C153: Specify whether acceleration in excess of 1 g is expected during transportation
Note on C155: Select type of reactor required
Note on C156: Specify rated current in Amps
Note on C157: Specify rated thermal short circuit current in Amps in accordance with IEC 60076-6
Note on C158: Specify time to withstand rated short circuit current in seconds
Note on C159: Specify impedance at rated voltage and current in ohms
Note on C161: Select whether lifting lugs are required
Note on C162: Select whether silica gel breather is required for the main tank
Note on C163: Select whether manual type or self-regenerating type silica gel breather is required
Note on C164: Select whether liquid level indicator is required
Note on C165: Select whether liquid gauge with contacts is required Default value : Yes
Note on C166: Select whether Buchholz relay with alarm and trip contacts is required
Note on C167: Select whether PRD is required for OLTC
Note on C168: Select whether PRD is required for liquid filled cable box
Note on C169: Select whether facility for directing emissions of liquid from the relief device in the direction is required.
Note on C170: This is used to quickly deenergize the transformer to minimize damage from internal short circuits. Default value : No
Note on C171: Select whether liquid temperature indicator with alarm and trip contacts is required
Note on C172: Select whether winding temperature Indicator With Alarm and trip contacts is required
Note on C173: Select type of winding temperature measurement required. Default value : PTC thermistor
Note on C174: Select whether cooling fans are required
Note on C175: If redundancy is required include information e.g. number of pumps, fans, liquid N2 in the additional notes.
Note on C176: Select whether control panel for fan starters for AF type transformer is required
Note on C177: Select whether cable box is required on the high voltage side
Note on C178: Select whether cable box is required on the low voltage side
Note on C179: Select whether cable box is required on the tertiary winding side
Note on C180: Select whether surge arrester is required to protect the HV winding from lightning or internal switching surges.
Note on C181: Select the surge arrester class in accordance with IEC 60099-4, Table 1.
Note on C182: Select whether a continuous dissolved gas-in-oil analysis (DGA) monitoring system for the transformer insulating liquid is required. If "required" is selected, specify the selected gases from IEC60599 in the "Additional notes" column.
Note on C183: Specify requirement of fiber optic temperature sensing where real time monitoring of winding hot spot temperature is required.
Note on C184: Specify the number of channels for the fiber optic temperature sensor based on the number of sensors required in accordance with IEC 60076-2, Table E.1.
Note on C185: Select whether core earthing terminals are to be provided at an accessible location.
Note on C186: Purchaser shall specify the earthing cable lug size to be terminated on the earthing terminal provided by supplier.
Note on C187: Specify whether provision for connection of portable earthing apparatus is required. Applicable for earthing of the HV terminals of dry type transformers before starting maintenance work.
Note on C188: Select whether-infra red inspection window is required for cable box for dry type transformer/reactor for use of thermal imaging camera.
Note on C189: Specify whether conservator diaphragm failure alarm contact is required Default value : No
Note on C190: Specify whether bi-directional rollers are required
Note on C191: Specify requirement of anti-condensation heaters for cable box where variations in ambient temperature could lead to condensation inside cable box.
Note on C192: Anti-condensation heater to be selected based on the substation environment (air conditioned or non air conditioned).
Note on C193: Requirement of ladder for access to be selected
Note on C194: Select whether a continuous partial discharge monitoring system is required. If "required" is selected, specify the transformer components to be monitored in the "Additional notes" column (e.g., windings, bushings, high voltage terminations). Default value : not required
Note on C195: Select whether a continuous temperature monitoring system for the transformer insulating liquid is required. Continuous measurement of the top oil temperature is an important factor in maximizing the service life. Default value : not required
Note on C196: Select whether a continuous temperature monitoring system for the transformer windings is required. Excessive heat in the transformer windings can result in tearing and displacement of the paper and dielectric breakdown resulting in premature failures. Default value : not required
Note on C197: Select whether a continuous cable termination thermal monitoring system for the transformer power connections is required. Continuous measurement of power connection temperature can detect hot spots from loose connections resulting in possible failure. Default value : not required
Note on C198: Select whether a moisture in oil monitoring system for the insulating liquid is required. Excessive moisture affects dielectric integrity of liquid/paper insulation system and can lead to partial discharges. Refer to IEC60422. Default value : not required
Note on C199: Specify portable earthing device to enable earthing at the plug in bushing connector Default value : not required
Note on C201: Select whether temperature rise test needs to be performed
Note on C202: Purchaser to specify whether temperature rise test required to be conducted at tapping other than the maximum current tapping
Note on C203: Select whether power consumption tests of fans and liquid pump motors needs to be performed
Note on C204: Select whether dielectric type tests (lightning impulse) need to be performed according to IEC 60076-3 clause 7.3.1.2 Default value : No
Note on C205: Select whether sound level test to be performed
Note on C206: Measurement of no-load loss and current at 90 % and 110 % of rated voltage needs to be performed
Note on C207: Select whether dielectric special tests (Table1, IEC 60076-3) need to be performed. The needed tests should be listed separately in the notes. Default value : No
Note on C208: Select winding hot-spot temperature-rise measurements are required to be done
Note on C209: Select whether capacitances windings-to-earth and between windings to be determined
Note on C210: Select whether determination of transient voltage transfer characteristics to be done in accordance with IEC 60076-3
Note on C211: Select whether measurement of zero-sequence impedance to be done in accordance with IEC 60076-1, 11.6.
Note on C212: Select whether short-circuit withstand test is to be done in accordance with IEC 60076-5.
Note on C213: Select whether Vacuum deflection test is to be done in accordance with IEC 60076-1, 11.9.
Note on C214: Select whether Pressure deflection test is to be done in accordance with IEC 60076-1, 11.10.
Note on C215: Select whether pressure deflection test for OLTC tank needs to be performed.
Note on C216: Select whether Vacuum tightness test is to be done in accordance with IEC 60076-1, 11.11.
Note on C217: Select whether vacuum tightness test needs to be performed for OLTC tank
Note on C218: Select whether Measurement of frequency response (Frequency response analysis-FRA) is to be done. The test procedure shall be agreed between purchaser and supplier.
Note on C219: Select whether check of external coating is to be done in accordance with ISO 2178 and ISO 2409 or as specified.
Note on C220: Select whether Measurement of dissolved gasses in dielectric liquid is to be done in accordance with IEC 60076-3.
Note on C221: Select whether Mechanical test is to be done. Test to be done for assessment of tank for suitability of transport in accordance with purchaser specification.
Note on C222: Purchaser to select whether a simulated on load start test is required in case of unit transformer feeding a motor. Unit transformer indicates a transformer feeding a single motor.
Note on C223: Specify whether routine test for pressurization system is required for Ex 'p' type transformer.
Note on C224: Select whether routine tests for Ex 'O' type transformer are required to be performed in accordance with IEC 60079-6

## Dry Type Transformers
Row | IOGP S-720D (1.01) Data Sheet for Transformers Dry Type Transformers |  |  |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | 1. General
6 |  | Equipment identifier : | input data
7 |  | Quantity : | input data
8 |  | Type of dry type transformer : | Cast resin encapsulated |  |  |  | select | Cast resin encapsulated | cast resin non-encapsulated | vacuum pressure impregnated | other
9 | 4.1,5.7.1,** | Service : | select |  |  |  | select | power transformer | lighting and small power transformer | unit transformer | generator transformer | auto-transformer | reactor | earthing transformer | mobile service transformer.
10 |  | Conformity assessment system : | D |  |  |  | select | A | B | C | D
11 |  | 2. Environmental conditions
12 | 5.5(Para,** | Altitude (if more than 1000m or 3280ft) : | input data | select |  |  | select | m | ft
13 | 4.2,** | Minimum ambient temperature : | input data | select |  |  | select | °C | °F
14 | 4.2,** | Maximum ambient temperature : | input data | select |  |  | select | °C | °F
15 | 4.2,** | Yearly average ambient temperature : | input data | select |  |  | select | °C | °F
16 | 5.5(Para,** | Design ambient temperature (if more than 40 °C or 104 °F ) : | input data | select |  |  | select | °C | °F
17 | 4.2,** | Relative humidity at maximum operating temperature : | input data | %
18 | 4.2 | Climatic class for dry type transformer as per IEC 60076-11 : | C1 |  |  |  | select | C1 | C2 | C3 | C4 | C5
19 | 4.2 | Environmental class for dry type transformer as per IEC 60076-11 : | E1 |  |  |  | select | E0 | E1 | E2 | E3 | E4
20 | 4.2 | Fire behavior class for dry type transformer as per IEC 60076-11 : | F0 |  |  |  | select | F0 | F1
21 | 9.6.18.1,9.6.18.3 | Corrosion class : | C3 |  |  |  | select | C3 | C4 | C5 | CX
22 | ** | Seismic zone as per IEC 60721-2-6, Figure 5 : | Zone 2 |  |  |  | select | zone 2 | zone 3 | zone 4
23 | 4.2,5.7.4.2(Para,** | Location : | select |  |  |  | select | indoor | outdoor | offshore fixed | offshore mobile
24 | ** | Unusual service conditions : | No |  |  |  | select | Yes | No
25 | ** | Vibration level for dry type transformer : | input data | mm/s
26 | 5.7.3 | Sound power level : | input data | dB(A)
27 |  | 3. Hazardous area classification
28 | 4.2,** | Hazardous area classification zone : | non hazardous |  |  |  | select | non hazardous | zone 1 | zone 2
29 | 4.2,** | Hazardous area classification gas group : | select |  |  |  | select | IIA | IIB | IIC
30 | 4.2,** | Hazardous area classification temperature class : | input data
31 |  | 4. Technical data
32 |  | 4.1 Electrical system data
33 | 5.4.1(Para,** | Rated voltage (HV) : | input data | kV
34 | 5.4.1(Para | Rated voltage (LV) : | input data | kV
35 | 5.4.1(Para | Rated voltage (tertiary) : | input data | kV
36 | 5.4.2(Para,** | Rated frequency : | 50 | Hz |  |  | select | 50 | 60
37 | **,A.1.2(a | System short circuit apparent power : | input data | MVA
38 | 6.4.3.e | Minimum full load power factor : | input data
39 |  | System inrush current limitations : | input data | A
40 | **,A.1.2(a | Supply voltage harmonic content : | input data | %
41 |  | 4.2 Transformer/reactor data
42 |  | 4.2.1 General
43 |  | Power frequency withstand voltage
44 | ** | Power frequency withstand voltage - HV winding : | input data | kV
45 | ** | Power frequency withstand voltage - LV winding : | input data | kV
46 | ** | Power frequency withstand voltage - tertiary winding : | input data | kV
47 | ** | Power frequency withstand voltage - neutral terminal : | input data | kV
48 |  | Lightning impulse withstand voltage
49 | ** | Lightning impulse withstand voltage - HV winding : | input data | kV
50 | ** | Lightning impulse withstand voltage - LV winding : | input data | kV
51 | ** | Lightning impulse withstand voltage - tertiary winding : | input data | kV
52 | ** | Lightning impulse withstand voltage - neutral terminal : | input data | kV
53 | 5.7.2(Para,7.1.1,** | Number of phases : | 3 |  |  |  | select | 1 | 2 | 3
54 | 6.4.3.a,** | Direction of power flow : | step-down |  |  |  | select | step-up | step-down | bi-directional
55 | 7.1.5,5.7.2(Para,7.1.1,** | Connection and phase displacement symbol (vector group) : | input data
56 | **,A.1.2(a,B.4(Para | Percentage impedance on air natural rating at principal tap : | input data | %
57 | 5.7.2(Para | High limit for zero sequence impedance : | input data | ohms/ph
58 | 5.7.2(Para | Low limit for zero sequence impedance : | input data | ohms/ph
59 | 5.1.1,** | Rated power in air natural mode (HV) : | input data | kVA
60 | 5.1.1,** | Rated power in air natural mode (LV) : | input data | kVA
61 | 5.1.1,** | Rated power in air natural mode (tertiary) : | input data | kVA
62 | 5.1.1,5.1.3(Para,** | Rated power in forced cooling mode (HV) : | input data | kVA
63 | 5.1.1,5.1.3(Para,** | Rated power in forced cooling mode (LV) : | input data | kVA
64 | 5.1.1,5.1.3(Para,** | Rated power in forced cooling mode (tertiary) : | input data | kVA
65 | 5.4.3(Para | Variation in V/Hz ratio from no load to rated load when exceeding 105 % : | input data | %
66 | **,A.1.2(a,A.2 | Parallel operation : | select |  |  |  | select | Yes | No
67 | 5.1.1 | Requirement of 1.8 times overloading for transformer feeding a group of motors : | select |  |  |  | select | Yes | No
68 | **,A.1.2(a,Table 1 | Tolerance on total losses when not in accordance with IEC 60076-1 : | input data | %
69 | 6.5(Para,**,A.1.2(a,Table 1 | Tolerance on impedance value when not in accordance with IEC 60076-1 : | input data | %
70 |  | 4.2.2 Neutral terminal
71 | 9.4(Para | Level of DC current in neutral : | input data | %
72 | ** | Transformer neutral earthing for HV winding : | select |  |  |  | select | solid | ungrounded | resistance grounded | earthing transformer
73 | ** | Transformer neutral earthing for LV winding : | select |  |  |  | select | solid | ungrounded | resistance grounded | earthing transformer
74 | ** | Transformer neutral earthing for tertiary winding : | select |  |  |  | select | solid | ungrounded | resistance grounded | earthing transformer
75 |  | 4.2.3 Winding
76 | ** | Winding conductor material : | select |  |  |  | select | aluminum | copper
77 | 5.7.2(Para | Requirement of delta connected stabilizing winding : | select |  |  |  | select | Yes | No
78 | 5.7.2(Para | Method of earthing of delta connected stabilizing winding : | Solidly grounded |  |  |  | select | solidly grounded | ungrounded
79 | ** | Winding class of insulation : | F |  |  |  | select | F | H | other
80 |  | 4.2.4 Termination
81 |  | Direction of cable entry (HV) : | bottom entry |  |  |  | select | top entry | bottom entry | side entry
82 |  | Direction of cable entry (LV) : | bottom entry |  |  |  | select | top entry | bottom entry | side entry
83 | ** | Cable type : | select |  |  |  | select | bare conductor | insulated
84 | ** | Number of cables (HV) : | input data
85 | ** | Number of cables (LV) : | input data
86 | ** | Number of cables (tertiary) : | input data
87 | 9.6.11.1.4,** | Cable conductor size (HV) : | input data | select |  |  | select | mm² | in²
88 | 9.6.11.1.4 | Cable conductor size (LV) : | input data | select |  |  | select | mm² | in²
89 | 9.6.11.1.4 | Cable conductor size (tertiary) : | input data | select |  |  | select | mm² | in²
90 | 9.6.11.1.4,** | Number of cores per cable (HV) : | input data
91 | 9.6.11.1.4 | Number of cores per cable (LV) : | input data
92 | 9.6.11.1.4 | Number of cores per cable (tertiary) : | input data
93 | 9.6.11.1.4,** | Number of cables per phase (HV) : | input data
94 | 9.6.11.1.4 | Number of cables per phase (LV) : | input data
95 | 9.6.11.1.4 | Number of cables per phase (tertiary) : | input data
96 | ** | Busduct type : | select |  |  |  | select | air insulated | gas insulated | sandwich type | cast resin
97 |  | 4.2.5 Tap changer
98 | 6.1(Para,6.4.1(Para,** | Tap changer required and type : | select |  |  |  | select | No | OLTC | DETC | bolted links
99 | 6.4.2.a,6.4.3.c | Voltage variation required on: : | select |  |  |  | select | HV | LV
100 | ** | Type of de-energized tap changer (DETC) : | hand operated |  |  |  | select | hand operated | motor operated
101 | 6.2.a,6.2.b,6.2.c | Category of voltage variation : | CFVV |  |  |  | select | CFVV | VFVV | CbVV
102 | 6.4.1(Para,6.4.2.b,6.4.3.b,6.4.3.c,**,B.4(Para | Tapping range : | input data | %
103 | 6.4.1(Para,6.4.2.b,6.4.3.b,6.4.3.c,** | Number of tapping positions : | input data
104 | 6.4.3.b | Principal tapping position : | select |  |  |  | select | symmetrical | asymmetrical
105 | 9.6.17.3.4 | Remote tap-changer cabinet for OLTC : | select |  |  |  | select | Yes | No
106 |  | 4.2.6 Cooling
107 | 5.2,5.1.3(Para,** | Type of cooling : | select |  |  |  | select | AN | AN/AF | AFWF
108 | 5.1.3(Para,A.1.2(a | Temperature rise of winding when not in accordance with IEC 60076-2 or IEC 60076-11 : | input data | select |  |  | select | °C | °F
109 | 4.2 | Cooling water inlet temperature when not in accordance with IEC 60076-2 and IEC 60076-11 : | input data | select |  |  | select | °C | °F
110 | 5.2 | Provision for mounting of cooling fans : | No |  |  |  | select | Yes | No
111 | ** | AF fan motor cabinet : | on transformer body |  |  |  | select | on transformer body | self-standing
112 |  | 4.2.7 Miscellaneous requirements
113 |  | a. Construction
114 | ** | Surface finish of tank and radiators : | select |  |  |  | select | hot dip galvanized | zinc coated
115 | 9.6.18.1 | Painting class required : | M |  |  |  | select | L | M | H | VH
116 | ** | Paint shade : | select |  |  |  | select | Supplier default | Other
117 | 9.6.1.6 | Ingress protection for transformer enclosure : | IP 2XD |  |  |  | select | IP 2XD | Other
118 |  | b. Interface
119 | ** | Auxiliary supply voltage details for cooling fans : | input data | V
120 | ** | Auxiliary supply voltage details for RTCC : | input data | V
121 | 8.3 | Requirement of current transformer in neutral : | select |  |  |  | select | Yes | No
122 | ** | Current transformer ratio : | input data | A
123 | ** | Current transformer accuracy class : | select |  |  |  | select | 0.5 | 1 | 1.5 | other
124 | ** | Current transformer burden : | input data | VA
125 |  | c. Transport
126 | ** | Impact recorder requirement during transportation : | select |  |  |  | select | Yes | No
127 | 5.7.4.2(Para | Acceleration in excess of 1 g during transportation : | select |  |  |  | select | Yes | No
128 |  | 4.3 Reactor specific requirements
129 | ** | Application : | select |  |  |  | select | shunt reactor | current limiting reactor | neutral earthing transformer | arc suppression reactor | discharge reactor
130 | ** | Rated current : | input data | A
131 | ** | Rated short circuit current : | input data | A
132 | ** | Time to withstand rated short circuit current : | input data | s
133 | 6.5(Para,** | Impedance at rated voltage and current : | input data | Ohms
134 |  | 5. Accessories
135 | 9.1.2,** | Lifting lugs : | select |  |  |  | select | Yes | No
136 | **,Annex F(Para 1,Table F.1 | Winding temperature indicator with alarm and trip contacts : | select |  |  |  | select | Yes | No
137 | **,Annex F(Para 1,Table F.1 | Winding temperature measurement type : | PTC thermistor |  |  |  | select | Not required | PTC thermistor | PT100 RTD
138 | ** | Cooling fans : | select |  |  |  | select | Yes | No
139 | ** | Redundancy of cooling fans : | select |  |  |  | select | Yes | No
140 | A.1.2(a | Isolating barrier for dry type transformers. : | select |  |  |  | select | Yes | No
141 | 9.6.13,** | Surge arrester requirement : | select |  |  |  | select | Yes | No
142 | 9.6.13 | Surge arrester class : | select |  |  |  | select | Station class | Distribution class
143 | 9.6.6.3,** | Earthing cable lug size : | input data | mm
144 | A.1.2(a | Provision for connection of portable earthing device to the air insulated terminals for voltages above 1 kV : | select |  |  |  | select | Yes | No
145 | A.1.2(a | Infra-red inspection window for cable connections : | select |  |  |  | select | Yes | No
146 | ** | Bi-directional rollers : | select |  |  |  | select | Yes | No
147 | 9.6.17.3.5 | Anti-condensation heater for remote tap-changer cabinet : | select |  |  |  | select | Yes | No
148 | Table F.1 | Partial discharge monitoring : | not required |  |  |  | select | not required | required
149 | Table F.1 | Winding temperature monitoring : | not required |  |  |  | select | not required | required
150 | Table F.1 | Cable termination thermal monitoring : | not required |  |  |  | select | not required | required
151 |  | 6. Testing requirements
152 | 11.1.3.a | Temperature rise test : | select |  |  |  | select | Yes | No
153 | 6.6.b | Temperature rise test at tapping other than the maximum current tapping : | select |  |  |  | select | Yes | No
154 | 11.1.3.d | Power consumption test of fans : | select |  |  |  | select | Yes | No
155 | 11.1.3.b,A.1.2(a | Dielectric type tests (lightning impulse) : | No |  |  |  | select | Yes | No
156 | 11.1.3.c | Sound level test : | select |  |  |  | select | Yes | No
157 | 11.1.3.e | Measurement of no-load loss and current at 90 % and 110 % of rated voltage : | select |  |  |  | select | Yes | No
158 | 11.1.4.a,A.1.2(a | Dielectric special tests (partial discharge test) : | No |  |  |  | select | Yes | No
159 | 11.1.4.b,A.1.2(a | Winding hot-spot temperature-rise measurements : | select |  |  |  | select | Yes | No
160 | 11.1.4.c,A.1.2(a | Determination of capacitances windings-to-earth and between windings : | select |  |  |  | select | Yes | No
161 | 11.1.4.e,A.1.2(a | Determination of transient voltage transfer characteristics : | select |  |  |  | select | Yes | No
162 | 11.1.4.f,A.1.2(a | Measurement of zero-sequence impedance : | select |  |  |  | select | Yes | No
163 | 11.1.4.g,A.1.2(a | Short-circuit withstand test : | select |  |  |  | select | Yes | No
164 | 11.1.4.l,A.1.2(a | Measurement of frequency response : | select |  |  |  | select | Yes | No
165 | 11.1.4.m,A.1.2(a | Check of external coating : | select |  |  |  | select | Yes | No
166 | 11.1.4 | Vibration test for dry type transformers as per IEC 60076-11 : | select |  |  |  | select | Yes | No
167 | 11.1.4 | Simulated transformer/motor on load start test for unit transformer : | select |  |  |  | select | Yes | No
Note on C6: Specify equipment tag number
Note on C7: Specify quantity of transformers
Note on C8: Select type of dry type transformer Default value : Cast resin encapsulated
Note on C9: Select transformer service as per the load fed by the transformer. Unit transformer refers to transformer feeding a single motor.
Note on C10: Select CAS level as applied in S-720Q, Annex A Default value : D
Note on C12: Specify altitude, if more than 1 000 m or 3 280 ft
Note on C13: Specify minimum ambient temperature (°C or °F)
Note on C14: Specify maximum ambient temperature (°C or °F)
Note on C15: Specify yearly average ambient temperature (°C or °F)
Note on C16: Specify design ambient temperature (if more than 40 °C or 104 °F )
Note on C17: IOGP default is maximum 90 %. Specify relative humidity at maximum operating temperature.
Note on C18: Specify climatic class for dry type transformer as per IEC 60076-11 Default value : C1
Note on C19: Specify environmental class as per IEC 60076-11. Default value : E1
Note on C20: Specify fire behavior class for dry type transformer as per IEC 60076-11 Default value : F0
Note on C21: IOGP default is "C3" in accordance with ISO 12944-2. Higher corrosion class may be specified for coastal (C4/C5) and offshore, outdoor (CX) environment. Default value : C3
Note on C22: IOGP default is Zone 2. Specify higher seismic zone where exceeding zone 2 as per IEC 60721-2-6 Default value : Zone 2
Note on C23: Specify type of location in accordance with installation area
Note on C24: If "Yes", specify unusual service conditions in the supplement in accordance with IEC 60076-1, 5.5. Default value : No
Note on C25: Specify vibration levels applicable for dry type transformer as per IEC 60076-11, 4.2.l
Note on C26: Purchaser to specify maximum allowable A weighted sound power level in accordance with IEC 60076-10.
Note on C28: Specify hazardous area classification as non-hazardous, zone 1 or zone 2 Default value : non hazardous
Note on C29: Specify hazardous area classification gas group (IIA, IIB, IIC)
Note on C30: Specify hazardous area classification temperature class. T3 is typically applicable to oil and gas applications.
Note on C33: Specify rated voltage in kV for HV winding for transformer/reactor as applicable
Note on C34: Specify rated voltage in kV for LV winding for transformer/reactor as applicable.
Note on C35: Specify rated voltage in kV for tertiary winding
Note on C36: Specify rated frequency in Hz for transformer/reactor as applicable. Default value : 50
Note on C37: Specify system short circuit apparent power in MVA
Note on C38: Purchaser to specify the minimum full load power factor as this affects the voltage drop of the transformer
Note on C39: Specify the system inrush current limitations if any (e.g. maximum value, duration). See IEC 60076-11, subclause 4.2 h).
Note on C40: Specify supply voltage harmonic content in % if more than 5 %
Note on C44: Power frequency withstand voltage to be specified in accordance with IEC 60076-3
Note on C45: Power frequency withstand voltage to be specified in accordance with IEC 60076-3
Note on C46: Power frequency withstand voltage to be specified in accordance with IEC 60076-3
Note on C47: Power frequency withstand voltage to be specified in accordance with IEC 60076-3
Note on C49: Specify lightning impulse withstand voltage in accordance with IEC 60076-3
Note on C50: Specify lightning impulse withstand voltage in accordance with IEC 60076-3
Note on C51: Specify lightning impulse withstand voltage in accordance with IEC 60076-3
Note on C52: Specify lightning impulse withstand voltage in accordance with IEC 60076-3
Note on C53: Select number of phases for transformer/reactor as applicable. Default value : 3
Note on C54: Added to indicate direction of power flow across the transformer Default value : step-down
Note on C55: Specify vector group in accordance with IEC 60076-1, 7.1.1 for transformer/reactor as applicable.
Note on C56: Specify percentage impedance on air natural rating at principal tap in %. For reactor indicate in reactor specific requirements.
Note on C57: Specify the high limit for zero sequence impedance. This is required to decide the requirement of a stabilizing winding.
Note on C58: Specify the low limit for zero sequence impedance. This is required for deciding the requirement of a stabilizing winding.
Note on C59: Specify rated power in kVA in air natural cooling mode for HV winding
Note on C60: Specify rated power in kVA in air natural cooling mode for LV winding
Note on C61: Specify rated power in kVA in air natural cooling mode for tertiary winding in case of 3 winding transformers
Note on C62: Indicate rated power in forced cooling mode (HV)
Note on C63: Indicate rated power in forced cooling mode (LV)
Note on C64: Indicate rated power in forced cooling mode (tertiary)
Note on C65: Specify variation in V/Hz ratio from no load to rated load when in excess of 105 % as indicated in IEC 60076-1, 5.4.3.
Note on C66: Select whether parallel operation is required
Note on C67: Select whether 1.8 times overloading capability of transformer is required for restarting of a group of motors
Note on C68: Specify tolerance on total losses in % when exceeding IEC 60076-1, Table 1.
Note on C69: Specify tolerance on impedance value in % when exceeding IEC 60076-1, Table 1.
Note on C71: Specify level of DC current expected to flow in the transformer neutral in accordance with IEC 60076-1, 9.4
Note on C72: Select type of transformer neutral earthing for HV winding
Note on C73: Select type of transformer neutral earthing for secondary winding
Note on C74: Select type of transformer neutral earthing for tertiary winding
Note on C76: Select winding conductor material
Note on C77: Specify whether delta connected stabilizing winding is required
Note on C78: Specify the type of earthing for the stabilizing winding. IOGP default is "solidly grounded". Default value : Solidly grounded
Note on C79: Specify winding class of insulation (F, H for dry type transformers) in accordance with IEC 60085 . If other is selected specify the class of insulation in the additional notes column. Default value : F
Note on C81: Select the direction of cable entry into the HV connection box. Default value : bottom entry
Note on C82: Select the direction of cable entry into the HV connection box. Default value : bottom entry
Note on C83: Select cable type
Note on C84: Specify number of cables to be terminated on the HV side
Note on C85: Specify number of cables to be terminated on the LV side
Note on C86: Specify number of cables to be terminated on the tertiary side
Note on C87: Specify cable conductor size for HV terminals
Note on C88: Specify cable conductor size for LV terminals
Note on C89: Specify cable conductor size for tertiary terminals
Note on C90: Specify number of cores per cable for HV terminals
Note on C91: Specify number of cores per cable for LV terminals
Note on C92: Specify number of cores per cable for tertiary terminals
Note on C93: Specify number of cables per phase for HV terminals
Note on C94: Specify number of cables per phase for LV terminals
Note on C95: Specify number of cables per phase for tertiary terminal
Note on C96: Select type of busduct
Note on C98: Select whether tap changer is required and the type
Note on C99: Purchaser to specify whether voltage variation is required on HV or LV side
Note on C100: Select type of de-energized tap changer (DETC) required Default value : hand operated
Note on C101: Specify the category of voltage variation for the tap changer in accordance with IEC 60076-1, 6.2. Default value : CFVV
Note on C102: Specify tapping range in %
Note on C103: Specify number of steps for tapping
Note on C104: Specify whether the principal tapping is symmetrical, asymmetrical
Note on C105: Remote tap-changer cabinet can be selected in accordance with purchaser's operation philosophy.
Note on C107: Select type of cooling required for transformer/reactor as applicable.
Note on C108: Select temperature rise of winding when not in accordance with IEC 60076-2 or IEC 60076-11
Note on C109: Cooling water inlet temperature to be specified when not in accordance with IEC 60076-2 and IEC 60076-11
Note on C110: Provision for mounting of cooling fans in future to be specified. IOGP default is "No" as this is not a standard requirement. Default value : No
Note on C111: Select required location of cooling fan cabinet- on transformer body, self-standing Default value : on transformer body
Note on C114: Specify type of surface finish for the transformer tank and radiators
Note on C115: IOGP default is "M" in accordance with ISO 12944-1. Higher painting class may be selected for coastal(H) and offshore, outdoor(VH) environment. Default value : M
Note on C116: Select the paint shade from either supplier default or "other" (preferred by purchaser).
Note on C117: Specify the ingress protection for the transformer enclosure as per IEC 60529. Default value : IP 2XD
Note on C119: Specify auxiliary supply voltage details in volts for cooling fans
Note on C120: Specify auxiliary supply voltage details in volts for remote tap changer cabinet (RTCC)
Note on C121: Specify whether current transformer in neutral is required.
Note on C122: Specify current transformer ratio
Note on C123: Specify current transformer accuracy class
Note on C124: Specify current transformer burden
Note on C126: Select impact recorder requirement
Note on C127: Specify whether acceleration in excess of 1 g is expected during transportation
Note on C129: Select type of reactor required
Note on C130: Specify rated current in Amps
Note on C131: Specify rated thermal short circuit current in Amps in accordance with IEC 60076-6
Note on C132: Specify time to withstand rated short circuit current in seconds
Note on C133: Specify impedance at rated voltage and current in ohms
Note on C135: Select whether lifting lugs are required
Note on C136: Select whether winding temperature indicator with alarm and trip contacts is required
Note on C137: Select type of winding temperature measurement required. Default value : PTC thermistor
Note on C138: Select whether cooling fans are required
Note on C139: Specify whether redundant cooling fans are required.
Note on C140: Specify whether an isolating barrier is required for shock protection of operating personnel when maintaining dry type transformers.
Note on C141: Select whether surge arrester is required to protect the HV winding from lightning or internal switching surges.
Note on C142: Select the surge arrester class in accordance with IEC 60099-4, Table 1.
Note on C143: Purchaser shall specify the earthing cable lug size to be terminated on the earthing terminal provided by supplier.
Note on C144: Specify whether provision for connection of portable earthing apparatus is required. Applicable for earthing of the HV terminals of dry type transformers before starting maintenance work.
Note on C145: Select whether infra-red inspection window is required for cable box for dry type transformer/reactor for use of thermal imaging camera.
Note on C146: Specify whether bi-directional rollers are required
Note on C147: Anti-condensation heater to be selected based on the substation environment (air conditioned or non air conditioned).
Note on C148: Select whether a continuous partial discharge monitoring system is required. If "required" is selected, specify the transformer components to be monitored in the "Additional notes" column (e.g., windings, bushings, high voltage terminations). Default value : not required
Note on C149: Select whether a continuous temperature monitoring system for the transformer windings is required. Excessive heat in the transformer windings can result in tearing and displacement of the paper and dielectric breakdown resulting in premature failures. Default value : not required
Note on C150: Select whether a continuous cable termination thermal monitoring system for the transformer power connections is required. Continuous measurement of power connection temperature can detect hot spots from loose connections resulting in possible failure. Default value : not required
Note on C152: Select whether temperature rise test needs to be performed
Note on C153: Purchaser to specify whether temperature rise test required to be conducted at tapping other than the maximum current tapping
Note on C154: Select whether power consumption tests of fans and liquid pump motors needs to be performed
Note on C155: Select whether dielectric type tests (lightning impulse) need to be performed as per IEC 60076-11, subclause 14.3.1. Default value : No
Note on C156: Select whether sound level test to be performed
Note on C157: Measurement of no-load loss and current at 90 % and 110 % of rated voltage needs to be performed
Note on C158: Select whether dielectric special tests (partial discharge test) are required if the transformer will be operated under single phase line-to-earth fault condition. See IEC 60076-11 subclause 14.4.1.
Note on C159: Select winding hot-spot temperature-rise measurements are required to be done
Note on C160: Select whether capacitances windings-to-earth and between windings to be determined
Note on C161: Select whether determination of transient voltage transfer characteristics to be done in accordance with IEC 60076-3
Note on C162: Select whether measurement of zero-sequence impedance to be done in accordance with IEC 60076-1, 11.6.
Note on C163: Select whether short-circuit withstand test is to be done in accordance with IEC 60076-5.
Note on C164: Select whether Measurement of frequency response (Frequency response analysis-FRA) is to be done. The test procedure shall be agreed between purchaser and supplier.
Note on C165: Select whether check of external coating is to be done in accordance with ISO 2178 and ISO 2409 or as specified.
Note on C166: Specify whether vibration test as per IEC 60076-11, 4.2.I is required for dry type transformers
Note on C167: Purchaser to select whether a simulated on load start test is required in case of unit transformer feeding a motor. Unit transformer indicates a transformer feeding a single motor.

## Supplement
Row |  | IOGP S-720D (1.01) Data Sheet for Transformers | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95

## Guidance
IOGP S-720D (1.01) Data Sheet for
Transformers
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-720 Supplementary Specification to IEC 60076-1 Transformers.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.