## Front & preliminaries
|  |  | SPECIFICATION | August 2025
|  |  | IOGP S-754L | Version 1.0
Information Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Revision history
VERSION | DATE | PURPOSE
1 | August 2025 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-754L (1.0) Information Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-754L (1.0) Information Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Introduction
The purpose of this information requirements specification (IRS) is to specify information requirements for the procurement of liquid-immersed distribution, power and regulating transformers in accordance with IOGP S-754 for application in the petroleum and natural gas industries.
The IRS defines the information requirements, including format, timing and purpose, to be provided by the supplier. It also defines the specific conditions to be satisfied for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
The IOGP S-754 specification documents follow a common structure (as shown below) comprising a specification, also known as a technical requirements specification (TRS), a procurement data sheet (PDS), this IRS and a quality requirements specification (QRS). These four specification documents, together with the purchase order, define the overall technical specification for procurement.
JIP33 Specification for Procurement Documents Information Requirements Specification (IRS)
This IRS is to be applied in conjunction with the specification, the PDS and the QRS, referred to in this document as IOGP S-754, IOGP S-754D and IOGP S-754Q respectively. Further information on the purpose of these documents and the order of precedence for their use is provided in the introduction of the specification.

## Instructions
IOGP S-754L (1.0) Information Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS structure contents
| 1 | 'Front & preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes/No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information submission abbreviations
Column I — 'Required As Built' (Yes/No), where "Yes" chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS.
Column K — 'Translation Required' (Yes/No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable formats
Column F — 'CFIHOS Document Type Code' relates to the CFIHOS document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PDS |  | procurement data sheet
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or "manufacturer"
| TRS |  | technical requirements specification
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3. Metadata listed below is as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The unique identifier for the 'document' according to the 'owner/operator' document numbering scheme. |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document. |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised. |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision. |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision. |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision. |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision. |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type. |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification code |  |  | A code that uniquely identifies an export control classification. |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
Table 3 — Supplier deliverable metadata

## Requirements
IOGP S-754L (1.0) Information Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement.
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Document Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Requirements
S754-IR-1 | Manufacturer master information schedule |  | Information deliverables list | No | For Acceptance |  | - | - |  | -
S754-IR-2 | Delivery schedule |  | Delivery/production schedule | Yes | For Information |  | - | - |  | -
S754-IR-3 | Progress report | Required for CAS A, CAS B, CAS C | Progress report | - | - |  | - | - |  | - | Guidance Note: CAS A: For Information, CAS B: For Information, CAS C: For Information, CAS D: (N/A)
S754-IR-4 | Quality plan | Required for CAS A, CAS B | Quality plan | - | - |  | - | - |  | - | Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Information, CAS C: (N/A), CAS D: (N/A)
S754-IR-5 | Sub-supplier list | Required for CAS A, CAS B | Sub-supplier list | - | - |  | - | - |  | - | Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Information, CAS C: (N/A), CAS D: (N/A)
S754-IR-6 | Inspection and test plan (ITP) |  | Inspection and test plan (ITP) | No | For Acceptance |  | - | - |  | -
S754-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | - | - |  | - | Guidance Note: If "Long term outdoor storage" is selected on the data sheet for "Equipment preservation", update the Purpose column from "For Information" to "For Acceptance".
S754-IR-8 | Non-conformance records |  | Non-conformance records | No | For Acceptance |  | - | - |  | -
S754-IR-9 | Deviation request |  | Deviation request | Yes | For Acceptance |  | - | - |  | -
Technical Information Requirements
Calculations
S754-IR-26 | Design data |  | Design calculation | No | For Information |  | - | - |  | - | Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
S754-IR-27 | Estimated weight |  | Weight calculation | Yes | For Information |  | - | - |  | -
S754-IR-62 | Total cost of ownership (TCO) calculation |  | Design calculation | Yes | For Information |  | - | - |  | - | These TCO calculations are necessary to demonstrate that the transformer is of a low loss design. This information is used to assist in the determination of the life cycle cost (LCC) incorporating an estimated power cost data. This information is required as part of the as-built drawing package.
S754-IR-64 | Load loss calculation |  | Design calculation | Yes | For Information |  | - | - |  | -
S754-IR-65 | No-load loss calculation |  | Design calculation | Yes | For Information |  | - | - |  | -
Certificates
S754-IR-21 | Regulatory compliance certificate | Required if certifications are specified | Regulatory compliance certificate | No | For Information |  | - | - |  | - | ABS or USCG Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
S754-IR-66 | Weight certificate | Required if offshore and marine applications are specified | Weight certificate | No | For Information |  | - | - |  | -
S754-IR-69 | Hazardous area certificate | Required if a hazardous (classified) area application is specified | Hazardous area certificate | No | For Information |  | - | - |  | - | Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
S754-IR-77 | Type test certificate | Required for CAS A, CAS B, CAS C | General certificate | - | - |  | - | - |  | - | The type test certificates are required to demonstrate a bespoke or new transformer design meets the requirements as defined in IEEE C57.12.00. Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: (N/A)
S754-IR-83 | Seismic certificate | Required if a seismic certification is required due to site location | Certificate of conformance | No | For Acceptance |  | - | - |  | -
S754-IR-90 | Wash certificate |  | General certificate | No | For Information |  | - | - |  | -
Data
S754-IR-79 | Painting and coating | Required for CAS A, CAS B, CAS C | Painting and coating procedure | - | - |  | - | - |  | - | Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: (N/A)
S754-IR-29 | Manufacturer data sheet |  | Manufacturer data sheet | Yes | For Information |  | - | - |  | - | This information is required as part of the as-built drawing package.
S754-IR-63 | Insulating liquid specification |  | Material specifications | No | For Information |  | - | - |  | - | This information is required as part of the as-built drawing package.
S754-IR-60 | Application software | Required if application software is specified | Application software | No | For Information |  | - | - |  | - | Only when required by the data sheet. This includes configuration files.
S754-IR-76 | OLTC data sheet | Required if an OLTC is specified | Manufacturer data sheet | Yes | For Information |  | - | - |  | - | This information is required as part of the as-built drawing package.
S754-IR-75 | Current transformer characteristic curves |  | Curves and tables calculations | No | For Information |  | - | - |  | -
S754-IR-88 | Alarm and trip setting list |  | Alarm and trip setting list | No | For Information |  | - | - |  | -
S754-IR-89 | Safety data sheet |  | Safety data sheet | No | For Information |  | - | - |  | -
Drawings
S754-IR-22 | Bill of materials |  | Bill of materials | No | For Information |  | - | - |  | - | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings. Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
S754-IR-24 | Schematic diagram |  | Schematic diagram | No | For Acceptance |  | - | - |  | - | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings. Drawing approval required prior to the start of manufacturing.
S754-IR-25 | Wiring diagram |  | Wiring diagram | No | For Information |  | - | - |  | - | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings. Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
S754-IR-30 | Detailed drawing |  | Detailed drawing | No | For Information |  | - | - |  | - | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information.
S754-IR-33 | General arrangement drawing |  | General arrangement diagram | Yes | For Acceptance |  | - | - |  | - | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Acceptance (before start of manufacturing), CAS D: For Acceptance (before start of manufacturing).
S754-IR-34 | Installation drawing |  | Installation diagram | No | For Information |  | - | - |  | - | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information.
S754-IR-68 | Name plate drawing |  | Name plate drawing | No | For Information |  | - | - |  | - | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings. Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Acceptance (before start of manufacturing), CAS D: For Information.
S754-IR-70 | Foundation loading diagram |  | Foundation loading diagram | No | For Information |  | - | - |  | - | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
S754-IR-85 | Communication block diagram |  | Block diagram | No | For Information |  | - | - |  | - | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings. Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
Manuals
S754-IR-39 | Commissioning instruction |  | Commissioning instruction | No | For Information |  | - | - |  | - | This information provides the necessary startup details and commissioning procedures to safely energize the transformer at the installation site.
S754-IR-41 | Installation manual |  | Installation manual | No | For Information |  | - | - |  | - | Installation Manual index, if required, should be provided in first revision of the document. When index agreed, Installation manual content shall be provided in subsequent revision of the document.
S754-IR-42 | Maintenance manual |  | Maintenance manual | No | For Information |  | - | - |  | - | Maintenance Manual index, if required, should be provided in first revision of the document. When index agreed, Maintenance manual content shall be provided in subsequent revision of the document.
S754-IR-43 | Operating manual |  | Operating manual | No | For Information |  | - | - |  | - | Operating Manual index, if required, should be provided in first revision of the document. When index agreed, Operating manual content shall be provided in subsequent revision of the document.
S754-IR-73 | Spare parts list |  | Consolidated spare parts list | No | For Information |  | - | - |  | -
S754-IR-20 | Special tools list |  | Special tools list | No | For Information |  | - | - |  | - | A list of special tools required to install and maintain the equipment is required.
S754-IR-86 | Packing list |  | Packing list | No | For Information |  | - | - |  | -
Procedures
S754-IR-47 | Lifting and rigging procedure |  | Lifting procedure | No | For Information |  | - | - |  | - | Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information.
S754-IR-46 | Factory acceptance test (FAT) procedure |  | Factory acceptance test (FAT) procedure | No | For Acceptance |  | - | - |  | - | A Factory Acceptance Test (FAT) procedure is required to gain alignment on what will be tested for acceptance.
Reports
S754-IR-49 | Factory acceptance test (FAT) records |  | Factory acceptance test (FAT) records | No | For Acceptance |  | - | - |  | -
S754-IR-54 | Design test reports |  | Type test report | No | For Information |  | - | - |  | - | Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Information, CAS C: (N/A), CAS D: (N/A)
S754-IR-87 | Routine test reports | Required for CAS A, CAS B, CAS C | Performance report | - | - |  |  | - |  | - | Guidance Note: CAS A: For Acceptance (before release of shipment), CAS B: For Acceptance (before release of shipment), CAS C: For Information, CAS D: For Information.
S754-IR-56 | Additional test reports |  | Performance report | No | For Acceptance |  |  | - |  | -
S754-IR-67 | Auxiliary power consumption report | Required if auxiliary cooling equipment is provided | Utility consumption report | No | For Information |  | - | - |  | - | These reports are necessary to demonstrate that the transformer cooling accessories are of a low loss design. This information is used to assist in the determination of the life cycle cost (LCC) incorporating an estimated power cost data.
S754-IR-74 | Audible sound level report | Required if audible sound level test is specified. | Noise test records | No | For Information |  | - | - |  | -
S754-IR-91 | Seismic report |  | General report | Yes | For Information |  |  | - |  | -
S754-IR-92 | Dynamic motion and load factors report |  | General report | Yes | For Information |  |  | - |  | -
Purchase Order Specific Information Requirements

## Definitions
IOGP S-754L (1.0) Information Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Document Type Code — CFIHOS document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Requirements
S754-IR-1 | Manufacturer master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Manufacturer's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S754-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by [vendor/sub-vendors]. Schedule details typically** include; a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [vendor's] standard practice unless otherwise agreed in the contract. |  | Native | CFIHOS-70000298
S754-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S754-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] |  | PDF | CFIHOS-70000451
S754-IR-5 | Sub-supplier list | Definition of processes, products or services that will be externally provided and the controls to be applied by the [manufacturer] to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . Note: ISO 9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. |  | PDF | CFIHOS-70000455
S754-IR-6 | Inspection and test plan (ITP) | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [manufacturer], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. |  | PDF | CFIHOS-70000180
S754-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning; e. padeye/skid stress design. | 6.16.1, 6.16.3 - 6.16.6, 10.1.1 - 10.1.10, 10.2.1 | PDF | CFIHOS-70000154
S754-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S754-IR-9 | Deviation request | A request, approval or rejection of changes to this specification. A deviation request would typically include justification and reasons for the request, and acceptance or rejection. | 4.4.2 | PDF | CFIHOS-70000389
Technical Information Requirements
Calculations
S754-IR-26 | Design data | Document providing information about data, and basic conditions and assumptions used for selection of appropriate system solutions, parts or material, as well as the way these data have been processed and evaluated. Minimal design calculations include: a) inrush currents, b) ANSI damage points or curve, c) X/R ratio, d) short circuit design withstand, e) minimum and maximum impedance corresponding to minimum and maximum tap voltage, f) zero sequence impedance g) exciting current at 100% and 110% rated voltage (amperes or percent) h) voltage regulation at 1.0 and 0.8 power factor | 8.5, 12.1.4 | PDF | CFIHOS-70000086
S754-IR-27 | Estimated weight | An estimated calculation to be provided with the proposal for the weights (kg) of the transformer and the specific components as listed below. a) Core and winding b) Tank and fittings c) Insulating liquid d) OLTC (if applicable) e) Total weight (with insulating liquid) f) Transportation weight g) Center of gravity h) Details of any temporary lifting/supporting equipment i) Mass moment of inertia | 6.16.3 - 6.16.6, 10.1.1, 10.1.2 | PDF | CFIHOS-70000357
S754-IR-62 | Total cost of ownership (TCO) calculation | Document providing information about the cost of ownership of the transformer over the lifetime considering the guaranteed load and no-load losses. |  | PDF | CFIHOS-70000086
S754-IR-64 | Load loss calculation | Load loss calculation at principal tapping at 0.8 and 1.0 power factor shall be submitted by supplier for the conditions specified below. a) 50% load losses (kW) and efficiency (%). b) 75% load losses (kW) and efficiency (%). c) 100% load losses (kW) and efficiency (%). d) 125% load losses (kW) and efficiency (%). | 9.3 | PDF | CFIHOS-70000086
S754-IR-65 | No-load loss calculation | No-load loss (kW) calculation at principal tapping shall be submitted by supplier. The same shall be used for verifying the measured no load loss during inspection. | 9.3 | PDF | CFIHOS-70000086
Certificates
S754-IR-21 | Regulatory compliance certificate | A document certifying conformity to local regulations which accompanies shipment of the transformer and its accessories . e.g., Official certificate issued by manufacturer. This would include USCG, ABS, or DNV type certifications or similar designations. | 4.3.4.1, 5.12.2.4, 5.13.2 - 5.13.5, 6.6.6.2 | PDF | CFIHOS-70000079
S754-IR-66 | Weight certificate | Independent certification of correct gross weight and information detailed in API 2A-WSD and API 2A-LRFD for the transformer and all auxiliary equipment including packing materials. This is required for offshore and marine applications. This document should meet the requirements of ISO 19901-5 and include the following: a) gross weight; b) center of gravity; c) mass moments of inertia components; d) calibration certificates of weight measurement devices; e) details of any temporary lifting/supporting equipment; f) dry weight. | 10.1.1, 10.1.2, 6.16.6 | PDF | CFIHOS-70000358
S754-IR-69 | Hazardous area certificate | Certificate issued by a recognized independent authority declaring that type tests have satisfied the specified standards; (e.g., UL, CSA, NEMA). Examples of ratings include suitability for hazardous (classified) locations and all conditions of safe use (i.e., CoA or X conditions). | 4.3.5, 5.12.2.6, 6.2.3.7, 6.11.7, 6.13.3.3 | PDF | CFIHOS-70000160
S754-IR-77 | Type test certificate | If a NRTL transformer is specified, the certificate is to provide evidence that the design meets the construction, testing, and performance requirements of IEEE Std C57.12.00, including the additional requirements specified in UL XPLH. | 8.2.2, 8.2.3, Table 17 | PDF | CFIHOS-70000239
S754-IR-83 | Seismic certificate | Document providing equipment certification by third party for seismic design. | 5.13.1 | PDF | CFIHOS-70000013
S754-IR-90 | Wash certificate | A document certifying compliance with specified requirements. [e.g., certificates needed for re-certifying, occupancy certificate, product certificates]. A tanker truck wash certificate is a document verifying that a tanker truck's interior has been thoroughly cleaned and sanitized to meet specific standards. This certificate ensures the tank is free of previous cargo residue and suitable for transporting a load of insulating liquid for a high voltage transformer. | 10.2.2 | PDF | CFIHOS-70000239
Data
S754-IR-79 | Painting and coating | The Manufacturer/Supplier's painting and coating system details. The minimum information includes: a) details of all surface treatments, b) galvanizing procedure (if needed and specific parts), c) base, intermediate and final painting systems d) paint minimum thickness of each application e) verification of suitability to meet the specified environmental conditions | 4.3.4.1, 6.17 | PDF | CFIHOS-70000384
S754-IR-29 | Manufacturer data sheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. This document includes technical information describing the transformer performance characteristics such as - A specification or drawing that describes the physical equipment and technical details for the purpose of procurement or fabrication. It complements the data sheet. This includes, but is not limited to, details such as: a. transformer ratings including KVA, HV, LV, %Z, cooling class, type, temp rise, winding materials b. bushing details (HV and LV), location and configuration, surge arrestors (if applicable) c. incoming and outgoing cable requirements d. DETC/OLTC tap changer details e. control cabinets and space heater details f. specific application requirements (marine/offshore, regulatory, etc.) g. accessories list h. monitoring, metering, protective relaying, and cooling system details i. communication, networking, and condition-based monitoring (CBM) requirements k. painting system and corrosion protection method l. insulating liquid details m. weight (total, w/o insulating fluid, major components) n. details for cooling fan motors, oil pump motors, and other auxiliary motors | 4.3.4.1 - 4.3.4.3, 6.6.6.2, 6.17, 6.18.1, 6.18.9 | PDF | CFIHOS-70000416
S754-IR-63 | Insulating liquid specification | A specification providing the details for the transformer insulating liquid as listed below. a) Volume (L) b) Type (e.g., mineral oil, natural ester, synthetic, silicon oil, HFHC) c) Brand and designation d) Dielectric strength e) PCB free statement | 6.6.1 - 6.6.4, 6.6.5.1, 8.2.1.1, 8.2.1.2, 8.7, 9.1, 9.2, 10.1.3 | PDF | CFIHOS-70000215
S754-IR-60 | Application software | A computer program designed for a specific task or use including configuration, monitoring, diagnostics, controls, protective, and communication devices provided with the transformer. Examples include thermal condition, partial discharge, dissolved gas, moisture content, and thermal capacity. | 6.2.6.1 - 6.2.6.7 | Native | CFIHOS-70000012
S754-IR-76 | OLTC data sheet | Document providing information on technical data and characteristics for the OLTC if one is specified for the transformer. This document provides a structured data form containing part number/model, design information, operational data and limitations of the equipment. This document includes the following information as a minimum: a) Number of taps above and below normal b) Step voltage c) Rated frequency (Hz) d) Continuous current rating e) 3-second over-current withstand f) Power frequency withstand voltage g) BIL (referenced to ground) h) Design mechanical life (number of operations) i) Maintenance requirements j) Tap designations | 6.15 | PDF | CFIHOS-70000416
S754-IR-75 | Current transformer characteristic curves | Performance data and characteristic curves for the current transformers: show the relationship between the secondary excitation current and the secondary excitation voltage to identify the saturation voltage. Additional information includes the following: a) ratio b) accuracy class c) internal resistance | 6.3.1 | PDF | CFIHOS-70000449
S754-IR-88 | Alarm and trip setting list | Parameters for various instruments, such as dissolved gas analysis monitors, monitoring equipment, fiber optic sensor systems, and other devices, are detailed in parameter setting tables. These tables include all instrument set points and alarms. | 6.2.1.1, 6.2.1.4, 6.2.6.2.1, 6.6.3.4 - 6.6.3.6 | PDF | CFIHOS-70000007
S754-IR-89 | Safety data sheet | Datasheets which summarize the physical and chemical properties of the substances - description of their harmful nature including potential impact on the health and safety of personnel and of the environment - precautions necessary to ensure their safe use and eventual disposal. | 6.6.4.1, 6.6.4.3, 8.2.1.1, 8.2.1.2 | PDF | CFIHOS-70000211
Drawings
S754-IR-22 | Bill of materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and references to specifications. Third party components and systems will also be included. Note When agreed includes details of sub-suppliers & associated PO's. | 4.3.4, 4.3.5, 6.1.1 - 6.1.3, 6.1.5 - 6.1.15, 6.2.1.1 - 6.2.1.6, 6.2.1.8, 6.2.2 - 6.2.6, 6.3.1 - 6.3.5, 6.3.8, 6.6.1 - 6.6.3, 6.6.5.2, 6.6.6, 6.7.2.2, 6.10.1.10, 6.10.1.12, 6.10.1.21, 6.10.1.22, 6.10.2.6, 6.11, 6.12, 6.13.1.9, 6.13.1.10, 6.13.1.12 - 6.13.1.14, 6.13.2.1, 6.13.2.2, 6.13.3.1 - 6.13.3.3, 6.13.3.13, 6.14.1.2 - 6.14.1.4, 6.14.2.1,6.14.2.2, 6.14.2.4 - 6.14.2.7, 6.14.2.9, 6.14.2.10, 6.14.3.1, 6.14.3.2, 6.14.3.4 - 6.14.3.6, 6.15, 6.17, 6.18.1, 12.1.6, 12.1.7, 12.1.9 - 12.1.11 | Native | CFIHOS-70000028
S754-IR-24 | Schematic diagram | A pictorial representation of the main elements and functions of the control circuits for electrical equipment with input/output sources (e.g., switches, alarm contacts, relays, contactors) and their relationships. This includes supplementary information necessary for the understanding of functions (e.g., notes, descriptions of particular control devices or functions). | 6.2.1.1, 6.2.1.4, 6.2.3.1 - 6.2.3.3, 6.2.3.8, 6.3.1 - 6.3.9, 6.6.3.4 - 6.6.3.6, 6.6.6.3, 6.6.6.5, 6.11.1 - 6.11.8, 6.11.10 - 6.11.12, 6.13.1.1 - 6.13.1.7, 6.13.1.15, 6.13.1.16, 6.13.2, 6.13.3.6 - 6.13.3.9, 6.13.3.13 - 6.13.3.15, 6.14.2.1, 6.14.2.2, 6.14.2.4, 6.14.2.6, 6.14.3.1, 6.14.3.2, 6.14.3.4 - 6.14.3.6, 6.15.1.11, 6.15.1.12 | - | CFIHOS-70000328
S754-IR-25 | Wiring diagram | Description: Diagram providing information on the circuitry and wiring of components (e.g., cooling system, space heaters, alarm and control circuits, NGR, OLTC controls) Mandatory content of information: – Graphical symbols representing the objects; – Graphical symbols representing the connections among objects; – Reference designations; – Terminal designations; – Signal level conventions (applicable to logic signals); – Information necessary to trace paths and circuits (e.g., signal designations, location references); – Communication cable connections; – Cable and wire identification and numbering (to and from information). Optional content of information: – Reference to other documents; – Information about wiring type and protection; | 6.2.1.1, 6.2.1.4, 6.2.3.1 - 6.2.3.3, 6.2.3.8, 6.2.5.4, 6.3.1 - 6.3.9, 6.6.3.4 - 6.6.3.6, 6.6.6.3, 6.6.6.5, 6.11.1 - 6.11.8, 6.11.10 - 6.11.12, 6.13.1.1 - 6.13.1.7, 6.13.1.9, 6.13.1.10, 6.13.1.15, 6.13.1.16, 6.13.2, 6.13.3.6 - 6.13.3.9, 6.13.3.13 - 6.13.3.15, 6.14.2.1, 6.14.2.2, 6.14.2.4, 6.14.2.6, 6.14.3.1, 6.14.3.2, 6.14.3.4 - 6.14.3.6, 6.15.1.11, 6.15.1.12 | Native | CFIHOS-70000268
S754-IR-30 | Detailed drawing | Drawing showing parts of a component, generally enlarged, and including specific information about the form and the assembly. Also supports other documents where a cross-sectional view or part list is necessary for clarity. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. Components requiring detailed drawings include primary and secondary bushings, cable and conductor terminations, current transformers, surge arrestors, accessories, NGR, OLTC, control cabinet details, etc. Drawings for the transformer tank, base, ATC, throat, and other fabricated items shall show all dimensions. Structural and lifting drawings are to show all structural elements, connection details, and precise details of fixed or removable pad eyes used for installation and maintenance. Any temporary lifting beams or spreader frames that have restrictions on the loads and sling angles must be identified in detail. Anchoring details for attaching the transformer to the foundation. | 4.3.4.1, 4.3.5, 6.1.1 - 6.1.3, 6.1.5 - 6.1.10, 6.1.13 - 6.1.15, 6.2.1, 6.2.2, 6.2.3.2 - 6.2.3.6, 6.2.3.8, 6.2.4, 6.2.5.2 - 6.2.5.8, 6.2.6.1 - 6.2.6.7, 6.3.5 - 6.3.9, 6.6.3.7.5, 6.6.6, 6.8 - 6.12, 6.13.1.15, 6.13.1.16, 6.13.2, 6.13.3.5 - 6.13.3.9, 6.13.3.12, 6.13.3.14, 6.13.3.15, 6.14.2.1, 6.14.2.2, 6.14.2.4 - 6.14.2.7, 6.14.2.9, 6.14.2.10, 6.14.3, 6.15.1.1 - 6.15.1.6, 6.15.1.11, 6.15.1.12, 6.15.2, 6.15.3.2, 6.18.2 - 6.18.8, 12.1.5 - 12.1.11, 12.1.13 | Native | CFIHOS-70000438
S754-IR-33 | General arrangement drawing | A drawing showing overall dimensions of the transformer, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing shall contain reference to main specifications and standards. For equipment / components the drawing may include cross sectional views. Document may contain the following information: • Main dimensions; • ATC dimensions; • Interface connections; • Estimated weight; • Quantity of insulating fluid (total and per compartment or tank); • Center of gravity (filled with insulating liquid); • Withdrawal/installation and maintenance space; • Installation and mounting details; • Location of manholes and handholes; • Lifting arrangement; • Untanking height (large units); • Bushing arrangement and termination; • Arrestor locations (if applicable); • Cooling fan locations and controls (if applicable); • Current transformer locations (if applicable); • Ground pad locations; • Ground resistor details, including dimensions, weights, and mounting requirements (if applicable); • Primary and secondary termination details; • Accessories general location and arrangement; • Size and location of conduit or cable entrances for Company connections. | 4.3.4, 4.3.5, 5.12.1, 5.12.2.1, 6.1.1 - 6.1.3, 6.1.6 - 6.1.10, 6.1.13 - 6.1.15, 6.2.1, 6.2.2, 6.2.3.4 - 6.2.3.6, 6.2.4.1, 6.2.4.2, 6.2.5.2 - 6.2.5.8, 6.2.6.3 - 6.2.6.5, 6.2.6.7, 6.3.1, 6.3.8, 6.6.2, 6.6.3, 6.6.5, 6.6.6, 6.7.2.2, 6.7.3, 6.8 - 6.10, 6.11.8, 6.11.9, 6.12, 6.13.1.11 - 6.13.1.16, 6.13.2.1, 6.13.2.2, 6.13.3.1 - 6.13.3.5, 6.13.3.10, 6.13.3.11, 6.14.1.2 - 6.14.1.6, 6.14.2.1 - 6.14.2.3, 6.14.2.5, 6.14.2.7, 6.14.3.1, 6.14.3.3, 6.14.3.4, 6.15.1.1, 6.15.1.4 - 6.15.1.6, 6.16, 6.18, 12.1.5 - 12.1.11, 12.1.13 | Native | CFIHOS-70000153
S754-IR-34 | Installation drawing | Installation drawings illustrate the assembly of components at site to the main transformer tank to complete the transformer assembly. These drawings provide the details for mounting, setting, erection, etc. of the transformer and all shipped separate accessories. These diagrams are for transient activity during installation (e.g. sequence of activity) and not finished work. | 6.17.3 | Native | CFIHOS-70000119
S754-IR-68 | Name plate drawing | A drawing that depicts the contents and information provided on the rating plate. | 4.3.4.1, 4.3.5, 5.12.1, 5.12.2, 5.13.2, 5.13.3, 6.1.12, 6.6.1, 6.15.1.10 | PDF | CFIHOS-70000445
S754-IR-70 | Foundation loading diagram | A diagram detailing static and dynamic forces or movements acting on foundations or other load bearing supports, anchor bolt details, lengths and pre-tensioning. May include Civil Structural for loads imposed, and Civil Foundations for foundation design. | 6.16.2, 6.16.3, 6.16.5 | PDF | CFIHOS-70000151
S754-IR-85 | Communication block diagram | The communication block diagram depicts the interconnected networks, cables and connections. Mandatory content of information includes: a. direction of main interfaces between communication equipment items; b. denomination of incoming and outgoing communication circuits; c. communication protocol designations and details (e.g. routers, hubs, ports, switches). d. communication system power supply details. | 6.2.6.1.2, 6.2.6.2.2, 6.2.6.3.2, 6.2.6.4.4, 6.2.6.5.3, 6.2.6.6 | Native | CFIHOS-70000237
Manuals
S754-IR-39 | Commissioning instruction | Instructions providing information on the commissioning of the transformer and all accessories. Instructions for commissioning are provided especially for large transformers in industrial applications. The purpose of such instructions is to provide the user with the information needed for initial setting-up of the product. |  | PDF | CFIHOS-70000366
S754-IR-41 | Installation manual | Description of methods of installing the transformer. Installation refers to the mounting, setting, erection, etc. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand-alone document. Note: Installation details for Auxiliary devices not pre-installed (e.g. temperature, fluid level, sudden pressure and monitor rapid relief, switches, and indicating devices) to be included in the installation manual. Complete installation instructions for parts shipped separately from tank and core assembly to accompany transformer shipment. | 6.2.6.8, 6.6.3.7.5, 10.1.8 - 10.1.10, 10.2.1 | PDF | CFIHOS-70000181
S754-IR-42 | Maintenance manual | Description of methods of maintaining the transformer and its accessories (e.g. NGR, OLTC, CBM). Typically originates from the equipment or package supplier. This would include recommended insulating liquid testing and evaluation procedures. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand-alone document. | 4.4.1, 6.1.1 - 6.1.3, 6.2.1.3, 6.2.1.6, 6.2.1.7, 6.2.4.3, 6.2.4.4, 6.2.5.1, 6.2.6.1 - 6.2.6.7, 6.6.2, 6.6.3, 6.6.6.4, 6.6.6.5, 6.10.1.21, 6.10.1.22, 6.11.10 - 6.11.12, 6.12, 6.14.1.2 - 6.14.1.5, 6.14.3.1, 6.14.3.2, 6.14.3.4, 6.14.3.6, 6.15.1.1 - 6.15.1.10, 6.15.2, 6.15.3.1, 10.1.3 - 10.1.7 | PDF | CFIHOS-70000206
S754-IR-43 | Operating manual | Description of methods of operating the transformer and its accessories (e.g. OLTC, CBM), including but not limited to control narrative, instructions, procedures, drawings, tables, etc. for the operation, stop, start, and emergency shutdown. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand-alone document. | 4.4.1, 6.2.1.3, 6.2.1.6, 6.2.1.7, 6.2.4.3, 6.2.4.4, 6.2.5.1, 6.2.6, 6.6.2, 6.6.3, 6.6.6.4, 6.6.6.5, 6.11.10 - 6.11.12, 6.12, 6.14.1.2 - 6.14.1.4, 6.14.2.4, 6.14.3.1, 6.14.3.2, 6.14.3.4, 6.14.3.6, 6.15.1.1 - 6.15.1.10, 6.15.2, 6.15.3.1, 10.1.3 - 10.1.7 | PDF | CFIHOS-70000228
S754-IR-73 | Spare parts list | A complete spare parts list for the transformer and all of the accessories necessary to support the installation, commissioning, start-up, and maintenance support. |  | Native | CFIHOS-70000420
S754-IR-20 | Special tools list | The Special Tools List shall identify all special tools necessary for handling, installation, repair, and maintenance of the transformer and its accessories. The Special Tools List shall include: • Identification - the tag number the special tool shall support • Description of the special tool • Storage, i.e. the location where the special tool can be found • Document references, if applicable Note that the actual special tool shall be marked with the identification, i.e. tag number that it supports. |  | PDF | CFIHOS-70000454
S754-IR-86 | Packing list | A detailed list of the equipment being packaged and shipped. | 10.1.2, 10.1.4, 10.1.7 | PDF | CFIHOS-70000269
Procedures
S754-IR-47 | Lifting and rigging procedure | The manufacturer proposed lifting requirements and handling methods. Drawings shall be provided indicating lifting points for the transformer, spreader bar requirements (if needed), center of gravity (with or without insulating fluid as shipped), gross weight, tag line locations, tilt restrictions, impact limitations, and dimensions. Similar information is required for other components shipped separately. | 6.16.1, 6.16.3 - 6.16.6, 10.1.1, 10.1.2 | PDF | CFIHOS-70000200
S754-IR-46 | Factory acceptance test (FAT) procedure | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. As a minimum, this document shall include all testing activities identified as routine in IEEE Std C57.12.00 or CSA standards and their acceptance criteria according to applicable standards, specifications and requirements to document the condition of the equipment as tested from factory. This document shall also include all tests identified in the Additional testing section of the PDS. Test set-up and test equipment shall be defined. Suppliers standard (routine) test procedures should be used as far as possible. This will include all the functional tests as specific in the technical specification. | 8.2.1, 8.5, 8.7, 9.1 - 9.3, 12.1.12 | PDF | CFIHOS-70000427
Reports
S754-IR-49 | Factory acceptance test (FAT) records | The FAT report will be used to verify that the equipment has been tested according to FAT procedure. The FAT report will be used for acceptance of the equipment delivery This document shall include all testing activities and their acceptance criteria according, , in accordance with the FAT procedure, to applicable standards, specifications and requirements,. to document the condition of the equipment as tested from factory. Test set-up and test equipment shall be defined. | 6.8, 6.13.1.8, 6.13.1.10, 6.13.1.11, 6.13.1.13, 6.13.1.14, 6.13.3.12, 6.14.1.1, 6.14.1.6, 6.14.2.8 - 6.14.2.10, 8.2.1, 8.5, 8.7, 9.1 - 9.3, 12.1.12 | PDF | CFIHOS-70000429
S754-IR-54 | Design test reports | The results of design tests (type tests) performed to provide evidence that the design meets the requirements of the functional specification. These design test requirements are specified in IEEE C57.12.00 or CSA standards. When specified, design (type) tests shall be independently verified by a third part and supported by a Certificate of Conformance (CFIHOS-70000013) | 6.1.4, 8.5 | PDF | CFIHOS-70000245
S754-IR-87 | Routine test reports | The results of the routine tests (production tests) performed to provide evidence that the manufactured transformer meets the requirements of the functional specification. These routine test requirements are specified in IEEE C57.12.00 or applicable CSA standards. Mandatory content of information: – Date of testing. – Ambient conditions – Test equipment calibration information – Signature of person responsible for test. – Object identification (type, series number, etc.) – Test procedure. – Measured values including oscillograms – Pass / Fail indication per test procedure. – Modifications made for repeated tests (due to failure) | 6.8, 8.2.1, 8.5, 8.7, 9.1 - 9.3, 12.1.12 | PDF | CFIHOS-70000449
S754-IR-56 | Additional test reports | The results of the specified additional tests performed to provide evidence that the manufactured transformer meets the requirements of the functional specification. These additional test requirements are specified in IEEE C57.12.00 or the applicable CSA standards. The additional tests (other tests) are selected individually in the data sheet. Mandatory content of information: – Date of testing. – Ambient conditions – Test equipment calibration information – Signature of person responsible for test. – Object identification (type, series number, etc.) – Test procedure. – Measured values including oscillograms – Pass / Fail indication per test procedure. – Modifications made for repeated tests (due to failure) | 6.8, 8.2.1, 8.5, 8.7, 9.1 - 9.3, 12.1.12 | PDF | CFIHOS-70000449
S754-IR-67 | Auxiliary power consumption report | Document providing power consumption of cooling fans, control cabinet(s), enclosure space heaters, OLTC and remote tap changer control cabinet where applicable |  | PDF | CFIHOS-70000203
S754-IR-74 | Audible sound level report | Transformer audible sound levels for the specified conditions, based on type tests, are to be provided: a) sound level (dB) at the self-cooled rating b) sound level (dB) at FOA rating(s) with cooling fans operational | Table 17 | PDF | CFIHOS-70000245
S754-IR-91 | Seismic report | Report provided by the manufacturer, providing equipment compliance to IEEE Std 693 for seismic design. | 5.13.1 | PDF | CFIHOS-70000259
S754-IR-92 | Dynamic motion and load factors report | Report provided by the manufacturer, providing information demonstrating that the equipment is in accordance with the applicable requirements in API 2A-WSD and API 2A-LRFD for minimizing the risk of damage from the specified dynamic motion and load factors (e.g., static/dynamic tilt, period, lateral/vertical acceleration) necessary for floating offshore and marine-ship applications. | 6.16.6 | PDF | CFIHOS-70000259
Purchase Order Specific Information Requirements

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Document Type Code
Hard Copy
Native
PDF
-