## Front & preliminaries
|  |  | SPECIFICATION | August 2025
|  |  | IOGP S-754D | Version 1.0
Procurement Data Sheet for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Revision history
VERSION | DATE | PURPOSE
1 | August 2025 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-754D (1.0) Procurement Data Sheet for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-754D (1.0) Procurement Data Sheet for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Introduction
The purpose of this procurement data sheet (PDS) is to specify purchaser-specific requirements for the procurement of liquid-immersed distribution, power and regulating transformers in accordance with IOGP S-754 for application in the petroleum and natural gas industries.
The PDS provides requirements where the specification requires the purchaser to define an application-specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser-supplied documents can be listed in the PDS to define scope and technical requirements for enquiry and purchase of the equipment.
The IOGP S-754 specification documents follow a common structure (as shown below) comprising a specification, also known as a technical requirements specification (TRS), this PDS, an information requirements specification (IRS) and a quality requirements specification (QRS). These four specification documents, together with the purchase order, define the overall technical specification for procurement.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)
This PDS is to be applied in conjunction with the specification, the IRS and the QRS, referred to in this document as IOGP S-754, IOGP S-754L and IOGP S-754Q respectively. Further information on the purpose of these documents and the order of precedence for their use is provided in the introduction of the specification.
This PDS consists of 3 worksheets. Complete the Tab for your specific transformer type. Guidance for the selection of the transformer type is provided in the table below.
PDS Power | Liquid-Immersed Power Transformers |  | 10 MVA to 150 MVA
PDS Distribution | Liquid-Immersed Distribution Substation Transformers |  | 300 kVA to 10 MVA
PDS Pad-mounted | Pad-mounted, Self-Cooled Transformers |  | Totally enclosed, compartmentalized up to 10 MVA

## PDS Power
Row | IOGP S-754D (1.0) Procurement Data Sheet for Power Transformers (IEEE) | [6 empty] | Issue
2 | Ref. clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Equipment identification
4 | 5.12.2 | Tag number : | input data |  | input data
5 | 5.12.2 | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Site conditions
9 | 4.1.2.1, 4.3.1, 4.4.1, 5.10, 6.11.5 | Maximum ambient air temperature : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50 | 55 | other
10 | 4.1.2.2, 4.3.1, 4.4.1 | Minimum ambient air temperature : | -20 | °C | -20 | °C |  |  |  |  | select | -20 | -30 | -40 | other
11 | 4.1.2.1, 4.3.1, 4.4.1, 5.10 | Ambient 24-hour average temperature : | 30 | °C | 30 | °C |  |  |  |  | select | 30 | 40 | 45 | 50 | other
12 | 4.3.1, 4.3.2, 4.4.1, 5.10, 5.12.2.5, Table 1 | Altitude of installation : | ≤ 1000 | m | ≤ 1000 | m |  |  |  |  | select | ≤ 1000 | other
13 | 4.3.3, 5.13.1 | Seismic design : | not required |  | not required | [5 empty] | select | required | not required
14 | 4.3.3, 5.13.1, 5.13.5 | Seismic site location : | input data |  | input data
15 | 4.3.3, 5.13.1 | Seismic certificate : | not required |  | not required | [5 empty] | select | required | not required
16 | 4.3.3, 4.3.5, 5.12.2.6, 6.2.3.6, 6.11.7 | Area classification : | unclassified |  | unclassified | [5 empty] | select | unclassified | classified
17 | 4.1.7, 4.4.1, 5.10 | Installation environment : | outdoor |  | outdoor | [5 empty] | select | indoor | outdoor
18 | 4.3.3, 4.3.4, 4.4.1, 5.13.4, 5.13.5, 6.6.6.2, 6.16.6, 6.17.1, 6.17.2 | Application/operating environment : | select |  | select | [5 empty] | select | onshore | offshore - fixed | offshore - floating | marine - ship | other
19 | 4.3.3, 4.4.1, 5.13.5, 6.17.1 | Unusual environments : | none |  | none | [5 empty] | select | none | corrosive gases | fumes / vapor / steam / salt air | excessive harmonics | hot and humid climates | abnormal vibration/shock/tilting | other or multiple
20 | 4.1.9 | Paint color : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | ANSI 61 grey | other
21 | 5.13.2, 5.13.4, 9.3 | Certification : | not required |  | not required | [5 empty] | select | not required | NRTL | USCG/ABS | other
22 | 5.13.3 | Compliance with Canadian standards : | not applicable |  | not applicable | [5 empty] | select | not applicable | CAN/CSA C2.1:06 | CAN/CSA C88 | CAN/CSA C227.4
23 |  | Ratings and system parameters
24 | 5.10, 5.4.2, 9.3, Table 2 | kVA rating : | input data | kVA | input data | kVA
25 | 5.1, 5.10 | Cooling class : | ONAN |  | ONAN | [5 empty] | select | ONAN | ONAN/ONAF | ONAN/ONAF1/ONAF2 | KNAN | KNAF | other
26 | 6.9, 7.4 | Winding material : | select |  | select | [5 empty] | select | copper | aluminum
27 | 5.1 | Primary winding voltage : | input data | kV | input data | kV
28 | 5.6, 5.10 | Primary winding configuration : | select |  | select | [5 empty] | select | delta | wye
29 | 5.10, 5.10.2.1 | Primary winding BIL : | input data | kV | input data | kV
30 | 5.10.3.2, 5.10.3.4, 6.8 | Primary neutral grounding : | select |  | select | [5 empty] | select | not applicable | solidly grounded | resistance grounded | ungrounded | other
31 | 5.10, Table 3, Table 4 | Secondary 1 winding voltage : | input data | kV | input data | kV
32 | 5.6, 5.10 | Secondary 1 winding configuration : | select |  | select | [5 empty] | select | delta | wye
33 | 5.10, Table 3, Table 4 | Secondary 1 winding BIL : | input data | kV | input data | kV
34 | 5.10.3.2, 5.10.3.4, 6.8 | Secondary 1 neutral grounding : | select |  | select | [5 empty] | select | not applicable | solidly grounded | low resistance grounded | high resistance grounded | ungrounded | other
35 | 5.10, Table 3, Table 4 | Secondary 2 winding voltage : | input data | kV | input data | kV
36 | 5.6, 5.10 | Secondary 2 winding configuration : | none |  | none | [5 empty] | select | delta | wye | none
37 | 5.10, Table 3, Table 4 | Secondary 2 winding BIL : | input data | kV | input data | kV
38 | 5.10.3.2, 5.10.3.4, 6.8 | Secondary 2 neutral grounding : | not applicable |  | not applicable | [5 empty] | select | not applicable | solidly grounded | low resistance grounded | high resistance grounded | ungrounded | other
39 | 5.10, Table 3, Table 4 | Tertiary winding voltage : | input data | kV | input data | kV
40 | 5.6, 5.10 | Tertiary winding configuration : | not applicable |  | not applicable | [5 empty] | select | delta | wye | not applicable
41 | 5.10, Table 3, Table 4 | Tertiary winding BIL : | input data | kV | input data | kV
42 | 5.2, 5.10 | Frequency : | 60 | Hz | 60 | Hz |  |  |  |  | select | 50 | 60 | other
43 | 5.8, 9.2, 12.1.4 | Impedance : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
44 | 8.2.5, Table C.1, Table C.2 | Audible sound level : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
45 | 7.1.5.5, 12.1.4 | Available fault current (symmetrical) : | input data | kA | input data | kA
46 | 7.1.5.2, 12.1.4 | System X/R ratio : | input data |  | input data
47 | 4.1.5 | Supply non-linear loads : | no |  | no | [5 empty] | select | no | yes
48 | 4.1.8 | Load application : | step-down |  | step-down | [5 empty] | select | step-down | step-up | generator step-up | system tie | other
49 | 4.3.3, 9.2 | Unusual service conditions : | none |  | none | [5 empty] | select | none | parallel operation | over 110% rated voltage | over 110% volts/hertz | other
50 | 6.2.5 | Grounding resistor provided/installed : | no |  | no | [5 empty] | select | no | yes
51 | 6.2.3, 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Auxiliary power : | 120 | V ac | 120 | V ac |  |  |  |  | select | 120 | 208 | 240 | other
52 | 5.10.3.2 | Neutral bushing grounding connection for solidly grounded systems : | grounded to ground pad with removable strap |  | grounded to ground pad with removable strap | [5 empty] | select | grounded to ground pad with removable strap | none
53 |  | Cooling system
54 | 6.6.1, 6.6.4, 6.15.1.10, 8.2.1, 8.2.1.1, 8.2.1.2 | Insulating liquid : | mineral oil |  | mineral oil | [5 empty] | select | mineral oil | natural ester | synthetic ester | silicone fluid | other
55 | 6.2.1.6, 6.6.2, 6.6.3, 6.6.6 | Liquid preservation system : | sealed-tank |  | sealed-tank | [5 empty] | select | sealed-tank | conservator | inert gas pressure system
56 | 6.14.1 | Radiator type : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | tube type | pancake type
57 | 4.3.3 | Radiator material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | galvanized steel | stainless steel
58 | 6.14.1.2 - 6.14.1.5 | Removable radiators : | no |  | no | [5 empty] | select | yes | no
59 | 6.14.2, 6.14.3 | Provision for fans : | no |  | no | [5 empty] | select | yes | no
60 | 6.2.3.8 | Fan monitoring system : | no |  | no | [5 empty] | select | yes | no
61 |  | Tap changer
62 | 6.15.1.1 | OLTC manufacturer : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
63 | 6.2, 6.15.1.11, 8.3.2 | Tap changer type : | DETC |  | DETC | [5 empty] | select | none | DETC | OLTC | bolted links
64 | Table 6 | Tap changer location : | primary winding |  | primary winding | [5 empty] | select | none | primary winding | secondary winding
65 |  | Tap changer operation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | operable from base level | other
66 | 1.4.1, 6.15.1.1 - 6.15.1.10, 6.15.1.12, 6.15.2 | OLTC switching : | vacuum |  | vacuum | [5 empty] | select | not applicable | vacuum | other
67 | 6.15.3.2 | OLTC remote control panel : | no |  | no | [5 empty] | select | no | yes
68 | 6.2.6.8 | OLTC interface connection : | digital communication |  | digital communication | [5 empty] | select | digital communication | hardwired | none
69 | 6.15.3.1 | OLTC parallel operation : | no |  | no | [5 empty] | select | no | yes
70 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | OLTC cabinet space heaters : | not required |  | not required | [5 empty] | select | not required | required
71 |  | Bushings
72 | 6.1, 6.10.1.3, 6.10.2.1, 6.10.2.2, 6.10.2.4 - 6.10.2.6, 12.1.5 | Primary bushing location : | select |  | select | [5 empty] | select | cover (exposed) | side (ATC) | side (throat) | side (iso phase)
73 | 6.1, 6.10.1.3, 6.10.2.1, 6.10.2.2, 6.10.2.4 - 6.10.2.6, 12.1.5 | Secondary bushing location : | select |  | select | [5 empty] | select | cover (exposed) | side (ATC) | side (throat) | side (iso phase)
74 | 5.10.3.5, 6.1, 6.10.1.3, 6.10.2.1, 6.10.2.2, 6.10.2.4 - 6.10.2.6 | Neutral bushing location : | select |  | select | [5 empty] | select | cover (exposed) | side (ATC) | side (throat) | inside tank
75 | 5.10.3.4 | Primary bushing BIL : | input data | kV | input data | kV
76 | 5.10.3.4 | Secondary bushing BIL : | input data | kV | input data | kV
77 | 5.10.3.4 | Neutral bushing BIL : | input data | kV | input data | kV
78 | 6.1.15 | Creepage distance : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | light contamination | heavy contamination | manufacturer's standard
79 | 6.3 | Primary current transformer (CT) function : | not applicable |  | not applicable | [5 empty] | select | metering | relaying | revenue | not applicable
80 | 6.3 | Secondary current transformer (CT) function : | not applicable |  | not applicable | [5 empty] | select | metering | relaying | revenue | not applicable
81 | 6.3 | Neutral current transformer (CT) function : | not applicable |  | not applicable | [5 empty] | select | metering | relaying | revenue | not applicable
82 | 6.12, 12.1.11 | Primary arrester class : | not applicable |  | not applicable | [5 empty] | select | substation | intermediate | distribution | not applicable
83 | 6.12, 12.1.11 | Secondary arrester class : | not applicable |  | not applicable | [5 empty] | select | substation | intermediate | distribution | not applicable
84 |  | Air terminal chamber (ATC)
85 | 6.10.1.20 | ATC type : | select |  | select | [5 empty] | select | manufacturer's standard | full height | other | not applicable
86 | 6.10.1.2, 6.10.1.7, 6.10.1.10, 6.10.1.11, 6.10.1.17 | Enclosure rating : | NEMA 3R |  | NEMA 3R | [5 empty] | select | NEMA 3R | NEMA 4 | NEMA 4X
87 | 6.10.1.4, 6.10.1.6, 6.10.1.9 | Enclosure material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | aluminum | 316L stainless steel
88 | 6.10.1.1, 6.10.1.2, 6.10.1.5, 6.10.1.6, 6.10.1.13, 6.10.1.15, 6.10.1.16 - 6.10.1.18 | Enclosure cover : | bolted |  | bolted | [5 empty] | select | bolted | hinged | bolted and hinged
89 | 6.10.1.4 - 6.10.1.8 | Primary cable entry : | bottom |  | bottom | [5 empty] | select | bottom | top | side
90 | 6.10.1.4 - 6.10.1.8 | Secondary cable entry : | bottom |  | bottom | [5 empty] | select | bottom | top | side
91 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heaters : | not required |  | not required | [5 empty] | select | not required | required
92 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heater thermostat : | not required |  | not required | [5 empty] | select | not required | required
93 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heater ammeter : | not required |  | not required | [5 empty] | select | not required | required
94 |  | Power connections
95 | 6.1.5, 6.10.2.3 | Primary connection : | select |  | select | [5 empty] | select | cable | cable bus (throat) | bus duct (throat) | iso phase duct
96 | 6.1.5, 6.10.2.3 | Secondary connection : | select |  | select | [5 empty] | select | cable | cable bus (throat) | bus duct (throat) | iso phase duct
97 | 6.1.5, 6.10.2.3 | Neutral connection : | none |  | none | [5 empty] | select | cable | cable bus (throat) | bus duct (throat) | iso phase duct
98 | 6.1.5 | Primary conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil | in. | mm
99 | 6.1.5 | Secondary conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil | in. | mm
100 | 6.1.5 | Neutral conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil | in. | mm
101 | 6.9 | Primary conductor material : | select |  | select | [5 empty] | select | copper | aluminum
102 | 6.9 | Secondary conductor material : | select |  | select | [5 empty] | select | copper | aluminum
103 | 6.9 | Neutral conductor material : | select |  | select | [5 empty] | select | copper | aluminum
104 | 6.1.5 | Number of primary conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
105 | 6.1.5 | Number of secondary conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
106 | 6.1.5 | Number of neutral conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
107 | 6.1.5 | Ground conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil
108 | 6.1.5 | Number of ground conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
109 |  | Accessories
110 | 6.2.4 | Sudden pressure relay (SPR) : | not required |  | not required | [5 empty] | select | not required | required
111 | 6.2 | Winding temperature indicator : | select |  | select | [5 empty] | select | not required | required
112 | 6.2.6.1, 6.2.6.8 | Insulating liquid temperature monitoring : | not required |  | not required | [5 empty] | select | not required | required
113 | 6.2.6.2, 6.2.6.8 | Winding temperature monitoring : | not required |  | not required | [5 empty] | select | not required | required
114 | 6.2.6.3, 6.2.6.8 | Cable termination thermal monitoring : | not required |  | not required | [5 empty] | select | not required | required
115 | 6.2.6.4, 6.2.6.8 | Dissolved gas monitoring : | not required |  | not required | [5 empty] | select | not required | required
116 | 6.2.6.5, 6.2.6.8 | Moisture in oil monitoring : | not required |  | not required | [5 empty] | select | not required | required
117 | 6.2.6.6, 6.2.6.8 | Partial discharge monitoring : | not required |  | not required | [5 empty] | select | not required | required
118 | 6.2.6.7 | Conservator membrane monitoring : | not required |  | not required | [5 empty] | select | not required | required
119 | 6.10.1.21, 6.10.1.22 | Thermal scanning inspection windows : | not required |  | not required | [5 empty] | select | not required | required
120 |  | Application software : | not required |  | not required | [5 empty] | select | not required | required
121 | 6.2.6.1.2, 6.2.6.4.4, 6.2.6.5.3, 6.2.6.6, 6.2.6.8 | Communication media : | select |  | select | [5 empty] | select | Ethernet copper | Ethernet fiber | serial | multiple | other
122 | 6.2.6.1.2, 6.2.6.4.4, 6.2.6.5.3, 6.2.6.6, 6.2.6.8 | Communication protocol : | select |  | select | [5 empty] | select | PROFIBUS | PROFINET | Modbus TCP/IP | IEC 61850 | multiple | other
123 | 6.2.1.8 | Onshore pressure-relief directional shroud and piping : | not required |  | not required | [5 empty] | select | not required | required
124 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heaters for control cabinets and throats : | not required |  | not required | [5 empty] | select | not required | required
125 |  | Supplemental testing
126 | 8.2.1.4, 8.2.2, 8.2.3, 8.2.5, Table 17 | Audible sound level : | not required |  | not required | [5 empty] | select | not required | required
127 | 8.2.1.4, 8.2.2, 8.2.3, 8.5, Table 17 | Temperature rise : | not required |  | not required | [5 empty] | select | not required | required
128 | 5.10.7.1, 8.2.1.4, 8.2.2, 8.2.3, Table 17 | Lightning impulse : | not required |  | not required | [5 empty] | select | not required | required
129 | 5.10.2.2, 8.2.1.4, 8.2.2, 8.2.3, Table 17, Table 5 | Switching impulse : | not required |  | not required | [5 empty] | select | not required | required
130 | 8.2.1.4, 8.2.3, Table 17, Table 18 | No-load losses at 110% of rated voltage : | not required |  | not required | [5 empty] | select | not required | required
131 | 8.2.1.4, 8.2.2, 8.2.3, Table 17 | Partial discharge : | not required |  | not required | [5 empty] | select | not required | required
132 | 8.2.1.4, 8.2.1.7, 8.2.3, Table 17 | Frequency response analysis : | not required |  | not required | [5 empty] | select | not required | required
133 | 8.2.1.4, 8.2.3, Table 17 | Short-circuit capability : | not required |  | not required | [5 empty] | select | not required | required | third-party
134 | 6.2.6.5.1, 8.2.1, 8.2.1.1, 8.2.1.2, 8.2.1.4, 8.2.3, Table 17 | Dissolved gas-in-oil analysis (DGA) : | required |  | required | [5 empty] | select | not required | required
135 |  | Shipping and preservation
136 | 10.1.1 - 10.1.10, 10.2.1 | Equipment preservation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | long term outdoor storage | special
137 | 10.1.7 | Impact recorder : | not required |  | not required | [5 empty] | select | not required | required
138 | 10.1.10 | Desiccant bags installed : | required |  | required | [5 empty] | select | not required | required
139 | 10.1.7 | Car seals on valves : | not required |  | not required | [5 empty] | select | not required | required
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the tag.
Note on C7: Select CAS level to be applied in IOGP S-754Q, Annex A. Default value : D
Note on C9: Select the maximum ambient air temperature of the air that is cooling the radiators. The default value as per IEEE Std C57.12.00 is 40 °C. If "other" is selected, specify the maximum limit in the "Additional notes" column. Default value : 40
Note on C10: Select the minimum ambient air temperature. Ambient temperatures below -20 °C are considered unusual service conditions. If "other" is selected, specify the minimum limit ( i.e., below -20 °C) in the "Additional notes" column. Default value : -20
Note on C11: Select the average 24-hour ambient air temperature of the air that is cooling the radiators. The default value as per IEEE Std C57.12.00 is 30 °C. If "other" is selected, specify the average ambient in the "Additional notes" column. Default value : 30
Note on C12: Select the transformer installation altitude. IEEE Std C57.12.00 is based on the maximum altitude of 1000 m (3300 ft). Derating information is provided in Table 1. If "other" is selected, specify the altitude in the "Additional notes" column. Default value : ≤ 1000
Note on C13: Select whether the seismic design is required. Additional information as per IEEE Std 693, such as seismic qualification level or the seismic exposure map information, should be provided in the "Additional notes" column. Default value : not required
Note on C14: Specify the site physical address or latitude and longitude to determine the seismic qualification level and additional parameters.
Note on C15: Select whether a third-party seismic certificate is required. Default value : not required
Note on C16: Select whether the transformer is installed in a hazardous (classified) area. If "classified", specify the Division/Zone, Group and AIT for the installation location in the "Additional notes" column. Default value : unclassified
Note on C17: Select whether the transformer is installed indoor or outdoor. Default value : outdoor
Note on C18: Select the operating environment for the transformer. If "other" is selected, specify the operating environment in the "Additional notes" column.
Note on C19: Select the unusual environments or contaminant to which the transformer will be exposed. If "other or multiple" is selected, specify in the "Additional notes" column. Default value : none
Note on C20: Select the paint color for the transformer. ANSI 61 grey refers to the paint color specified in ASTM D1535 (Munsell Notation 8.3G 6.10/0.54). If "other" is selected, specify the paint color using the ANSI designation in the "Additional notes" column. Default value : manufacturer's standard
Note on C21: Select the certification requirements for the transformer. If "other" is selected, specify in the "Additional notes" column. NRTL certification in accordance with UL guideline XPLH applies only to distribution transformers rated 69 kV or below. Default value : not required
Note on C22: Select the Canadian standard to which the transformer will be built. Default value : not applicable
Note on C24: Select the base kVA rating for the transformer. The preferred continuous base kVA ratings are listed in Table 2.
Note on C25: Select the transformer cooling class. If "other" is selected, specify the method of cooling in the "Additional notes" column. Default value : ONAN
Note on C26: Select the base material for the transformer windings. Copper is normally used for power transformer windings and aluminum is used for distribution and pad-mounted transformers.
Note on C27: Specify the value of the voltage in kV for the primary winding. The preferred values for nominal system voltages are given in Table 3 and Table 4.
Note on C28: Select the winding configuration for the transformer primary windings. Standard connection arrangements for particular types of transformers are in IEEE Std C57.12.70.
Note on C29: Specify the basic lightning impulse insulation level (BIL). BIL is dependent on the degree of exposure of the transformer and characteristics of the overvoltage protection system. Refer to Table 3 and Table 4 for guidance.
Note on C30: Select the transformer neutral grounding arrangement for the transformer primary winding. Select "not applicable" for a delta winding configuration. If "other" is selected, indicate the grounding type in the "Additional notes" column.
Note on C31: Specify the value of the voltage in kV for the secondary winding. The preferred values for nominal system voltages are given in Table 3 and Table 4.
Note on C32: Select the winding configuration for the transformer secondary winding. Standard connection arrangements for particular types of transformers are in IEEE Std C57.12.70.
Note on C33: Specify the basic lightning impulse insulation level (BIL). BIL is dependent on the degree of exposure of the transformer and characteristics of the overvoltage protection system. Refer to Table 3 and Table 4 for guidance.
Note on C34: Select the transformer neutral grounding arrangement for the transformer secondary winding. Select "not applicable" for a delta winding configuration.
Note on C35: Specify the nominal voltage rating in kV for the additional secondary winding for three-winding transformer applications. This is not applicable for standard two-winding transformers.
Note on C36: Select the winding configuration for the additional secondary winding for three-winding transformer applications. This is not applicable for standard two-winding transformers. Default value : none
Note on C37: Specify the basic lightning impulse insulation level (BIL) for the additional secondary winding for three-winding transformer applications. This is not applicable for standard two-winding transformers.
Note on C38: Select the transformer neutral grounding arrangement for the additional secondary winding for three-winding transformer applications. This is not applicable for standard two-winding transformers. Select "not applicable" for a delta winding configuration. Default value : not applicable
Note on C39: Specify the nominal voltage rating in kV for the tertiary winding for large (Class II) transformer applications. This is not applicable for standard two-winding transformers.
Note on C40: Select the winding configuration for the tertiary winding for large (Class II) transformer applications. This is not applicable for standard two-winding transformers. Default value : not applicable
Note on C41: Specify the basic lightning impulse insulation level (BIL) for the tertiary winding for large (Class II) transformer applications. This is not applicable for standard two-winding transformers.
Note on C42: Select the nominal operating frequency. If "other"' is selected, specify in the "Additional notes" column. Default value : 60
Note on C43: Select whether the transformer impedance will be determined by the manufacturer or a specific value of impedance is required. If "other" is selected, specify the required transformer impedance in the "Additional notes" column. Default value : manufacturer's standard
Note on C44: Select whether the audible level is determined by the manufacturer or a specific maximum permissible audible sound level is required. If "other" is selected, specify the maximum sound level as measured per NEMA TR1 in the "Additional notes" column. Default value : manufacturer's standard
Note on C45: Specify the available fault current (symmetrical) of the system at the point of connection for the primary of the transformer. This value is normally available from the purchaser's power system study.
Note on C46: Specify the X/R ratio (system reactance / system resistance) of the system at the point of connection for the primary of the transformer. This value is normally available from the purchaser's power system.
Note on C47: Select whether the transformer will be supplying large non-linear loads. If "yes" is selected, specify additional details for the number, size and type of non-linear loads or advise % THD anticipated in the "Additional notes" column. Default value : no
Note on C48: Select the type of service for this transformer. If "other" is selected, specify additional details for the specific type of service in the "Additional notes" column. Default value : step-down
Note on C49: Select the type of unusual service conditions for this transformer. If "other" is selected, specify additional details for the specific type of unusual service in the "Additional notes" column. Default value : none
Note on C50: Select whether a grounding resistor is to be provided and installed on the transformer skid. If "yes" is selected, specify the NGR rating, withstand time and any particular installation requirements in the "Additional notes" column. Default value : no
Note on C51: Select the auxiliary power feeder voltage supplied to the transformer for fans, space heaters, controls and accessories. If "other" is selected, specify additional details including the voltage and number of phases in the "Additional notes" column. Default value : 120
Note on C52: Select the transformer neutral bushing grounding connection for solidly grounded systems. Default value : grounded to ground pad with removable strap
Note on C54: Select the type of insulating liquid for the transformer. Natural ester oil is used for low environmental impact and improved fire resistance. If is "other" is selected, specify the insulating liquid in the "Additional notes" column. Default value : mineral oil
Note on C55: Select the type of liquid insulation preservation system. The conservator-type transformer should only be used for very large transformer applications (above 30 MVA). Default value : sealed-tank
Note on C56: Select the radiator type for the transformer application. The tube-type radiator is preferred for offshore and marine applications due to corrosion concerns. If is "other" is selected, specify the unique radiator type in the "Additional notes" column. Default value : manufacturer's standard
Note on C57: Select the material for the transformer radiator fabrication. If stainless steel is selected, specify the grade of stainless steel in the "Additional notes" column. Default value : manufacturer's standard
Note on C58: Select whether the transformer radiators are required to be removable. This is normally preferred for offshore and marine applications due to corrosion concerns and when replacement during expected lifetime is anticipated. Default value : no
Note on C59: Select whether provisions for future fans (forced-cooling) is required. This is an option for the ONAN transformer cooling class only. Default value : no
Note on C60: Select whether a cooling fan monitoring system for forced-cooling applications is required. Default value : no
Note on C62: Select "other" if the operating company or the site has a technically approved manufacturer at that location. If "other" is selected, specify the on-load tap changer (OLTC) manufacturer in the "Additional notes" column. Default value : manufacturer's standard
Note on C63: Select the tap changer type for the transformer. The de-energized tap changer (DETC) installed on the primary side is typically used for most transformer applications. The on-load tap changer (OLTC) is only available for power transformers. Default value : DETC
Note on C64: Select the transformer winding for the tap changer location. The de-energized tap changer (DETC) is typically installed on the primary winding and the on-load tap changer (OLTC) is normally installed on the secondary winding. Default value : primary winding
Note on C65: Select the operator location for the de-energized tap changer (DETC). This selection is not applicable for the on-load tap changer (OLTC) option. If "other" is selected, specify the operator location in the "Additional notes" column. Default value : manufacturer's standard
Note on C66: Select the tap changer switching type for the transformer on-load tap changer (OLTC). The vacuum type is typically used in most applications. If "other" is selected, specify the type in the "Additional notes" column. Default value : vacuum
Note on C67: Select whether a remote control panel for the on-load tap changer (OLTC) is required for this transformer application. The remote control panel is normally installed in a separate control room. Default value : no
Note on C68: Select the communications interface for the on-load tap changer (OLTC) to the remote control panel or facility control system. Default value : digital communication
Note on C69: Select whether the OLTC will be used in parallel operation. If "yes" is selected, specify the control philosophy (i.e., master/follower, circulating current, power factor, circulating reactive current, negative reactance) in the "Additional notes" column. Default value : no
Note on C70: Select whether space heaters are required in the local control cabinet for the OLTC. Space heaters are typically installed in the transformer OLTC local control cabinet where moisture and condensation are problematic for the installation location. Default value : not required
Note on C72: Select the primary bushing location. The "cover" option is used for overhead line applications. The "side" option is used for cable or bus duct feeder applications.
Note on C73: Select the primary bushing location. The "cover" option is used for overhead line applications. The "side" option is used for cable or bus duct feeder applications.
Note on C74: Select the neutral bushing location. The "cover" option is normally used for overhead line applications. The "side" options are normally required for cable or bus duct type feeder applications.
Note on C75: Specify the basic lightning impulse insulation level (BIL) for the primary bushing. The minimum BIL level for the bushing is no less than the winding BIL level. In certain applications, a higher BIL level may be preferred.
Note on C76: Specify the basic lightning impulse insulation level (BIL) for the secondary bushing. The minimum BIL level for the bushing is no less than the winding BIL level. In certain applications, a higher BIL level may be preferred.
Note on C77: Specify the basic lightning impulse insulation level (BIL) for the neutral bushing. The minimum BIL level for the bushing is no less than the winding BIL level. In certain applications, a higher BIL level may be preferred.
Note on C78: Select the cover (exposed) bushing creepage distance as a function of anticipated environmental contamination. Refer to IEEE Std C57.19.01-2017, Table 1 for additional guidance. Default value : manufacturer's standard
Note on C79: Select the type of accuracy class for the primary current transformers (CT). For multi-ratio CT applications, specify the desired ratios in the "Additional notes" column. The accuracy class specifics and ratio should be shown on the one-line drawings. Default value : not applicable
Note on C80: Select the type of accuracy class for the secondary current transformers (CT). For multi-ratio CT applications, specify the desired ratios in the "Additional notes" column. The accuracy class specifics and ratio should be shown on the one-line drawing. Default value : not applicable
Note on C81: Select the type of accuracy class for the neutral current transformers (CT). For multi-ratio CT applications, specify the desired ratios in the "Additional notes" column. The accuracy class specifics and ratio should be shown on the one-line drawings. Default value : not applicable
Note on C82: Select the arrester class for the transformer primary. Substation class arresters are typically provided for cover (exposed) bushings and intermediate class arresters are more applicable for ATCs. Default value : not applicable
Note on C83: Select the arrester class for the transformer secondary. Substation class arresters are typically provided for cover (exposed) bushings and intermediate class arresters are more applicable for ATCs. Default value : not applicable
Note on C85: Select the ATC type. If ATC has been selected for both the primary and secondary, the ATC type will apply to both. Full height ATCs provide mechanical protection for incoming cables. If "other" is selected, specify dimensions in "Additional notes".
Note on C86: Select the enclosure rating for the transformer ATC(s). NEMA 4 with 316L stainless steel material is typical for offshore, marine and corrosive environment applications. Default value : NEMA 3R
Note on C87: Select the material for the ATC enclosure. 316L stainless steel can be used for extreme climate and corrosive environment conditions. Default value : manufacturer's standard
Note on C88: Select the type of main cover for the ATC(s). A hinged door is more practical for maintenance and repair activities when multiple devices are installed within the ATC(s). Default value : bolted
Note on C89: Select the location for primary cable entry into the transformer ATC(s). The entry of cables into the top of the ATC is generally not recommended due to water ingress associated with the deterioration of sealing materials used for cable glands. Default value : bottom
Note on C90: Select the location for secondary cable entry into the transformer ATC(s). The entry of cables into the top of the ATC is generally not recommended due to water ingress associated with the deterioration of sealing materials used for cable glands. Default value : bottom
Note on C91: Select whether space heaters are required in the ATC(s). Space heaters are typically installed in transformer ATCs where moisture and condensation are problematic for the installation location. Default value : not required
Note on C92: Select whether a space heater thermostat is required to control the space heaters in the ATCs. A space heater thermostat is typically used to control the space heaters to prevent excessive heating inside the ATC during periods of high ambient temperature. Default value : not required
Note on C93: Select whether an ammeter for the ATC space heater circuit is required. A space heater circuit ammeter is typically installed in the transformer control cabinet to provide a positive indication that the space heaters are functioning. Default value : not required
Note on C95: Select the primary power connection type. This will determine the conductor termination arrangement on each of the primary bushings.
Note on C96: Select the secondary power connection type. This will determine the conductor termination arrangement on each of the secondary bushings. For three-winding transformers, the additional secondary winding is typically the same.
Note on C97: Select the neutral power connection type. This will determine the conductor termination arrangement on the neutral bushing. Default value : none
Note on C98: Specify the power conductor size for the transformer primary. Select the appropriate unit designation (i.e., AWG, kcmil, in., mm) in the "UOM" (units) column.
Note on C99: Specify the power conductor size for the transformer secondary. Select the appropriate unit designation (i.e., AWG, kcmil, in., mm) in the "UOM" (units) column. For three-winding transformers, the additional secondary winding is typically the same.
Note on C100: Specify the power conductor size for the transformer neutral. Select the appropriate unit designation (i.e., AWG, kcmil, in., mm) in the "UOM" (units) column.
Note on C101: Select the material for the primary power connection. This will determine the need for any dissimilar metal interfaces for the conductor termination to the primary bushings.
Note on C102: Select the material for the secondary power connection. This will determine the need for any dissimilar metal interfaces for the conductor termination to the secondary bushings.
Note on C103: Select the material for the neutral power connection. This will determine the need for any dissimilar metal interfaces for the conductor termination to the neutral bushing.
Note on C104: Specify the number of power conductors for the transformer primary. If "other" is selected, specify the number of phase conductors in the "Additional notes" column.
Note on C105: Specify the number of power conductors for the transformer secondary. If "other" is selected, specify the number of phase conductors in the "Additional notes" column. For three-winding transformers, the additional secondary winding is typically the same.
Note on C106: Specify the number of power conductors for the transformer neutral. If "other" is selected, specify the number of neutral conductors in the "Additional notes" column.
Note on C107: Specify the ground conductor size for the transformer. Specify the appropriate unit designation (i.e., AWG, kcmil) in the "UOM" (units) column.
Note on C108: Specify the number of ground conductors for the transformer. If "other" is selected, specify the number of ground conductors in the "Additional notes" column.
Note on C110: Select whether a sudden pressure relay (SPR) is required. The SPR is normally provided with a seal-in relay for detection of sudden rise in gas pressure. This is used to quickly de-energize the transformer to minimize damage from internal short circuits. Default value : not required
Note on C111: Select whether a winding temperature indicator is required. This accessory is standard for power transformers. It provides a hottest-spot temperature measurement for the transformer windings and can be used for alarms and cooling fan control.
Note on C112: Select whether a continuous temperature monitoring system for the transformer insulating liquid is required. Continuous measurement of the top oil temperature is an important factor in maximizing the service life. Default value : not required
Note on C113: Select whether a continuous temperature monitoring system for the transformer windings is required. If "required" is selected, specify the type of continuous temperature monitoring system in the "Additional notes" column. Default value : not required
Note on C114: Select whether a continuous cable termination thermal monitoring system for the transformer power connections is required. Continuous measurement of power connection temperatures can detect hot spots from loose connections resulting in possible failure. Default value : not required
Note on C115: Select whether a continuous dissolved gas-in-oil analysis (DGA) monitoring system for the transformer insulating liquid is required. If "required" is selected, specify the selected gases from IEEE Std C57.143-2012 Table 4 in the "Additional notes" column. Default value : not required
Note on C116: Select whether a moisture in oil monitoring system for the insulating liquid is required. Excessive moisture affects dielectric integrity of liquid/paper insulation system and can lead to partial discharges, dielectric breakdown and reduced life. Default value : not required
Note on C117: Select whether a continuous partial discharge monitoring system is required. If "required" is selected, specify the transformer components to be monitored in the "Additional notes" column (e.g., windings, bushings, high-voltage terminations). Default value : not required
Note on C118: Select whether a conservator membrane monitoring system is required. A failed membrane can block the outlet from the conservator to the main tank, creating a vacuum that can occur resulting in the formation of gas bubbles in the insulating liquid. Default value : not required
Note on C119: Select whether thermal scanning inspection windows are required in the ATC(s). The manufacturer recommends the locations in order to provide adequate viewing for the transformer power connections. Default value : not required
Note on C120: Select whether individual software packages for configuration, diagnostics, monitoring and CBM data analytics are required. Provide specific requirements in the "Additional notes" column. This includes non-standard interface cables. Default value : not required
Note on C121: Select the communication media. Depending on the selection, additional information regarding the physical layer may be required. If "multiple" or "other" is selected, specify in the "Additional notes" column and in the project drawings.
Note on C122: Select the communication protocol. Depending on the selection, additional information regarding the physical layer may be required. If "multiple" or "other" is selected, specify in the "Additional notes" column and in the project drawings.
Note on C123: Select whether a pressure-relief directional shroud and piping is required for onshore application. If "required" is selected, specify details of the shroud and piping in the "Additional notes" column. Default value : not required
Note on C124: Select whether space heaters are required in control cabinets and/or throats. If "required" is selected, specify the space heater locations in the "Additional notes" column. Default value : not required
Note on C126: Select whether the transformer is to be subjected to the audible sound level design test in subclause 8.2.5. Default value : not required
Note on C127: Select whether the transformer is to be subjected to the temperature rise design test in IEEE Std C57.12.90. If the temperature rise testing conditions are different than those of the design test, specify each parameter in the "Additional notes" column. Default value : not required
Note on C128: Select whether the lightning impulse design test described in Table 5 and IEEE Std C57.12.90 is required. This is a routine test for distribution transformers and power transformers rated 15 MVA and above with a primary voltage rating 69 kV and above. Default value : not required
Note on C129: Select whether the transformer is to be subjected to the switching impulse design test in IEEE Std C57.12.90. This test is routine for all transformers with a primary voltage rating of 345 kV and above and is not recommended for distribution transformers. Default value : not required
Note on C130: Select whether the transformer is to be subjected to the no-load losses at 110% of rated voltage test in IEEE Std C57.12.90. Default value : not required
Note on C131: Select whether the transformer is to be subjected to the partial discharge design test in IEEE Std C57.12.90. This test is normally conducted on all high-voltage components. This provides baseline information if partial discharge monitoring is selected. Default value : not required
Note on C132: Select whether the transformer is to be subjected to the frequency response analysis (FRA) test in IEEE Std C57.12.90. This test provides baseline information to assist with detecting coil mechanical movement due to shipping or electrical fault events. Default value : not required
Note on C133: Select whether the transformer is to be subjected to the short-circuit capability test in IEEE Std C57.12.90. Distribution type transformers will have a design (type) test report available. Power type transformers normally use the calculation method. Default value : not required
Note on C134: Select whether the transformer is to be subjected to the dissolved gas-in-oil analysis test before the start of all tests and after the completion of all tests in IEEE Std C57.12.00. This is a routine test for large (Class II) power transformers. Default value : required
Note on C136: Select the transformer preservation requirement. Manufacturer's standard packaging is appropriate for domestic shipping (not offshore) and short-term outdoor storage. If "special" is selected, specify in the "Additional notes" column or "Supplement"' tab. Default value : manufacturer's standard
Note on C137: Select whether a shipping impact recorder is required to be installed on the transformer for shipment. For transformers rated 10 MVA and above, impact recorders are included in guidance and shipping preparations defined in IEEE Std C57.150. Default value : not required
Note on C138: Select whether desiccant bags are required to be installed for shipping. Default value : required
Note on C139: Select whether the installation of car seals is required on every valve and oil drain on the transformer tank for shipping. Default value : not required

## PDS Distribution
Row | IOGP S-754D (1.0) Procurement Data Sheet for Distribution Transformers (IEEE) | [6 empty] | Issue
2 | Ref. clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Equipment identification
4 | 5.12.2 | Tag number : | input data |  | input data
5 | 5.12.2 | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Site conditions
9 | 4.1.2.1, 4.3.1, 4.4.1, 5.10, 6.11.5 | Maximum ambient air temperature : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50 | 55 | other
10 | 4.1.2.2, 4.3.1, 4.4.1 | Minimum ambient air temperature : | -20 | °C | -20 | °C |  |  |  |  | select | -20 | -30 | -40 | other
11 | 4.1.2.1, 4.3.1, 4.4.1, 5.10 | Ambient 24-hour average temperature : | 30 | °C | 30 | °C |  |  |  |  | select | 30 | 40 | 45 | 50 | other
12 | 4.3.1, 4.3.2, 4.4.1, 5.10, 5.12.2.5, Table 1 | Altitude of installation : | ≤ 1000 | m | ≤ 1000 | m |  |  |  |  | select | ≤ 1000 | other
13 | 4.3.3, 5.13.1 | Seismic design : | not required |  | not required | [5 empty] | select | required | not required
14 | 4.3.3, 5.13.1, 5.13.5 | Seismic site location : | input data |  | input data
15 | 4.3.3, 5.13.1 | Seismic certificate : | not required |  | not required | [5 empty] | select | required | not required
16 | 4.3.3, 4.3.5, 5.12.2.6, 6.2.3.6, 6.11.7 | Area classification : | unclassified |  | unclassified | [5 empty] | select | unclassified | classified
17 | 4.1.7, 4.4.1, 5.10 | Installation environment : | outdoor |  | outdoor | [5 empty] | select | indoor | outdoor
18 | 4.3.3, 4.3.4, 4.4.1, 5.13.4, 5.13.5, 6.6.6.2, 6.16.6, 6.17.1, 6.17.2 | Application/operating environment : | select |  | select | [5 empty] | select | onshore | offshore - fixed | offshore - floating | marine - ship | other
19 | 4.3.3, 4.4.1, 5.13.5, 6.17.1 | Unusual environments : | none |  | none | [5 empty] | select | none | corrosive gases | fumes / vapor / steam / salt air | excessive harmonics | hot and humid climates | abnormal vibration/shock/tilting | other or multiple
20 | 4.1.9 | Paint color : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | ANSI 61 grey | other
21 | 5.13.2, 5.13.4, 9.3 | Certification : | not required |  | not required | [5 empty] | select | not required | NRTL | USCG/ABS | other
22 | 5.13.3 | Compliance with Canadian standards : | not applicable |  | not applicable | [5 empty] | select | not applicable | CAN/CSA C2.1:06 | CAN/CSA C88 | CAN/CSA C227.4
23 |  | Ratings and system parameters
24 | 5.10, 5.4.2, 9.3, Table 2 | kVA rating : | input data | kVA | input data | kVA
25 | 5.1, 5.10 | Cooling class : | ONAN |  | ONAN | [5 empty] | select | ONAN | ONAN/ONAF | ONAN/ONAF1/ONAF2 | KNAN | KNAF | other
26 | 6.9, 7.4 | Winding material : | select |  | select | [5 empty] | select | copper | aluminum
27 | 5.1 | Primary winding voltage : | input data | kV | input data | kV
28 | 5.6, 5.10 | Primary winding configuration : | select |  | select | [5 empty] | select | delta | wye
29 | 5.10, 5.10.2.1 | Primary winding BIL : | input data | kV | input data | kV
30 | 5.10.3.2, 5.10.3.4, 6.8 | Primary neutral grounding : | select |  | select | [5 empty] | select | not applicable | solidly grounded | resistance grounded | ungrounded | other
31 | 5.10, Table 3, Table 4 | Secondary 1 winding voltage : | input data | kV | input data | kV
32 | 5.6, 5.10 | Secondary 1 winding configuration : | select |  | select | [5 empty] | select | delta | wye
33 | 5.10, Table 3, Table 4 | Secondary 1 winding BIL : | input data | kV | input data | kV
34 | 5.10.3.2, 5.10.3.4, 6.8 | Secondary 1 neutral grounding : | select |  | select | [5 empty] | select | not applicable | solidly grounded | low resistance grounded | high resistance grounded | ungrounded | other
35 | 5.2, 5.10 | Frequency : | 60 | Hz | 60 | Hz |  |  |  |  | select | 50 | 60 | other
36 | 5.8, 9.2, 12.1.4 | Impedance : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
37 | 8.2.5, Table C.1, Table C.2 | Audible sound level : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
38 | 7.1.5.5, 12.1.4 | Available fault current (symmetrical) : | input data | kA | input data | kA
39 | 7.1.5.2, 12.1.4 | System X/R ratio : | input data |  | input data
40 | 4.1.5 | Supply non-linear loads : | no |  | no | [5 empty] | select | no | yes
41 | 4.1.8 | Load application : | step-down |  | step-down | [5 empty] | select | step-down | step-up | generator step-up | system tie | other
42 | 4.3.3, 9.2 | Unusual service conditions : | none |  | none | [5 empty] | select | none | parallel operation | over 110% rated voltage | over 110% volts/hertz | other
43 | 6.2.5 | Grounding resistor provided/installed : | no |  | no | [5 empty] | select | no | yes
44 | 6.2.3, 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Auxiliary power : | 120 | V ac | 120 | V ac |  |  |  |  | select | 120 | 208 | 240 | other
45 | 5.10.3.2 | Neutral bushing grounding connection for solidly grounded systems : | grounded to ground pad with removable strap |  | grounded to ground pad with removable strap | [5 empty] | select | grounded to ground pad with removable strap | none
46 |  | Cooling system
47 | 6.6.1, 6.6.4, 6.15.1.10, 8.2.1, 8.2.1.1, 8.2.1.2 | Insulating liquid : | mineral oil |  | mineral oil | [5 empty] | select | mineral oil | natural ester | synthetic ester | silicone fluid | other
48 | 4.3.3 | Radiator material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | galvanized steel | stainless steel
49 | 6.14.1.2 - 6.14.1.5 | Removable radiators : | no |  | no | [5 empty] | select | yes | no
50 | 6.14.2, 6.14.3 | Provision for fans : | no |  | no | [5 empty] | select | yes | no
51 | 6.2.3.8 | Fan monitoring system : | no |  | no | [5 empty] | select | yes | no
52 |  | Bushings
53 | 6.1, 6.10.1.3, 6.10.2.1, 6.10.2.2, 6.10.2.4 - 6.10.2.6, 12.1.5 | Primary bushing location : | select |  | select | [5 empty] | select | cover (exposed) | side (ATC) | side (throat) | side (iso phase)
54 | 6.1, 6.10.1.3, 6.10.2.1, 6.10.2.2, 6.10.2.4 - 6.10.2.6, 12.1.5 | Secondary bushing location : | select |  | select | [5 empty] | select | cover (exposed) | side (ATC) | side (throat) | side (iso phase)
55 | 5.10.3.5, 6.1, 6.10.1.3, 6.10.2.1, 6.10.2.2, 6.10.2.4 - 6.10.2.6 | Neutral bushing location : | select |  | select | [5 empty] | select | cover (exposed) | side (ATC) | side (throat) | inside tank
56 | 5.10.3.4 | Primary bushing BIL : | input data | kV | input data | kV
57 | 5.10.3.4 | Secondary bushing BIL : | input data | kV | input data | kV
58 | 5.10.3.4 | Neutral bushing BIL : | input data | kV | input data | kV
59 | 6.12, 12.1.11 | Primary arrester class : | not applicable |  | not applicable | [5 empty] | select | substation | intermediate | distribution | not applicable
60 | 6.12, 12.1.11 | Secondary arrester class : | not applicable |  | not applicable | [5 empty] | select | substation | intermediate | distribution | not applicable
61 |  | Air terminal chamber (ATC)
62 | 6.10.1.20 | ATC type : | select |  | select | [5 empty] | select | manufacturer's standard | full height | other | not applicable
63 | 6.10.1.2, 6.10.1.7, 6.10.1.10, 6.10.1.11, 6.10.1.17 | Enclosure rating : | NEMA 3R |  | NEMA 3R | [5 empty] | select | NEMA 3R | NEMA 4 | NEMA 4X
64 | 6.10.1.4, 6.10.1.6, 6.10.1.9 | Enclosure material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | aluminum | 316L stainless steel
65 | 6.10.1.1, 6.10.1.2, 6.10.1.5, 6.10.1.6, 6.10.1.13, 6.10.1.15, 6.10.1.16 - 6.10.1.18 | Enclosure cover : | bolted |  | bolted | [5 empty] | select | bolted | hinged | bolted and hinged
66 | 6.10.1.4 - 6.10.1.8 | Primary cable entry : | bottom |  | bottom | [5 empty] | select | bottom | top | side
67 | 6.10.1.4 - 6.10.1.8 | Secondary cable entry : | bottom |  | bottom | [5 empty] | select | bottom | top | side
68 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heaters : | not required |  | not required | [5 empty] | select | not required | required
69 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heater thermostat : | not required |  | not required | [5 empty] | select | not required | required
70 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heater ammeter : | not required |  | not required | [5 empty] | select | not required | required
71 |  | Power connections
72 | 6.1.5, 6.10.2.3 | Primary connection : | select |  | select | [5 empty] | select | cable | cable bus (throat) | bus duct (throat) | iso phase duct
73 | 6.1.5, 6.10.2.3 | Secondary connection : | select |  | select | [5 empty] | select | cable | cable bus (throat) | bus duct (throat) | iso phase duct
74 | 6.1.5, 6.10.2.3 | Neutral connection : | none |  | none | [5 empty] | select | cable | cable bus (throat) | bus duct (throat) | iso phase duct
75 | 6.1.5 | Primary conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil | in. | mm
76 | 6.1.5 | Secondary conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil | in. | mm
77 | 6.1.5 | Neutral conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil | in. | mm
78 | 6.9 | Primary conductor material : | select |  | select | [5 empty] | select | copper | aluminum
79 | 6.9 | Secondary conductor material : | select |  | select | [5 empty] | select | copper | aluminum
80 | 6.9 | Neutral conductor material : | select |  | select | [5 empty] | select | copper | aluminum
81 | 6.1.5 | Number of primary conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
82 | 6.1.5 | Number of secondary conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
83 | 6.1.5 | Number of neutral conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
84 | 6.1.5 | Ground conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil
85 | 6.1.5 | Number of ground conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
86 |  | Accessories
87 | 6.2.4 | Sudden pressure relay (SPR) : | not required |  | not required | [5 empty] | select | not required | required
88 | 6.2 | Winding temperature indicator : | select |  | select | [5 empty] | select | not required | required
89 | 6.2.6.1, 6.2.6.8 | Insulating liquid temperature monitoring : | not required |  | not required | [5 empty] | select | not required | required
90 | 6.2.6.2, 6.2.6.8 | Winding temperature monitoring : | not required |  | not required | [5 empty] | select | not required | required
91 | 6.2.6.3, 6.2.6.8 | Cable termination thermal monitoring : | not required |  | not required | [5 empty] | select | not required | required
92 | 6.2.6.4, 6.2.6.8 | Dissolved gas monitoring : | not required |  | not required | [5 empty] | select | not required | required
93 | 6.2.6.5, 6.2.6.8 | Moisture in oil monitoring : | not required |  | not required | [5 empty] | select | not required | required
94 | 6.2.6.6, 6.2.6.8 | Partial discharge monitoring : | not required |  | not required | [5 empty] | select | not required | required
95 | 6.10.1.21, 6.10.1.22 | Thermal scanning inspection windows : | not required |  | not required | [5 empty] | select | not required | required
96 |  | Application software : | not required |  | not required | [5 empty] | select | not required | required
97 | 6.2.6.1.2, 6.2.6.4.4, 6.2.6.5.3, 6.2.6.6, 6.2.6.8 | Communication media : | select |  | select | [5 empty] | select | Ethernet copper | Ethernet fiber | serial | multiple | other
98 | 6.2.6.1.2, 6.2.6.4.4, 6.2.6.5.3, 6.2.6.6, 6.2.6.8 | Communication protocol : | select |  | select | [5 empty] | select | PROFIBUS | PROFINET | Modbus TCP/IP | IEC 61850 | multiple | other
99 | 6.2.1.8 | Onshore pressure-relief directional shroud and piping : | not required |  | not required | [5 empty] | select | not required | required
100 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heaters for control cabinets and throats : | not required |  | not required | [5 empty] | select | not required | required
101 |  | Supplemental testing
102 | 8.2.1.4, 8.2.2, 8.2.3, 8.2.5, Table 17 | Audible sound level : | not required |  | not required | [5 empty] | select | not required | required
103 | 8.2.1.4, 8.2.2, 8.2.3, 8.5, Table 17 | Temperature rise : | not required |  | not required | [5 empty] | select | not required | required
104 | 5.10.7.1, 8.2.1.4, 8.2.2, 8.2.3, Table 17 | Lightning impulse : | not required |  | not required | [5 empty] | select | not required | required
105 | 8.2.1.4, 8.2.2, 8.2.3, Table 17 | Core insulation resistance : | not required |  | not required | [5 empty] | select | not required | required
106 | 8.2.1.4, 8.2.2, 8.2.3, Table 17 | Partial discharge : | not required |  | not required | [5 empty] | select | not required | required
107 | 8.2.1.4, 8.2.3, Table 17 | Short-circuit capability : | not required |  | not required | [5 empty] | select | not required | required | third-party
108 | 6.2.6.5.1, 8.2.1, 8.2.1.1, 8.2.1.2, 8.2.1.4, 8.2.3, Table 17 | Dissolved gas-in-oil analysis (DGA) : | required |  | required | [5 empty] | select | not required | required
109 | 8.2.1.5, Table 17 | Winding insulation resistance : | required |  | required | [5 empty] | select | not required | required
110 |  | Shipping and preservation
111 | 10.1.1 - 10.1.10, 10.2.1 | Equipment preservation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | long term outdoor storage | special
112 | 10.1.10 | Desiccant bags installed : | required |  | required | [5 empty] | select | not required | required
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the tag.
Note on C7: Select CAS level to be applied in IOGP S-754Q, Annex A. Default value : D
Note on C9: Select the maximum ambient air temperature of the air that is cooling the radiators. The default value as per IEEE Std C57.12.00 is 40 °C. If "other" is selected, specify the maximum limit in the "Additional notes" column. Default value : 40
Note on C10: Select the minimum ambient air temperature. Ambient temperatures below -20 °C are considered unusual service conditions. If "other" is selected, specify the minimum limit ( i.e., below -20 °C) in the "Additional notes" column. Default value : -20
Note on C11: Select the average 24-hour ambient air temperature of the air that is cooling the radiators. The default value as per IEEE Std C57.12.00 is 30 °C. If "other" is selected, specify the average ambient in the "Additional notes" column. Default value : 30
Note on C12: Select the transformer installation altitude. IEEE Std C57.12.00 is based on the maximum altitude of 1000 m (3300 ft). Derating information is provided in Table 1. If "other" is selected, specify the altitude in the "Additional notes" column. Default value : ≤ 1000
Note on C13: Select whether the seismic design is required. Additional information as per IEEE Std 693, such as seismic qualification level or the seismic exposure map information, should be provided in the "Additional notes" column. Default value : not required
Note on C14: Specify the site physical address or latitude and longitude to determine the seismic qualification level and additional parameters.
Note on C15: Select whether a third-party seismic certificate is required. Default value : not required
Note on C16: Select whether the transformer is installed in a hazardous (classified) area. If "classified", specify the Division/Zone, Group and AIT for the installation location in the "Additional notes" column. Default value : unclassified
Note on C17: Select whether the transformer is installed indoor or outdoor. Default value : outdoor
Note on C18: Select the operating environment for the transformer. If "other" is selected, specify the operating environment in the "Additional notes" column.
Note on C19: Select the unusual environments or contaminant to which the transformer will be exposed. If "other or multiple" is selected, specify in the "Additional notes" column. Default value : none
Note on C20: Select the paint color for the transformer. ANSI 61 grey refers to the paint color specified in ASTM D1535 (Munsell Notation 8.3G 6.10/0.54). If "other" is selected, specify the paint color using the ANSI designation in the "Additional notes" column. Default value : manufacturer's standard
Note on C21: Select the certification requirements for the transformer. If "other" is selected, specify in the "Additional notes" column. NRTL certification in accordance with UL guideline XPLH applies only to distribution transformers rated 69 kV or below. Default value : not required
Note on C22: Select the Canadian standard to which the transformer will be built. Default value : not applicable
Note on C24: Select the base kVA rating for the transformer. The preferred continuous base kVA ratings are listed in Table 2.
Note on C25: Select the transformer cooling class. If "other" is selected, specify the method of cooling in the "Additional notes" column. Default value : ONAN
Note on C26: Select the base material for the transformer windings. Copper is normally used for power transformer windings and aluminum is used for distribution and pad-mounted transformers.
Note on C27: Specify the value of the voltage in kV for the primary winding. The preferred values for nominal system voltages are given in Table 3 and Table 4.
Note on C28: Select the winding configuration for the transformer primary windings. Standard connection arrangements for particular types of transformers are in IEEE Std C57.12.70.
Note on C29: Specify the basic lightning impulse insulation level (BIL). BIL is dependent on the degree of exposure of the transformer and characteristics of the overvoltage protection system. Refer to Table 3 and Table 4 for guidance.
Note on C30: Select the transformer neutral grounding arrangement for the transformer primary winding. Select "not applicable" for a delta winding configuration. If "other" is selected, indicate the grounding type in the "Additional notes" column.
Note on C31: Specify the value of the voltage in kV for the secondary winding. The preferred values for nominal system voltages are given in Table 3 and Table 4.
Note on C32: Select the winding configuration for the transformer secondary winding. Standard connection arrangements for particular types of transformers are in IEEE Std C57.12.70.
Note on C33: Specify the basic lightning impulse insulation level (BIL). BIL is dependent on the degree of exposure of the transformer and characteristics of the overvoltage protection system. Refer to Table 3 and Table 4 for guidance.
Note on C34: Select the transformer neutral grounding arrangement for the transformer secondary winding. Select "not applicable" for a delta winding configuration.
Note on C35: Select the nominal operating frequency. If "other"' is selected, specify in the "Additional notes" column. Default value : 60
Note on C36: Select whether the transformer impedance will be determined by the manufacturer or a specific value of impedance is required. If "other" is selected, specify the required transformer impedance in the "Additional notes" column. Default value : manufacturer's standard
Note on C37: Select whether the audible level is determined by the manufacturer or a specific maximum permissible audible sound level is required. If "other" is selected, specify the maximum sound level as measured per NEMA TR1 in the "Additional notes" column. Default value : manufacturer's standard
Note on C38: Specify the available fault current (symmetrical) of the system at the point of connection for the primary of the transformer. This value is normally available from the purchaser's power system study.
Note on C39: Specify the X/R ratio (system reactance / system resistance) of the system at the point of connection for the primary of the transformer. This value is normally available from the purchaser's power system.
Note on C40: Select whether the transformer will be supplying large non-linear loads. If "yes" is selected, specify additional details for the number, size and type of non-linear loads or advise % THD anticipated in the "Additional notes" column. Default value : no
Note on C41: Select the type of service for this transformer. If "other" is selected, specify additional details for the specific type of service in the "Additional notes" column. Default value : step-down
Note on C42: Select the type of unusual service conditions for this transformer. If "other" is selected, specify additional details for the specific type of unusual service in the "Additional notes" column. Default value : none
Note on C43: Select whether a grounding resistor is to be provided and installed on the transformer skid. If "yes" is selected, specify the NGR rating, withstand time and any particular installation requirements in the "Additional notes" column. Default value : no
Note on C44: Select the auxiliary power feeder voltage supplied to the transformer for fans, space heaters, controls and accessories. If "other" is selected, specify additional details including the voltage and number of phases in the "Additional notes" column. Default value : 120
Note on C45: Select the transformer neutral bushing grounding connection for solidly grounded systems. Default value : grounded to ground pad with removable strap
Note on C47: Select the type of insulating liquid for the transformer. Natural ester oil is used for low environmental impact and improved fire resistance. If is "other" is selected, specify the insulating liquid in the "Additional notes" column. Default value : mineral oil
Note on C48: Select the material for the transformer radiator fabrication. If stainless steel is selected, specify the grade of stainless steel in the "Additional notes" column. Default value : manufacturer's standard
Note on C49: Select whether the transformer radiators are required to be removable. This is normally preferred for offshore and marine applications due to corrosion concerns and when replacement during expected lifetime is anticipated. Default value : no
Note on C50: Select whether provisions for future fans (forced-cooling) is required. This is an option for the ONAN transformer cooling class only. Default value : no
Note on C51: Select whether a cooling fan monitoring system for forced-cooling applications is required. Default value : no
Note on C53: Select the primary bushing location. The "cover" option is used for overhead line applications. The "side" option is used for cable or bus duct feeder applications.
Note on C54: Select the primary bushing location. The "cover" option is used for overhead line applications. The "side" option is used for cable or bus duct feeder applications.
Note on C55: Select the neutral bushing location. The "cover" option is normally used for overhead line applications. The "side" options are normally required for cable or bus duct type feeder applications.
Note on C56: Specify the basic lightning impulse insulation level (BIL) for the primary bushing. The minimum BIL level for the bushing is no less than the winding BIL level. In certain applications, a higher BIL level may be preferred.
Note on C57: Specify the basic lightning impulse insulation level (BIL) for the secondary bushing. The minimum BIL level for the bushing is no less than the winding BIL level. In certain applications, a higher BIL level may be preferred.
Note on C58: Specify the basic lightning impulse insulation level (BIL) for the neutral bushing. The minimum BIL level for the bushing is no less than the winding BIL level. In certain applications, a higher BIL level may be preferred.
Note on C59: Select the arrester class for the transformer primary. Substation class arresters are typically provided for cover (exposed) bushings and intermediate class arresters are more applicable for ATCs. Default value : not applicable
Note on C60: Select the arrester class for the transformer secondary. Substation class arresters are typically provided for cover (exposed) bushings and intermediate class arresters are more applicable for ATCs. Default value : not applicable
Note on C62: Select the ATC type. If ATC has been selected for both the primary and secondary, the ATC type will apply to both. Full height ATCs provide mechanical protection for incoming cables. If "other" is selected, specify dimensions in "Additional notes".
Note on C63: Select the enclosure rating for the transformer ATC(s). NEMA 4 with 316L stainless steel material is typical for offshore, marine and corrosive environment applications. Default value : NEMA 3R
Note on C64: Select the material for the ATC enclosure. 316L stainless steel can be used for extreme climate and corrosive environment conditions. Default value : manufacturer's standard
Note on C65: Select the type of main cover for the ATC(s). A hinged door is more practical for maintenance and repair activities when multiple devices are installed within the ATC(s). Default value : bolted
Note on C66: Select the location for primary cable entry into the transformer ATC(s). The entry of cables into the top of the ATC is generally not recommended due to water ingress associated with the deterioration of sealing materials used for cable glands. Default value : bottom
Note on C67: Select the location for secondary cable entry into the transformer ATC(s). The entry of cables into the top of the ATC is generally not recommended due to water ingress associated with the deterioration of sealing materials used for cable glands. Default value : bottom
Note on C68: Select whether space heaters are required in the ATC(s). Space heaters are typically installed in transformer ATCs where moisture and condensation are problematic for the installation location. Default value : not required
Note on C69: Select whether a space heater thermostat is required to control the space heaters in the ATCs. A space heater thermostat is typically used to control the space heaters to prevent excessive heating inside the ATC during periods of high ambient temperature. Default value : not required
Note on C70: Select whether an ammeter for the ATC space heater circuit is required. A space heater circuit ammeter is typically installed in the transformer control cabinet to provide a positive indication that the space heaters are functioning. Default value : not required
Note on C72: Select the primary power connection type. This will determine the conductor termination arrangement on each of the primary bushings.
Note on C73: Select the secondary power connection type. This will determine the conductor termination arrangement on each of the secondary bushings. For three-winding transformers, the additional secondary winding is typically the same.
Note on C74: Select the neutral power connection type. This will determine the conductor termination arrangement on the neutral bushing. Default value : none
Note on C75: Specify the power conductor size for the transformer primary. Select the appropriate unit designation (i.e., AWG, kcmil, in., mm) in the "UOM" (units) column.
Note on C76: Specify the power conductor size for the transformer secondary. Select the appropriate unit designation (i.e., AWG, kcmil, in., mm) in the "UOM" (units) column. For three-winding transformers, the additional secondary winding is typically the same.
Note on C77: Specify the power conductor size for the transformer neutral. Select the appropriate unit designation (i.e., AWG, kcmil, in., mm) in the "UOM" (units) column.
Note on C78: Select the material for the primary power connection. This will determine the need for any dissimilar metal interfaces for the conductor termination to the primary bushings.
Note on C79: Select the material for the secondary power connection. This will determine the need for any dissimilar metal interfaces for the conductor termination to the secondary bushings.
Note on C80: Select the material for the neutral power connection. This will determine the need for any dissimilar metal interfaces for the conductor termination to the neutral bushing.
Note on C81: Specify the number of power conductors for the transformer primary. If "other" is selected, specify the number of phase conductors in the "Additional notes" column.
Note on C82: Specify the number of power conductors for the transformer secondary. If "other" is selected, specify the number of phase conductors in the "Additional notes" column. For three-winding transformers, the additional secondary winding is typically the same.
Note on C83: Specify the number of power conductors for the transformer neutral. If "other" is selected, specify the number of neutral conductors in the "Additional notes" column.
Note on C84: Specify the ground conductor size for the transformer. Specify the appropriate unit designation (i.e., AWG, kcmil) in the "UOM" (units) column.
Note on C85: Specify the number of ground conductors for the transformer. If "other" is selected, specify the number of ground conductors in the "Additional notes" column.
Note on C87: Select whether a sudden pressure relay (SPR) is required. The SPR is normally provided with a seal-in relay for detection of sudden rise in gas pressure. This is used to quickly de-energize the transformer to minimize damage from internal short circuits. Default value : not required
Note on C88: Select whether a winding temperature indicator is required. This accessory is standard for power transformers. It provides a hottest-spot temperature measurement for the transformer windings and can be used for alarms and cooling fan control.
Note on C89: Select whether a continuous temperature monitoring system for the transformer insulating liquid is required. Continuous measurement of the top oil temperature is an important factor in maximizing the service life. Default value : not required
Note on C90: Select whether a continuous temperature monitoring system for the transformer windings is required. If "required" is selected, specify the type of continuous temperature monitoring system in the "Additional notes" column. Default value : not required
Note on C91: Select whether a continuous cable termination thermal monitoring system for the transformer power connections is required. Continuous measurement of power connection temperatures can detect hot spots from loose connections resulting in possible failure. Default value : not required
Note on C92: Select whether a continuous dissolved gas-in-oil analysis (DGA) monitoring system for the transformer insulating liquid is required. If "required" is selected, specify the selected gases from IEEE Std C57.143-2012 Table 4 in the "Additional notes" column. Default value : not required
Note on C93: Select whether a moisture in oil monitoring system for the insulating liquid is required. Excessive moisture affects dielectric integrity of liquid/paper insulation system and can lead to partial discharges, dielectric breakdown and reduced life. Default value : not required
Note on C94: Select whether a continuous partial discharge monitoring system is required. If "required" is selected, specify the transformer components to be monitored in the "Additional notes" column (e.g., windings, bushings, high-voltage terminations). Default value : not required
Note on C95: Select whether thermal scanning inspection windows are required in the ATC(s). The manufacturer recommends the locations in order to provide adequate viewing for the transformer power connections. Default value : not required
Note on C96: Select whether individual software packages for configuration, diagnostics, monitoring and CBM data analytics are required. Provide specific requirements in the "Additional notes" column. This includes non-standard interface cables. Default value : not required
Note on C97: Select the communication media. Depending on the selection, additional information regarding the physical layer may be required. If "multiple" or "other" is selected, specify in the "Additional notes" column and in the project drawings.
Note on C98: Select the communication protocol. Depending on the selection, additional information regarding the physical layer may be required. If "multiple" or "other" is selected, specify in the "Additional notes" column and in the project drawings.
Note on C99: Select whether a pressure-relief directional shroud and piping is required for onshore application. If "required" is selected, specify details of the shroud and piping in the "Additional notes" column. Default value : not required
Note on C100: Select whether space heaters are required in control cabinets and/or throats. If "required" is selected, specify the space heater locations in the "Additional notes" column. Default value : not required
Note on C102: Select whether the transformer is to be subjected to the audible sound level design test in subclause 8.2.5. Default value : not required
Note on C103: Select whether the transformer is to be subjected to the temperature rise design test in IEEE Std C57.12.90. If the temperature rise testing conditions are different than those of the design test, specify each parameter in the "Additional notes" column. Default value : not required
Note on C104: Select whether the lightning impulse design test described in Table 5 and IEEE Std C57.12.90 is required. This is a routine test for distribution transformers and power transformers rated 15 MVA and above with a primary voltage rating 69 kV and above. Default value : not required
Note on C105: Select whether the transformer is to be subjected to the core insulation resistance design test in IEEE Std C57.12.00. This is a routine test for any power transformer. Default value : not required
Note on C106: Select whether the transformer is to be subjected to the partial discharge design test in IEEE Std C57.12.90. This test is normally conducted on all high-voltage components. This provides baseline information if partial discharge monitoring is selected. Default value : not required
Note on C107: Select whether the transformer is to be subjected to the short-circuit capability test in IEEE Std C57.12.90. Distribution type transformers will have a design (type) test report available. Power type transformers normally use the calculation method. Default value : not required
Note on C108: Select whether the transformer is to be subjected to the dissolved gas-in-oil analysis test before the start of all tests and after the completion of all tests in IEEE Std C57.12.00. This is a routine test for large (Class II) power transformers. Default value : required
Note on C109: Select whether the transformer is to be subjected to the winding insulation resistance test after the completion of all tests in IEEE Std C57.12.00. This is a routine test for power transformers. Default value : required
Note on C111: Select the transformer preservation requirement. Manufacturer's standard packaging is appropriate for domestic shipping (not offshore) and short-term outdoor storage. If "special" is selected, specify in the "Additional notes" column or "Supplement"' tab. Default value : manufacturer's standard
Note on C112: Select whether desiccant bags are required to be installed for shipping. Default value : required

## PDS Pad-mounted
Row | IOGP S-754D (1.0) Procurement Data Sheet for Pad-mounted Transformers (IEEE) | [6 empty] | Issue
2 | Ref. clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Equipment identification
4 | 5.12.2 | Tag number : | input data |  | input data
5 | 5.12.2 | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Site conditions
9 | 4.1.2.1, 4.3.1, 4.4.1, 5.10, 6.11.5 | Maximum ambient air temperature : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50 | 55 | other
10 | 4.1.2.2, 4.3.1, 4.4.1 | Minimum ambient air temperature : | -20 | °C | -20 | °C |  |  |  |  | select | -20 | -30 | -40 | other
11 | 4.1.2.1, 4.3.1, 4.4.1, 5.10 | Ambient 24-hour average temperature : | 30 | °C | 30 | °C |  |  |  |  | select | 30 | 40 | 45 | 50 | other
12 | 4.3.1, 4.3.2, 4.4.1, 5.10, 5.12.2.5, Table 1 | Altitude of installation : | ≤ 1000 | m | ≤ 1000 | m |  |  |  |  | select | ≤ 1000 | other
13 | 4.3.3, 5.13.1 | Seismic design : | not required |  | not required | [5 empty] | select | required | not required
14 | 4.3.3, 5.13.1, 5.13.5 | Seismic site location : | input data |  | input data
15 | 4.3.3, 5.13.1 | Seismic certificate : | not required |  | not required | [5 empty] | select | required | not required
16 | 4.3.3, 4.3.5, 5.12.2.6, 6.2.3.6, 6.11.7 | Area classification : | unclassified |  | unclassified | [5 empty] | select | unclassified | classified
17 | 4.1.7, 4.4.1, 5.10 | Installation environment : | outdoor |  | outdoor | [5 empty] | select | indoor | outdoor
18 | 4.3.3, 4.4.1, 5.13.5, 6.17.1 | Unusual environments : | none |  | none | [5 empty] | select | none | corrosive gases | fumes / vapor / steam / salt air | excessive harmonics | hot and humid climates | abnormal vibration/shock/tilting | other or multiple
19 | 4.1.9 | Paint color : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | ANSI 61 grey | other
20 | 5.13.2, 5.13.4, 9.3 | Certification : | not required |  | not required | [5 empty] | select | not required | NRTL | USCG/ABS | other
21 | 5.13.3 | Compliance with Canadian standards : | not applicable |  | not applicable | [5 empty] | select | not applicable | CAN/CSA C2.1:06 | CAN/CSA C88 | CAN/CSA C227.4
22 |  | Ratings and system parameters
23 | 5.10, 5.4.2, 9.3, Table 2 | kVA rating : | input data | kVA | input data | kVA
24 | 6.9, 7.4 | Winding material : | select |  | select | [5 empty] | select | copper | aluminum
25 | 5.1 | Primary winding voltage : | input data | kV | input data | kV
26 | 5.6, 5.10 | Primary winding configuration : | select |  | select | [5 empty] | select | delta | wye
27 | 5.10, 5.10.2.1 | Primary winding BIL : | input data | kV | input data | kV
28 | 5.10.3.2, 5.10.3.4, 6.8 | Primary neutral grounding : | select |  | select | [5 empty] | select | not applicable | solidly grounded | resistance grounded | ungrounded | other
29 | 5.10, Table 3, Table 4 | Secondary 1 winding voltage : | input data | kV | input data | kV
30 | 5.6, 5.10 | Secondary 1 winding configuration : | select |  | select | [5 empty] | select | delta | wye
31 | 5.10, Table 3, Table 4 | Secondary 1 winding BIL : | input data | kV | input data | kV
32 | 5.10.3.2, 5.10.3.4, 6.8 | Secondary 1 neutral grounding : | select |  | select | [5 empty] | select | not applicable | solidly grounded | low resistance grounded | high resistance grounded | ungrounded | other
33 | 5.2, 5.10 | Frequency : | 60 | Hz | 60 | Hz |  |  |  |  | select | 50 | 60 | other
34 | 7.1.5.5, 12.1.4 | Available fault current (symmetrical) : | input data | kA | input data | kA
35 | 7.1.5.2, 12.1.4 | System X/R ratio : | input data |  | input data
36 | 4.1.5 | Supply non-linear loads : | no |  | no | [5 empty] | select | no | yes
37 | 6.2.3, 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Auxiliary power : | 120 | V ac | 120 | V ac |  |  |  |  | select | 120 | 208 | 240 | other
38 | 5.10.3.2 | Neutral bushing grounding connection for solidly grounded systems : | grounded to ground pad with removable strap |  | grounded to ground pad with removable strap | [5 empty] | select | grounded to ground pad with removable strap | none
39 |  | Cooling system
40 | 6.6.1, 6.6.4, 6.15.1.10, 8.2.1, 8.2.1.1, 8.2.1.2 | Insulating liquid : | mineral oil |  | mineral oil | [5 empty] | select | mineral oil | natural ester | synthetic ester | silicone fluid | other
41 |  | Bushings
42 | 5.10.3.4 | Primary bushing BIL : | input data | kV | input data | kV
43 | 5.10.3.4 | Secondary bushing BIL : | input data | kV | input data | kV
44 | 5.10.3.4 | Neutral bushing BIL : | input data | kV | input data | kV
45 |  | Air terminal chamber (ATC)
46 | 6.10.1.2, 6.10.1.7, 6.10.1.10, 6.10.1.11, 6.10.1.17 | Enclosure rating : | NEMA 3R |  | NEMA 3R | [5 empty] | select | NEMA 3R | NEMA 4 | NEMA 4X
47 | 6.10.1.4, 6.10.1.6, 6.10.1.9 | Enclosure material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | aluminum | 316L stainless steel
48 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heaters : | not required |  | not required | [5 empty] | select | not required | required
49 |  | Power connections
50 | 6.1.5 | Primary conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil | in. | mm
51 | 6.1.5 | Secondary conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil | in. | mm
52 | 6.1.5 | Neutral conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil | in. | mm
53 | 6.9 | Primary conductor material : | select |  | select | [5 empty] | select | copper | aluminum
54 | 6.9 | Secondary conductor material : | select |  | select | [5 empty] | select | copper | aluminum
55 | 6.9 | Neutral conductor material : | select |  | select | [5 empty] | select | copper | aluminum
56 | 6.1.5 | Number of primary conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
57 | 6.1.5 | Number of secondary conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
58 | 6.1.5 | Number of neutral conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
59 | 6.1.5 | Ground conductor size : | input data | select | input data | select |  |  |  |  | select | AWG | kcmil
60 | 6.1.5 | Number of ground conductors per phase : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4 | other
61 |  | Accessories
62 | 6.10.1.21, 6.10.1.22 | Thermal scanning inspection windows : | not required |  | not required | [5 empty] | select | not required | required
63 | 12.1.2 | Pad-mounted overcurrent protection : | not required |  | not required | [5 empty] | select | not required | required
64 | 12.1.1, 12.1.2 | Pad-mounted insulated switch : | not required |  | not required | [5 empty] | select | not required | required
65 |  | Pad-mounted sampling location : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | external from terminations
66 | 6.2.1.8 | Onshore pressure-relief directional shroud and piping : | not required |  | not required | [5 empty] | select | not required | required
67 | 6.11.1 - 6.11.8, 6.11.10 - 6.11.12 | Space heaters for control cabinets and throats : | not required |  | not required | [5 empty] | select | not required | required
68 |  | Supplemental testing
69 | 6.2.6.5.1, 8.2.1, 8.2.1.1, 8.2.1.2, 8.2.1.4, 8.2.3, Table 17 | Dissolved gas-in-oil analysis (DGA) : | required |  | required | [5 empty] | select | not required | required
70 | 8.2.1.5, Table 17 | Winding insulation resistance : | required |  | required | [5 empty] | select | not required | required
71 |  | Shipping and preservation
72 | 10.1.1 - 10.1.10, 10.2.1 | Equipment preservation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | long term outdoor storage | special
73 | 10.1.10 | Desiccant bags installed : | required |  | required | [5 empty] | select | not required | required
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the tag.
Note on C7: Select CAS level to be applied in IOGP S-754Q, Annex A. Default value : D
Note on C9: Select the maximum ambient air temperature of the air that is cooling the radiators. The default value as per IEEE Std C57.12.00 is 40 °C. If "other" is selected, specify the maximum limit in the "Additional notes" column. Default value : 40
Note on C10: Select the minimum ambient air temperature. Ambient temperatures below -20 °C are considered unusual service conditions. If "other" is selected, specify the minimum limit ( i.e., below -20 °C) in the "Additional notes" column. Default value : -20
Note on C11: Select the average 24-hour ambient air temperature of the air that is cooling the radiators. The default value as per IEEE Std C57.12.00 is 30 °C. If "other" is selected, specify the average ambient in the "Additional notes" column. Default value : 30
Note on C12: Select the transformer installation altitude. IEEE Std C57.12.00 is based on the maximum altitude of 1000 m (3300 ft). Derating information is provided in Table 1. If "other" is selected, specify the altitude in the "Additional notes" column. Default value : ≤ 1000
Note on C13: Select whether the seismic design is required. Additional information as per IEEE Std 693, such as seismic qualification level or the seismic exposure map information, should be provided in the "Additional notes" column. Default value : not required
Note on C14: Specify the site physical address or latitude and longitude to determine the seismic qualification level and additional parameters.
Note on C15: Select whether a third-party seismic certificate is required. Default value : not required
Note on C16: Select whether the transformer is installed in a hazardous (classified) area. If "classified", specify the Division/Zone, Group and AIT for the installation location in the "Additional notes" column. Default value : unclassified
Note on C17: Select whether the transformer is installed indoor or outdoor. Default value : outdoor
Note on C18: Select the unusual environments or contaminant to which the transformer will be exposed. If "other or multiple" is selected, specify in the "Additional notes" column. Default value : none
Note on C19: Select the paint color for the transformer. ANSI 61 grey refers to the paint color specified in ASTM D1535 (Munsell Notation 8.3G 6.10/0.54). If "other" is selected, specify the paint color using the ANSI designation in the "Additional notes" column. Default value : manufacturer's standard
Note on C20: Select the certification requirements for the transformer. If "other" is selected, specify in the "Additional notes" column. NRTL certification in accordance with UL guideline XPLH applies only to distribution transformers rated 69 kV or below. Default value : not required
Note on C21: Select the Canadian standard to which the transformer will be built. Default value : not applicable
Note on C23: Select the base kVA rating for the transformer. The preferred continuous base kVA ratings are listed in Table 2.
Note on C24: Select the base material for the transformer windings. Copper is normally used for power transformer windings and aluminum is used for distribution and pad-mounted transformers.
Note on C25: Specify the value of the voltage in kV for the primary winding. The preferred values for nominal system voltages are given in Table 3 and Table 4.
Note on C26: Select the winding configuration for the transformer primary windings. Standard connection arrangements for particular types of transformers are in IEEE Std C57.12.70.
Note on C27: Specify the basic lightning impulse insulation level (BIL). BIL is dependent on the degree of exposure of the transformer and characteristics of the overvoltage protection system. Refer to Table 3 and Table 4 for guidance.
Note on C28: Select the transformer neutral grounding arrangement for the transformer primary winding. Select "not applicable" for a delta winding configuration. If "other" is selected, indicate the grounding type in the "Additional notes" column.
Note on C29: Specify the value of the voltage in kV for the secondary winding. The preferred values for nominal system voltages are given in Table 3 and Table 4.
Note on C30: Select the winding configuration for the transformer secondary winding. Standard connection arrangements for particular types of transformers are in IEEE Std C57.12.70.
Note on C31: Specify the basic lightning impulse insulation level (BIL). BIL is dependent on the degree of exposure of the transformer and characteristics of the overvoltage protection system. Refer to Table 3 and Table 4 for guidance.
Note on C32: Select the transformer neutral grounding arrangement for the transformer secondary winding. Select "not applicable" for a delta winding configuration.
Note on C33: Select the nominal operating frequency. If "other"' is selected, specify in the "Additional notes" column. Default value : 60
Note on C34: Specify the available fault current (symmetrical) of the system at the point of connection for the primary of the transformer. This value is normally available from the purchaser's power system study.
Note on C35: Specify the X/R ratio (system reactance / system resistance) of the system at the point of connection for the primary of the transformer. This value is normally available from the purchaser's power system.
Note on C36: Select whether the transformer will be supplying large non-linear loads. If "yes" is selected, specify additional details for the number, size and type of non-linear loads or advise % THD anticipated in the "Additional notes" column. Default value : no
Note on C37: Select the auxiliary power feeder voltage supplied to the transformer for fans, space heaters, controls and accessories. If "other" is selected, specify additional details including the voltage and number of phases in the "Additional notes" column. Default value : 120
Note on C38: Select the transformer neutral bushing grounding connection for solidly grounded systems. Default value : grounded to ground pad with removable strap
Note on C40: Select the type of insulating liquid for the transformer. Natural ester oil is used for low environmental impact and improved fire resistance. If is "other" is selected, specify the insulating liquid in the "Additional notes" column. Default value : mineral oil
Note on C42: Specify the basic lightning impulse insulation level (BIL) for the primary bushing. The minimum BIL level for the bushing is no less than the winding BIL level. In certain applications, a higher BIL level may be preferred.
Note on C43: Specify the basic lightning impulse insulation level (BIL) for the secondary bushing. The minimum BIL level for the bushing is no less than the winding BIL level. In certain applications, a higher BIL level may be preferred.
Note on C44: Specify the basic lightning impulse insulation level (BIL) for the neutral bushing. The minimum BIL level for the bushing is no less than the winding BIL level. In certain applications, a higher BIL level may be preferred.
Note on C46: Select the enclosure rating for the transformer ATC(s). NEMA 4 with 316L stainless steel material is typical for offshore, marine and corrosive environment applications. Default value : NEMA 3R
Note on C47: Select the material for the ATC enclosure. 316L stainless steel can be used for extreme climate and corrosive environment conditions. Default value : manufacturer's standard
Note on C48: Select whether space heaters are required in the ATC(s). Space heaters are typically installed in transformer ATCs where moisture and condensation are problematic for the installation location. Default value : not required
Note on C50: Specify the power conductor size for the transformer primary. Select the appropriate unit designation (i.e., AWG, kcmil, in., mm) in the "UOM" (units) column.
Note on C51: Specify the power conductor size for the transformer secondary. Select the appropriate unit designation (i.e., AWG, kcmil, in., mm) in the "UOM" (units) column. For three-winding transformers, the additional secondary winding is typically the same.
Note on C52: Specify the power conductor size for the transformer neutral. Select the appropriate unit designation (i.e., AWG, kcmil, in., mm) in the "UOM" (units) column.
Note on C53: Select the material for the primary power connection. This will determine the need for any dissimilar metal interfaces for the conductor termination to the primary bushings.
Note on C54: Select the material for the secondary power connection. This will determine the need for any dissimilar metal interfaces for the conductor termination to the secondary bushings.
Note on C55: Select the material for the neutral power connection. This will determine the need for any dissimilar metal interfaces for the conductor termination to the neutral bushing.
Note on C56: Specify the number of power conductors for the transformer primary. If "other" is selected, specify the number of phase conductors in the "Additional notes" column.
Note on C57: Specify the number of power conductors for the transformer secondary. If "other" is selected, specify the number of phase conductors in the "Additional notes" column. For three-winding transformers, the additional secondary winding is typically the same.
Note on C58: Specify the number of power conductors for the transformer neutral. If "other" is selected, specify the number of neutral conductors in the "Additional notes" column.
Note on C59: Specify the ground conductor size for the transformer. Specify the appropriate unit designation (i.e., AWG, kcmil) in the "UOM" (units) column.
Note on C60: Specify the number of ground conductors for the transformer. If "other" is selected, specify the number of ground conductors in the "Additional notes" column.
Note on C62: Select whether thermal scanning inspection windows are required in the ATC(s). The manufacturer recommends the locations in order to provide adequate viewing for the transformer power connections. Default value : not required
Note on C63: Select whether overcurrent protection is required for the pad-mounted transformer. If required, review the options in IEEE Std C57.12.34-2022, Annex A.3 and specify the details for the type of overcurrent protection in the "Additional notes" column. Default value : not required
Note on C64: Select whether an under insulating liquid switch is required for the pad-mounted transformer. If required, review the options in IEEE Std C57.12.34-2022, Annex A.4 and specify the details of the switch in the "Additional notes" column. Default value : not required
Note on C65: Select the sampling location for the pad-mounted transformer. Default value : manufacturer's standard
Note on C66: Select whether a pressure-relief directional shroud and piping is required for onshore application. If "required" is selected, specify details of the shroud and piping in the "Additional notes" column. Default value : not required
Note on C67: Select whether space heaters are required in control cabinets and/or throats. If "required" is selected, specify the space heater locations in the "Additional notes" column. Default value : not required
Note on C69: Select whether the transformer is to be subjected to the dissolved gas-in-oil analysis test before the start of all tests and after the completion of all tests in IEEE Std C57.12.00. This is a routine test for large (Class II) power transformers. Default value : required
Note on C70: Select whether the transformer is to be subjected to the winding insulation resistance test after the completion of all tests in IEEE Std C57.12.00. This is a routine test for power transformers. Default value : required
Note on C72: Select the transformer preservation requirement. Manufacturer's standard packaging is appropriate for domestic shipping (not offshore) and short-term outdoor storage. If "special" is selected, specify in the "Additional notes" column or "Supplement"' tab. Default value : manufacturer's standard
Note on C73: Select whether desiccant bags are required to be installed for shipping. Default value : required

## Supplement
Row |  | IOGP S-754D (1.0) Procurement Data Sheet for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE) | Issue
2 | Purchase order specific requirements
3 | Delete this sheet if not required.
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60

## Guidance
IOGP S-754D (1.0) Procurement Data Sheet for Liquid-Immersed Distribution, Power and Regulating Transformers (IEEE)
Guidance on the use of this procurement data sheet (PDS)
This PDS is to be used in conjunction with IOGP S-754, Supplementary Specification to IEEE Std C57.12.00 for Liquid-Immersed Distribution, Power and Regulating Transformers.
This PDS consists of 3 worksheets. Complete the Tab for your specific transformer type. Guidance for the selection of the transformer type is provided in the table below.
PDS Power |  | Liquid-Immersed Power Transformers |  | 10 MVA to 150 MVA
PDS Distribution |  | Liquid-Immersed Distribution Substation Transformers |  | 300 kVA to 10 MVA
PDS Pad-mounted |  | Pad-mounted, Self-Cooled Transformers |  | Totally enclosed, compartmentalized up to 10 MVA
This PDS is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This PDS, completed with requested values, should be delivered back to the purchaser by using the PDS template or other mutually agreed method.
The Ref. clause column provides references back to the following: — parent standard and/or supplementary specification when the PDS is used in conjunction with a supplementary specification; — specification when the PDS is used in conjunction with a standalone specification.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the PDS item and/or an explanation of how to complete the input.
The Additional notes column may be used by the purchaser or supplier to provide additional information pertinent to the specification and/or supply of the equipment.
The Issue column should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the PDS that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data in a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set in accordance with essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the PDS. This worksheet is not intended to modify requirements defined in the specification.
The Purchaser requirement and Purchaser requirement UOM columns specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
The Supplier offered value and Supplier offered UOM columns are used by the supplier to declare the offered value. Where the offered product characteristic differs from the purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the purchaser requirement.
The Requirement CFIHOS ID and Equipment CFIHOS ID in columns K and L enable information exchange in a data-centric manner. Note that these columns are in a hidden area of the worksheet and can be unhidden for use.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  |  | select | select | select
input data |  |  | select | input data | select
select |  |  | UOM | select | UOM
input data |  |  | UOM | input data | UOM
select |  |  |  | select
input data |  |  |  | input data
select |  |  | select | select | select
input data |  |  | select | input data | select
select |  |  | UOM | select | UOM
input data |  |  | UOM | input data | UOM
select |  |  |  | select
input data |  |  |  | input data
select |  |  | select | select | select
input data |  |  | select | input data | select
select |  |  | UOM | select | UOM
input data |  |  | UOM | input data | UOM
select |  |  |  | select
input data |  |  |  | input data