## Addendum 1
Date of issue:
September 2025
Affected publication:
IOGP S-560D, Procurement Data Sheet for Low-voltage Switchgear and Controlgear (IEC), Third Edition, December 2022
ADDENDUM 1
This addendum (Version 3.01) replaces Edition 3.0 published in December 2022.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Row | Column | Update
| 10 | All | New data sheet item "Local language for information/caution/danger/warning labels"
| 36 | All | New data sheet item "Early smoke / fire detection"
| 37 | All | New data sheet item "Status colour of indicators and on human machine interface screens"
| 61 | All | New data sheet item "Provision for moving shipping section to location"
| 63 | Purchaser requirement / Supplier offered value - options | Options "IK08, IK09, IK10" * deleted New option "other"
| 76 | Purchaser requirement / Supplier offered value - options | New option "other"
| 77 | Purchaser requirement / Supplier offered value - options | New option "other"
| 79 | Purchaser requirement / Supplier offered value - options | New option "ACB"
| 88 | Description | Embedded guidance note amended
|  | Purchaser requirement / Supplier offered value - options | Options "≥4, ≥7, 5, ≥15, ≥37" * deleted New option "other"
| 98 | Description | Default value in guidance note amended
|  | Purchaser requirement / Supplier offered value | Default value amended to "required"
| 100 | Description | Amended from "Auxiliary circuit wiring insulation type" * to "Internal wiring insulation type" Embedded guidance note amended
|  | Purchaser requirement / Supplier offered value - options | Option "other" deleted New option "PVC"
| 102 | All | New data sheet item "Busbar plating material"
| 125 | Purchaser requirement / Supplier offered value - options | New option "other (see single line diagram/circuit schedule)"
List of updates (continued)
| Row | Column | Update
| 156 | Purchaser requirement / Supplier offered value - options | Option "required" * deleted New options "manufacturer's standard, maintenance mode switch (SCPD), arc flash relay (light sensor), arc quenching device (AQD), current limiting device (IALD), other"
| 152 * | All | Data sheet item "Internal arc-fault reduction device (IARD) type" * deleted
| 153 * | All | Data sheet item "Internal arc-fault control device (IACD) type" * deleted
| 157 | All | New data sheet item "Maintenance mode activation method"
| Several | Row | Numbering updated as per new and deleted rows
* Data from Edition 3.0.

## Front & Preliminaries
[5 empty] | SPECIFICATION | September 2025
[5 empty] | IOGP S-560D | Version 3.01
ADDENDUM 1 TO THIRD EDITION (DECEMBER 2022)
Procurement Data Sheet for
Low-voltage Switchgear and
Controlgear (IEC)
Revision history
| VERSION | DATE | PURPOSE
| 3.01 | September 2025 | Addendum 1
| 3 | December 2022 | Third Edition
| 2 | November 2016 | Second Edition
| 1 | June 2016 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-560D (3.01) Procurement Data Sheet for
Low-voltage Switchgear and Controlgear (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
This third edition cancels and replaces the second edition published in November 2016. Due to technical writing requirements leading to extensive changes, this third edition should be treated as a new document.
IOGP S-560D (3.01) Procurement Data Sheet for
Low-voltage Switchgear and Controlgear (IEC)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of low-voltage switchgear and controlgear in accordance with IOGP S-560 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-560), information requirements specification (IOGP S-560L) and quality requirements specification (IOGP S-560Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Procurement Data Sheet
Row | IOGP S-560D (3.01) Procurement Data Sheet for Low-voltage Switchgear and Controlgear (IEC) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Project country : | input data |  | input data
9 |  | Project region : | input data |  | input data
10 |  | Local language for information/caution/danger/warning labels : | input data |  | input data
11 |  | Electrical system
12 | 8.6.1 | Earthing system : | select |  | select | [5 empty] | select | TT | TN-C | TN-C-S | IT | TN-S | other
13 |  | System configuration phases/wires : | select |  | select | [5 empty] | select | 3-phase 3-wire | 3-phase 4-wire | other
14 |  | Voltage ratings
15 | 5.2.1 | Nominal voltage of supply system : | select | V | select | V |  |  |  |  | select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | other
16 |  | Transient overvoltages : | category III |  | category III | [5 empty] | select | category III | category IV
17 |  | Current ratings
18 | 5.3.1 | Rated current of assembly busbars (InA) : | select | A | select | A |  |  |  |  | select | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000
19 | 6.1 | Rated peak withstand current (Ipk) : | select | kA | select | kA |  |  |  |  | select | 40 | 52,5 | 66,15 | 84 | 105 | 138,6
20 | 6.1,9.3.1 | Rated short-time withstand current (Icw) : | select | kA | select | kA |  |  |  |  | select | 20 | 25 | 31,5 | 40 | 50 | other
21 | 6.1 | Rated short-time withstand current (Icw) time duration : | 1 | s | 1 | s |  |  |  |  | select | 1 | 3
22 |  | Short-circuit current in neutral conductor and in protective circuit : | 60 | % | 60 | % |  |  |  |  | select | 60 | 100 | other
23 |  | Rated diversity factor (RDF)
24 |  | Assumed loading factor distribution - 1 circuit : | 1,0 |  | 1,0
25 |  | Assumed loading factor distribution - 2 and 3 circuits : | 0.9 |  | 0.9
26 |  | Assumed loading factor distribution - 4 and 5 circuits : | 0.8 |  | 0.8
27 |  | Assumed loading factor distribution - 6 and 9 circuits : | 0.6 |  | 0.6
28 |  | Assumed loading factor distribution - 10 or more circuits : | 0.7 |  | 0.7
29 |  | Assumed loading factor electric actuator (MOV) : | 0.2 |  | 0.2
30 |  | Assumed loading factor motors rated less than or equal to 100 kW : | 0.8 |  | 0.8
31 |  | Assumed loading factor motors rated greater than 100 kW : | 1 |  | 1
32 |  | Rated frequency (fn)
33 | 5.5 | Rated frequency (fn) : | 50 | Hz | 50 | Hz |  |  |  |  | select | 50 | 60 | DC
34 |  | Other characteristics
35 | 8.102.1 | Mounting arrangement : | select |  | select | [5 empty] | select | manufacturer's standard | longitudinal channels flush with floor | directly bolted to concrete floor | mounted on elevated stanchions | other
36 |  | Early smoke / fire detection : | not required |  | not required | [5 empty] | select | required | not required
37 | Table 19 | Status colour for indicators and human machine interface (HMI) screens : | Table 19 |  | Table 19 | [5 empty] | select | Table 19 | user defined
38 |  | Information relating to assembly
39 |  | Language used for all provided information : | English |  | English | [5 empty] | select | English | other
40 |  | Instructions for handling, installation, operation and maintenance
41 | 6.2.2 | Lifting device for withdrawable parts heavier than 25 kg : | not required |  | not required | [5 empty] | select | not required | required
42 |  | Device and/or component identification
43 |  | Main component, primary identification language : | English |  | English | [5 empty] | select | English | other
44 |  | Mimic (synoptic) diagrams : | not required |  | not required | [5 empty] | select | not required | required
45 |  | Normal service conditions
46 |  | Location type : | indoor climate controlled |  | indoor climate controlled | [5 empty] | select | indoor climate controlled | indoor ventilated | other
47 | 8.102.3,8.102.4 | Operating environment : | onshore |  | onshore | [5 empty] | select | onshore | offshore – fixed | offshore – floating | marine (ship) | other
48 | 7.1.1 | Ambient air temperature - lower limit : | -5 | °C | -5 | °C |  |  |  |  | select | -5 | other
49 |  | Ambient air temperature - upper limit : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | other
50 |  | Ambient air temperature - daily average maximum : | 35 | °C | 35 | °C |  |  |  |  | select | 35 | other
51 |  | Humidity conditions - maximum relative humidity : | 95 % at −5 °C to +30 °C | % | 95 % at −5 °C to +30 °C | % |  |  |  |  | select | 95 % at −5 °C to +30 °C | other
52 |  | Pollution degree of macro-environment (of installation environment) : | 3 |  | 3 | [5 empty] | select | 1 | 2 | 3
53 |  | Altitude : | ≤ 2 000 | m | ≤ 2 000 | m |  |  |  |  | select | ≤ 2 000 | other
54 |  | Special service conditions
55 |  | Seismic activity zone in accordance with IEC 60721-2-6 : | not applicable |  | not applicable | [5 empty] | select | not applicable | Zone 1 | Zone 2 | Zone 3 | Zone 4
56 |  | EMC environment : | A |  | A | [5 empty] | select | A | B
57 | 8.102.3,8.102.4 | Maximum rolling of vessel in dynamic conditions : | not applicable |  | not applicable
58 | 8.102.3,8.102.4 | Maximum pitching of vessel in dynamic conditions : | not applicable |  | not applicable
59 |  | Storage and handling
60 |  | Storage and handling environmental conditions : | within IEC default conditions |  | within IEC default conditions | [5 empty] | select | within IEC default conditions | outside IEC default conditions | manufacturer's standard packing | special packing | other
61 |  | Provision for moving switchgear shipping section to location : | select |  | select | [5 empty] | select | rolled across floor on pipes | not applicable
62 |  | Degree of protection provided by assembly enclosure
63 |  | Minimum external mechanical impact protection : | IK07 |  | IK07 | [5 empty] | select | IK07 | other
64 | 8.2.2 | Protection against ingress of solid foreign bodies and ingress of water : | IP3X |  | IP3X | [5 empty] | select | IP3X | IP4X | IP31 | IP41 | other
65 |  | Protection against electric shock
66 |  | Type of protection against electric shock - basic protection : | constructional (manufacturer's standard) |  | constructional (manufacturer's standard) | [5 empty] | select | constructional (manufacturer's standard) | additional measures
67 |  | Type of protection against electric shock - fault protection : | automatic disconnection of supply |  | automatic disconnection of supply | [5 empty] | select | automatic disconnection of supply | electrical separation | total insulation
68 |  | Access to manually operated devices : | authorized persons |  | authorized persons | [5 empty] | select | authorized persons | other
69 | 8.5.5.101.7 | Closed compartment doors : | manufacturer's standard locking facility |  | manufacturer's standard locking facility | [5 empty] | select | manufacturer's standard locking facility | padlockable | hasp and padlock
70 | 8.2.3 | Safety shutters, disconnectors and switches : | select |  | select | [5 empty] | select | manufacturer's standard locking facility | padlockable | hasp and padlock
71 | 8.5.5.101.7 | Padlock provider : | select |  | select | [5 empty] | select | not applicable | user supplied | manufacturer supplied
72 |  | Withdrawable parts (IEC 61439-2)
73 | 8.5.101 | Type of electrical connections for outgoing functional units rated up to and including 630 A : | withdrawable |  | withdrawable | [5 empty] | select | withdrawable | disconnectable | fixed
74 | 8.5.2.101 | Facility to remotely test withdrawn functional units : | select |  | select | [5 empty] | select | required | not required
75 |  | Selection of switching devices and components
76 | 8.5.3.101.2 | Incoming unit switching device requirement : | withdrawable ACB |  | withdrawable ACB | [5 empty] | select | withdrawable ACB | withdrawable switch-disconnector | non-withdrawable switch-disconnector | other
77 |  | Bus coupler switching device requirement : | withdrawable ACB |  | withdrawable ACB | [5 empty] | select | withdrawable ACB | withdrawable switch-disconnector | non-withdrawable switch-disconnector | other
78 | 8.5.3,8.5.3.104.1 | Main circuit protection for lighting and small power feeders : | select |  | select | [5 empty] | select | MCCB/MCB | fuse-links with blade contacts (DIN NH fuse system) | fuse-links for bolted connections (BS88 bolted) | other
79 | 8.5.3.104.1,8.5.3.105.1 | Main circuit protection for motor starters and contactor feeders : | select |  | select | [5 empty] | select | MCCB/MCB | fuse-links with blade contacts (DIN NH fuse system) | fuse-links for bolted connections (BS88 bolted) | ACB | other
80 |  | Air circuit breakers
81 | 8.5.3.103.2.5 | Spring charging motor voltage : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | AC line-neutral | AC line-line | 24 V DC | 48 V DC | 110 V DC | 125 V DC
82 |  | Air circuit breaker control voltage : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | 24 V DC | 48 V DC | 110 V DC | 125 V DC | AC line-neutral
83 | 8.5.3.103.2.10 | Air circuit breaker auxiliary contact provision : | none |  | none | [5 empty] | select | none | 1 NO and 1 NC | 2 NO and 2 NC | other
84 |  | Motor starters and contactor feeders
85 | 8.5.3.105.13,8.5.3.105.14,8.5.3.105.15 | Contactor control circuit voltage : | 230 V AC |  | 230 V AC | [5 empty] | select | 230 V AC | 110 V AC | other
86 | 8.5.3.105.13,8.5.3.105.14,8.5.3.105.15 | Contactor control power source : | internal within each functional unit |  | internal within each functional unit | [5 empty] | select | internal within each functional unit | internal within each bus section | external supply | other
87 | 8.5.3.106.5 | Earth fault front of compartment reset : | select |  | select | [5 empty] | select | required | not required
88 |  | Minimum motor size for space heater : | not required | kW | not required | kW |  |  |  |  | select | not required | other
89 |  | Motor space heater supply voltage : | select |  | select | [5 empty] | select | 230 V AC | 110 V AC | other
90 |  | Unearthed electrical supplies (IT)
91 |  | Provision of portable insulation fault locator : | select |  | select | [5 empty] | select | not applicable | required | not required
92 |  | Accessibility
93 | 8.5.5.101.2 | PSC-assembly physical configuration : | select |  | select | [5 empty] | select | access front and back | access front only | back to back | other
94 |  | Auxiliary components
95 | 8.5.10.2.3.3,8.5.3.103.2.11 | Test blocks for ACB protection relay injection testing : | not required |  | not required | [5 empty] | select | not required | required - manufacturer's standard | required - type FT-1 | required - other
96 | 8.5.10.2.3.1 | Energy and maximum demand metering accuracy : | select |  | select | [5 empty] | select | class 1,0 | class 0,5 | class 0,1
97 |  | Internal electrical circuits and connections
98 | 8.6.1 | Main circuit busbar insulation : | required |  | required | [5 empty] | select | required | required - colour coded | not required | other
99 |  | Main circuit earth-neutral link within incoming circuit units : | required |  | required | [5 empty] | select | required | not required | not applicable
100 |  | Internal wiring insulation type : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | low smoke zero halogen | manufacturer's standard | PVC
101 | 8.6.5 | Supplementary conductor marking by colour : | not required |  | not required | [5 empty] | select | not required | required - see supplement
102 |  | Busbar plating material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | tin | silver | other
103 |  | Terminals for external conductors
104 |  | Incoming (supply) unit direction of external conductors : | select |  | select | [5 empty] | select | from below | from above
105 | 8.8 | Incoming (supply) unit external conductor type : | select |  | select | [5 empty] | select | cable | busbar trunking system
106 |  | Outgoing (load) unit direction of external conductors : | select |  | select | [5 empty] | select | from below | from above
107 | 8.8 | Outgoing (load) unit external conductor type : | cable |  | cable
108 |  | Auxiliary cable direction of external conductors : | select |  | select | [5 empty] | select | from below | from above
109 |  | Auxiliary cable external conductor type : | cable |  | cable
110 |  | External conductor material : | copper |  | copper | [5 empty] | select | copper | aluminium
111 | 8.8 | Multicore cable entry method : | undrilled removable gland-plate |  | undrilled removable gland-plate | [5 empty] | select | undrilled removable gland-plate | drilled removable gland-plate | multi-cable transit | other
112 | 8.8 | Single core cable entry method (non-magnetic) : | undrilled removable gland-plate |  | undrilled removable gland-plate | [5 empty] | select | undrilled removable gland-plate | drilled removable gland-plate | multi-cable transit | other
113 |  | Special glanding requirement : | none |  | none | [5 empty] | select | none | insulated glands | other
114 |  | Terminals for control and auxiliaries
115 |  | Minimum spare unwired terminal provision for future use : | 10 % spare |  | 10 % spare | [5 empty] | select | 10 % spare | 20 % spare | other
116 |  | Internal separation of PSC-assemblies (IEC 61439-2:2020)
117 | 8.101] | Internal separation for ACB functional units : | Form 4a |  | Form 4a | [5 empty] | select | Form 4a | Form 4b | Form 3 type 2 | Form 4 type 1 | Form 4 type 2 | Form 4 type 3 | Form 4 type 4 | Form 4 type 5 | Form 4 type 6 | Form 4 type 7
118 | 8.101] | Internal separation for non-ACB functional units : | Form 3b |  | Form 3b | [5 empty] | select | Form 3b | Form 4a | Form 4b | Form 3 type 2 | Form 4 type 1 | Form 4 type 2 | Form 4 type 3 | Form 4 type 4 | Form 4 type 5 | Form 4 type 6 | Form 4 type 7
119 |  | Enclosure space heaters
120 | 8.103.1.1 | Assembly enclosure space heater requirement : | not required |  | not required | [5 empty] | select | not required | required
121 | 8.103.1.1 | Assembly enclosure space heater voltage : | select |  | select | [5 empty] | select | 230 V AC | 110 V AC | other
122 |  | Assembly enclosure space heater control method : | not applicable |  | not applicable | [5 empty] | select | not applicable | permanently on | thermostat | hygrostat
123 | 8.103.3,8.103.2.1,8.103.2.2,8.103.3.1,8.103.3.2,8.103.3.3,8.103.3.4,8.103.3.5 | Assembly enclosure space heater monitoring method : | not applicable |  | not applicable | [5 empty] | select | not applicable | supply side monitoring | heater current monitoring
124 |  | Provision for future development
125 |  | Provision of equipped spare functional outgoing units : | one of each type |  | one of each type | [5 empty] | select | 5% | 10% | 15% | 20% | one of each type | other (see single line diagram / circuit schedule)
126 |  | Provision of space for future outgoing functional units : | 10% |  | 10% | [5 empty] | select | 5% | 10% | 15% | 20%
127 |  | Condition monitoring
128 | 8.105.2.1 | Thermal monitoring : | not required |  | not required | [5 empty] | select | not required | required
129 |  | Circuit breaker condition monitoring : | not required |  | not required | [5 empty] | select | not required | required
130 |  | Motor condition monitoring equipment : | not required |  | not required | [5 empty] | select | not required | required
131 |  | Interface with control systems
132 |  | IED brand : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
133 |  | Process control interface (ICSS/DCS) media : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | not required | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fibre) | multiple | other
134 |  | Process control interface (ICSS/DCS) protocol : | select |  | select | [5 empty] | select | not required | volt-free contact / 4-20mA | DeviceNet | EtherNet/IP | IEC 61850 | Modbus TCP/IP | Profinet | Profibus | multiple | other
135 |  | Process control interface (ICSS/DCS) network redundancy : | select |  | select | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
136 |  | Electrical control interface (ECMS) media : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fibre) | other
137 |  | Electrical control interface (ECMS) protocol : | not required |  | not required | [5 empty] | select | not required | volt free contact / 4-20mA | DeviceNet | EtherNet/IP | IEC 61850 | Modbus TCP/IP | Profinet | Profibus | other
138 |  | Electrical control interface (ECMS) network redundancy : | not applicable |  | not applicable | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
139 | 8.5.3.106.9 | IED remote configuration via ECMS : | not applicable |  | not applicable | [5 empty] | select | not applicable | not required (local at IED only) | required | other
140 |  | Switchgear interlocking / intertripping interfaces
141 |  | Interlocking / intertripping interface media : | hardwired discrete |  | hardwired discrete | [5 empty] | select | hardwired discrete | not applicable | manufacturer's standard | via ECMS interface media | other
142 |  | Interlocking / intertripping interface protocol : | hardwired |  | hardwired | [5 empty] | select | hardwired | not required | manufacturer's standard | IEC 61850 | other
143 |  | Power management system (PMS) interfaces
144 |  | IED to power management system interface media : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | via ECMS media | hardwired discrete | serial cable | ethernet (Cu) | ethernet (fibre) | other
145 |  | IED to power management system interface protocol : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | volt-free contact / 4-20mA | via ECMS interface | IEC 61850 | other
146 |  | IED to power management system network redundancy : | not applicable |  | not applicable | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
147 |  | Generator control panel interfaces
148 |  | IED to generator control panel interface media : | not required |  | not required | [5 empty] | select | not required | hardwired | via ECMS media | other
149 |  | IED to generator control panel interface protocol : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | volt-free contact / 4-20mA | via ECMS interface | IEC 61850 | other
150 |  | Cyber security
151 |  | Security certification for industrial automation and control system components : | not required |  | not required | [5 empty] | select | not required | required | other
152 |  | Ratings of the internal arc classification (IAC)
153 | 6.1,9.3.1 | IEC TR 61641:2014 arcing class : | arcing class A |  | arcing class A | [5 empty] | select | arcing class A | arcing class B | arcing class C
154 | 9.3.1 | Permissible short-circuit current under arcing conditions (Ip arc) : | input data | kA | input data | kA
155 | 9.3.1 | Permissible arc duration (tarc) : | 0,3 | s | 0,3 | s |  |  |  |  | select | 0,3 | 0,5 | other
156 | 9.3.1 | Integrated internal arc-fault mitigation system (IAMS) : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | maintenance mode switch (SCPD) | arc flash relay (light sensor) | arc quenching device (AQD) | current limiting device (IALD) | other
157 |  | Maintenance mode activation method : | not required |  | not required | [5 empty] | select | not required | manufacturer's standard | local | remote | network communications | other
158 |  | Routine verification
159 | 11.101.1 | ECMS simulation test : | not applicable |  | not applicable | [5 empty] | select | not applicable | not required | required
Note on C4: Indicate the unique tag number for the equipment.
Note on C5: A functional description of the tag.
Note on C7: Select the CAS level to be applied in IOGP S-560Q, Annex A. For industrial proven solutions, CAS level D is specified unless user risk assessment indicates that a more stringent CAS level, C up to A is required. Default value : D
Note on C8: The name assigned by ISO to the country in ISO 3166-1.
Note on C9: Geographic location of the project within a country which will determine the applicability of local regulatory requirements.
Note on C10: Specify any additional local/native language to be used for information/caution/danger/warning messages on the equipment labels.
Note on C12: Select the type of system earthing in accordance with IEC 61439-2:2020 Table AA.1 and IEC 60364-1.
Note on C13: Select 3-phase, 3-wire when no neutral conductor required, 3-phase, 4-wire when a neutral conductor is required or "other" for systems other than 3-phase systems and detail the requirement in the additional notes.
Note on C15: Select the nominal voltage of the electrical system in accordance with IEC 61439-1:2020 3.8.9.1, 5.2.1 and IEC 60038:2021 Table 1.
Note on C16: See IEC 61439-1:2020 Table G.1. Category III: equipment intended to form part of a building or permanent industrial wiring installation. Category IV: equipment installed at/near the origin of electrical supply to buildings or for even higher reliability. Default value : category III
Note on C18: 630 A to 4 000 A are typical current ratings for PSC-assemblies for industrial use. Other standard ratings taken from the R10 numerical series of values that might be required for smaller assemblies are 315 A, 400 A and 500 A. See IEC 61439-3 for < 250 A.
Note on C19: Peak current values derived from IEC 61439-1:2020 Table 7 with Icw multiplied by factor "n" to give Ipk. When Icw is 20 kA, the corresponding Ipk is 40 kA. Likewise, 25kA = 52.5 kA, 31.5 kA = 66.15 kA, 40 kA = 84 kA, 50 kA = 105 kA and 63 kA = 138,6 kA.
Note on C20: 20 kA to 50 kA are typical withstand current ratings for PSC-assemblies for industrial use. Other standard ratings taken from the R10 numerical series of values that might be required are 10 kA, 12.5 kA, 16 kA and in special cases 63 kA, 80 kA and 100 kA.
Note on C21: Maximum duration for industrial installations does not normally exceed 1 s. Default value : 1
Note on C22: Data sheet set at the IEC 61439-1 default of 60 % of phase values. Unless otherwise agreed between the original manufacturer and the user, the value of the test current in the neutral and protective conductors should be at least 60 % of the line current. Default value : 60
Note on C24: No assumed loading factor value given for a section containing only one distribution circuit. in IEC 61439-2:2020, Table 101. Consequently a value of 1,0 is applied as there is no diversity with just one circuit in place which could be 100 % loaded. Default value : 1,0
Note on C25: Table 101 value of 0,9 is used as the default position, but may be adjusted higher or lower if required by the purchaser. Default value : 0.9
Note on C26: Table 101 value of 0,8 used as the default position, but may be adjusted higher or lower if required by the purchaser. Default value : 0.8
Note on C27: Table 101 value of 0,6 used as the default position, but may be adjusted higher or lower if required by the purchaser. If all circuits can be heavily loaded simultaneously, a higher factor might apply. Default value : 0.6
Note on C28: Table 101 value of 0,7 used as the default position, but may be adjusted higher or lower if required by the purchaser. If all circuits can be heavily loaded simultaneously, a higher factor might apply. Default value : 0.7
Note on C29: Table 101 default value of 0,2 used and not anticipated to require modification for MOV circuits. Default value : 0.2
Note on C30: Table 101 value of 0,8 used as the default position, but may be adjusted higher or lower if required by the purchaser. If all circuits can be heavily loaded simultaneously, such as banks of cooling fans in summer, a higher factor might apply. Default value : 0.8
Note on C31: Table 101 value of 1,0 used as the default position, but may be adjusted lower if required by the purchaser. Table 101 value of 1.0 recommended as >100 kW motors starters typically occupy a whole vertical panel. Default value : 1.0
Note on C33: Select as appropriate. IEC 61439-2:2020 Table AA.1 has three options DC/50 Hz/60 Hz. IOGP S-560 is written for AC system use but IEC 61439-2:2020 does also cover assemblies for use on DC photovoltaic systems. Default value : 50
Note on C35: If longitudinal channels flush with floor selected, indicate in the additional notes either "Floor channels provided by purchaser" or "Floor channels provided by supplier".
Note on C36: Select "required" and specify the detection details in "Additional notes" if required. Default value : not required
Note on C37: Select the status colour for the indicators and human machine interface (HMI) screens. Specify details of user-defined colours for indicators in "Additional notes". Default value : Table 19
Note on C39: Specify the language used for all information to be provided. Where the language is other than English, this can be confirmed in the "Additional notes" column. Default value : English
Note on C41: Specify whether a lifting device, typically a wheeled hoist to facilitate the removal of functional units and associated components with a mass greater than 25 kg is to be provided by the supplier Default value : not required
Note on C43: Specify the language in which the labels and notices shall be written. Where the language is other than English or if dual language labels are required, this can be confirmed in the "Additional notes". Default value : English
Note on C44: Specify whether a mimic one-line (synoptic) diagram is to be provided on the front of the PSC-assembly, displaying the single line arrangement of busbars and the main circuit switching devices. Default value : not required
Note on C46: Indoor climate controlled (HVAC or heating only) = default selection as this is the most common location type and the basis on which technical requirements in IOGP S-560 are written. For outdoor locations, select "other" and specify in “Additional notes”. Default value : indoor climate controlled
Note on C47: "Onshore" is the default selection as this is the most common operating environment. User (purchaser) to select alternate environment if required. Default value : onshore
Note on C48: Modify the data sheet default value only if the installation conditions (switchroom/outdoor) are colder than the IEC default. IEC 61439-1:2020, Table 15 default is -5 °C for indoor installations and -25 °C for outdoor installations. Default value : -5
Note on C49: Modify the data sheet default value only if the installation conditions are hotter than the IEC default. IEC 61439-1:2020, Table 15 default for indoor and outdoor installations is +40 °C. Default value : 40
Note on C50: Modify the data sheet default value only if the installation conditions are hotter than the IEC default. IEC 61439-1:2020, Table 15 default for indoor and outdoor installations is 35 °C. Default value : 35
Note on C51: Select the humidity limit as per Table 15. The IEC default for indoor installations is 95% at −5 °C to +30 °C, for outdoor installations is 100% at −25 °C to +27 °C. If "other" is selected, enter the humidity in the "Additional notes" column. Default value : 95 % at −5 °C to +30 °C
Note on C52: IEC 61439 (all parts) default is pollution degree 3 (industrial) which is more onerous than degree 1 or 2. Pollution degree 4 is not a data sheet selection as degree 4 is not applicable for a micro-environment inside the PSC-assembly. Default value : 3
Note on C53: Select a value other than the IEC 61439-1 default of 2 000 m only if the site elevation is higher than 2 000 m. Default value : ≤ 2 000
Note on C55: Where seismic certification in accordance with IEC 60068-3-3 is required, select the seismic activity zone as defined in IEC 60721-2-6 for the location where the drive is used. Where seismic certification is "not required", select "not applicable". Default value : not applicable
Note on C56: See IEC 61439-1:2020, Annex J.9.4.1. Environment A relates to a power network supplied from a high- or medium-voltage transformer dedicated to the supply of an installation feeding manufacturing or similar plant, operating in industrial locations. Default value : A
Note on C57: Where a floating or marine location is specified, select the maximum rotation about fore-and-aft axis of the vessel under dynamic conditions as defined in IEC 60092-101, e.g. ± 22° 30'. Default value : not applicable
Note on C58: Where a floating or marine location is specified, select the maximum rotation about athwartship axis of the vessel under dynamic conditions defined in IEC 60092-101, e.g. ± 7° 30'. Default value : not applicable
Note on C60: Table AA.1 default values –25 °C to + 55 °C and for periods not exceeding 24 h, up to +70 °C. If "special packing" or "other" is selected, use the "'Additional note" column or '"Supplement" tab for additional details. Default value: within IEC default conditions
Note on C61: Select the means of safely handling the switchgear shipping section without damage when an overhead lifting means is not available. The enclosure structure will be strengthened for rolling on floor without deformation of the enclosure base.
Note on C63: IEC 61439-1:2020 has no default IK position. IK07 minimum for indoor restricted access areas limited to authorized personnel only. Minimum of IK08 suggested for indoor unrestricted access areas or workshop, fabrication shops or similar areas. Default value : IK07
Note on C64: IP31/41 requires PSC-assemblies to be type tested (not self-declared) for vertically dripping water by the manufacturers. Manufacturers fitting a top cover or similar to give IPXXW drip protection is "suitable for use" but is not verified by an IEC test. Default value : IP3X
Note on C66: Select the type of protection against electric shock – basic protection (direct contact) in accordance with IEC 61439-1:2020, 8.4.2. Where additional measures are specified, provide the details in the "Additional notes" column. Default value : constructional (manufacturer's standard)
Note on C67: Select the type of protection against electric shock – fault protection (indirect contact) in accordance with IEC 61439-1:2020, 8.4.3. Where additional measures are specified, provide details in the "Additional notes" column. Default value : automatic disconnection of supply
Note on C68: IEC 61439-2:2020 3.1.101 defines that PSC-assemblies are for applications where operation by ordinary persons is not intended. An authorized person is a skilled person or an instructed person who is empowered to execute defined work. Default value : authorized persons
Note on C69: Specify the means of access control with regards to closed compartments covers and doors. Default value : manufacturer's standard locking facility
Note on C70: Select the means of locking facility with regards to safety shutters, disconnectors and switches.
Note on C71: Where padlockable facilities are specified, the purchaser may request that padlocks are provided by the manufacturer. Where padlockable facilities are not specified, select "not applicable".
Note on C73: Select the electrical connection method for functional units for outgoing circuits with rated currents up to and including 630 A. Outgoing circuits with rated current above 630 A should be provided with withdrawable air circuit breakers (ACBs). Default value : withdrawable
Note on C74: User's selection of the technical requirement "If specified", facilities for remote testing of withdrawable main circuit units should be provided by means of extension umbilicals or specific test modules.
Note on C76: Secondary selective substation incomers are normally fitted with withdrawable ACBs. An alternative is load-break fault-make switch-disconnectors with the low-voltage protection relays intertripping the high-voltage upstream breakers. Default value : withdrawable ACB
Note on C77: Secondary selective substation bus couplers are normally fitted with withdrawable ACBs. An alternative is load-break fault-make switch-disconnectors with the low-voltage protection relays intertripping the high-voltage upstream breakers. Default value : withdrawable ACB
Note on C78: Select the type of short circuit protection device to be applied across all lighting and small power feeders. IEC 60269-2 defines (national legacy) fuse systems A to K. A and B are (DIN) NH fuse-links, E is (BS88) fuse-links for bolted connections.
Note on C79: Select the type of short circuit protection device to be applied across all motor and contactor feeders. IEC 60269-2 defines (national legacy) fuse systems A to K. Notably, A and B are (DIN) NH fuse-links, E is (BS88) fuse-links for bolted connections.
Note on C81: Select the spring charging motor voltage of the air circuit breakers. Default value : manufacturer's standard
Note on C82: Select the air circuit breaker control voltage. with regards to tripping, closing, protection and indication of device. Default value : manufacturer's standard
Note on C83: Select the number of auxiliary contacts required for each air circuit breaker (NO-normally open, NC-normally closed). Default value : none
Note on C85: Select a value to suit user/project requirements. 230 V AC default assumes a phase-to-neutral supply available. For supplies other than phase-to-neutral derived, the control circuit voltage is via control power transformers. "Other" may be DC UPS supply. Default value : 230 V AC
Note on C86: Select a source configuration to suit user/project requirements (individual unit/common for each busbar). For control circuit voltage other than phase-to-neutral derived, the source is via control power transformers. “External supply” may be DC UPS power. Default value : internal within each functional unit
Note on C87: Select when a facility is to be provided for earth fault protection to be manually reset from the front of compartment (resettable without opening the functional unit).
Note on C88: Select whether space heaters in the motor are required. If "other" is selected, specify the motor sizes in kW that require space heating. Default value : not required
Note on C89: Select the motor heater supply voltage. Motor manufacturers typically offer two standard options for motors heaters, one rated for use on 100-120V AC supplies and heaters rated for use on 200-240 V AC supplies. See data sheet entry "supply voltage".
Note on C91: Select where a portable insulation fault locator is to be provided for PSC-assemblies with unearthed electrical supplies (IT).
Note on C93: Select the physical configuration as required for the installation space constraints.
Note on C95: For incomers, bus coupler and ACB equipped outgoing circuits, specify if the protection relays should have front of panel test blocks. If the site has an operational default, select "required - other" and define the type in the "Additional notes" column. Default value : not required
Note on C96: Accuracy class index: class 1,0 is 1% accuracy, class 0,5 is 0,5%, etc. The verification of accuracy may be performed using any of the meter test methods specified in IEC 62057-1.
Note on C98: The default is "required" but manufacturers may employ busbar barriers, insulation or encapsulation to reduce arc-fault risk, which for arcing class A, B and C is to be subjected to verification testing according to IEC TR 61641. Default value : required
Note on C99: The data sheet default presumes a 3-phase, 4-wire, solidly earthed neutral system (TN-S). Not required if N-PE links are at transformer/generator star points. Not applicable for 3-wire systems or for 4-wire resistance earthed and insulated earth systems. Default value : required
Note on C100: Select the internal wiring insulation type. Low smoke, zero halogen is typically required in offshore installations and in high occupancy buildings. Default value : manufacturer's standard
Note on C101: Table 20 requires alphanumeric/symbol identification of conductors. Conductor insulation typically black throughout. If colour also required, Purchaser to stipulate local/regional code colours in the supplement tab. Default value : not required
Note on C102: Select the choice of material to be used for busbar plating to protect the busbar material from corrosion. If "other", specify details of busbar insulation material in "Additional notes". Default value : manufacturer's standard
Note on C104: Select the incoming (supply) unit direction of external conductors in accordance with 8.8.
Note on C105: Select the incoming (supply) unit external conductor type in accordance with 8.8.
Note on C106: Specify the outgoing (load) unit direction of external conductors in accordance with 8.8.
Note on C107: A default of "cable" is assumed for the outgoing main circuits. Default value : cable
Note on C108: Select auxiliary the cable direction of external conductors in accordance with 8.8.
Note on C109: A default of "cable" is assumed for the outgoing auxiliary (control) circuits. Default value : cable
Note on C110: Select the external conductor material in accordance with 8.8. Default value : copper
Note on C111: Gland plates typically undrilled as gland sizes and entry points are often not finalized until well into construction. Cable transits often used on pre-fabricated switchrooms, on offshore modules or if a gas or water seal is required. Default value : undrilled removable gland-plate
Note on C112: Gland plates typically undrilled as gland sizes and entry points are often not finalized until well into construction. Cable transits often used on pre-fabricated switchrooms, on offshore modules or if a gas or water seal is required. Default value : undrilled removable gland-plate
Note on C113: Select when special glanding requirements such as insulation between the gland and the gland plate are required. Default value : none
Note on C115: See 8.8. Terminals for the connection of external auxiliary control cables should be provided with a minimum of 10 % spare unwired terminals. Modify default value if alternate spare terminal provision is required. Default value : 10 % spare
Note on C117: Internal separation should be a minimum of Form 4a for ACBs and a minimum of Form 3b for all other functional units. Purchaser's discretionary use of BS EN 61439-2 options for internal separation forms with "type" sub-forms included. Default value : Form 4a
Note on C118: Internal separation should be a minimum of Form 4a for ACBs and a minimum of Form 3b for all other functional units. Purchaser's discretionary use of BS EN 61439-2 options for internal separation forms with "type" sub-forms included. Default value : Form 3b
Note on C120: Select when an enclosure space heater is required in each section (vertical panel) of the PSC-assembly. Default value : not required
Note on C121: Select the supply voltage for which the heater should be rated. Where space heaters have not been specified, select "not applicable".
Note on C122: Not applicable when assembly enclosure space heaters are selected as not required. Select "permanently on", "thermostat" or "hygrostat "(humidity) control to suit the installation requirements. Default value : not applicable
Note on C123: Not applicable when enclosure space heaters not required. Supply side monitoring = local LED indication and remote supervision volt-free contact. Heater current monitoring =heater control unit with momentary push button and ammeter. Default value : not applicable
Note on C125: Select the amount of spare functional outgoing units to be provided for future usage. Default value : one of each type
Note on C126: Select the amount unequipped space provision for future functional units for outgoing circuits. Default value : 10 %
Note on C128: Select where an integrated thermal monitoring system is required. Technical details to be confirmed in the supplementary sheet or outside of this procurement data sheet. Default value : not required
Note on C129: Select where an integrated circuit breaker condition monitoring system is required. Technical details to be confirmed in the supplementary sheet or outside of this procurement data sheet. Default value : not required
Note on C130: Select where motor condition monitoring hardware is to be installed in motor starter functional units. Technical details to be confirmed in the "Supplementary" tab or outside of this procurement data sheet Default value : not required
Note on C132: Select "other" if the operating company or the site has a default IED brand for operational and/or system integration commonality at that location. If "other" is selected, specify the IED manufacturer/IED range in the "Additional notes" column. Default value : manufacturer's standard
Note on C133: Select the communication media within the PSC-assembly for interface to the process control system. If "multiple" or "other" is selected, provide details in the "Additional notes" column and in the project drawings. Default value : manufacturer's standard
Note on C134: Select the communication protocol within the PSC-assembly for the stated media interface to the process control system. If "multiple" or "other" is selected, provide details in the "Additional note" column and in the project drawing.
Note on C135: PRP or HSR (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. Select "other" to specify other redundancy protocols.
Note on C136: If required, select the communication media within the PSC-assembly for interface to the electrical control and management system. Where "other" media is specified provide details in the "Additional notes" column Default value : not required
Note on C137: If required, select the communication protocol within the PSC-assembly for the stated media interface to the electrical control and management system. Where "other" protocol is specified, provide details in the "Additional notes" column. Default value : not required
Note on C138: PRP or HSR (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. Select "other" to specify other redundancy protocols. Default value : not applicable
Note on C139: Not applicable if ECMS is not specified. Where required, this is an optional facility provided by the electrical control system / power management system to remotely edit an IEDs protection and logic settings by a user with the correct system privileges. Default value : not applicable
Note on C141: For PSC-assemblies in the same substation building, a default of "hardwired discrete" is presumed from the PSC-assembly to upstream or downstream switchboards, but may be IED-to-IED communication or via the ECMS station bus. Default value : hardwired discrete
Note on C142: A default of "hardwired" is presumed for discrete hardwired interlocking / intertripping from the PSC-assembly to upstream or downstream switchboards, but may be IED-to-IED communication or via the ECMS station bus. Default value : hardwired
Note on C144: If required, select the communication media within the PSC-assembly for interface to the load shedding and/or sequenced restart system. Where "other" media is specified, provide details in the "Additional notes" column. Default value : not required
Note on C145: If required, select the communication protocol from IEDs via the stated media interface to the power management system. Where "other" protocol is specified, provide details in the "Additional notes" column. Default value : not required
Note on C146: PRP or HSR (IEC 62439-3) provides seamless failover against failure of a network component for most industrial ethernet protocols. Select "other" to specify other redundancy protocols. Default value : not applicable
Note on C148: If required, select the communication media within the PSC-assembly for interface to the generator control panel. Where "other" media is specified, provide details in the "Additional notes" column. Default value : not required
Note on C149: If required, specify the communication protocol from IEDs via the stated media interface to the generator control panel. Where "other" protocol is specified, provide details in the "Additional notes" column. Default value : not required
Note on C151: Select where certification confirming compliance with IEC 62443-4-2 for automation and control system components is required. Default value : not required
Note on C153: In accordance with IEC TR 61641:2014, 4.1, select the arcing class (A, B or C) to provide personnel protection by arc tested zones. Arcing class I only provides a reduced risk of arcing faults solely by means of arc ignition protected zones. Default value : arcing class A
Note on C154: To be specified by the manufacturer if the arc duration is limited by a non current-limiting device (inside or upstream of the assembly) and/or an arc mitigation device that does not limit the arc current.
Note on C155: See IEC TR 61641:2014, 8.5. Normally, the duration of test will be between 0,1 s and 0,5 s. When high voltage protection equipment is relied upon to isolate a fault, the permissible arc duration of the incoming switching device in general will be 0,3 s. Default value : 0,3
Note on C156: Select when an integrated internal arc-fault mitigation systems (IAMS) in accordance with IEC TS 63107 is required. Default value : not required
Note on C157: Select either the method of activation of the maintenance mode function or “not required”. If “other” is selected, specify the activation method type in “Additional notes”. The method defines how the activation of maintenance mode is visually indicated. Default value : not required
Note on C159: Not applicable when there is not an electrical control and management system (ECMS) specified. Purchaser to define the extent of simulation testing required to validate the ECMS interfaces between the remote HMI and IEDs on the PSC-assembly. Default value : not applicable

## Supplement
Row |  | IOGP S-560D (3.01) Procurement Data Sheet for Low-voltage Switchgear and Controlgear (IEC) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-560D (3.01) Procurement Data Sheet for
Low-voltage Switchgear and Controlgear (IEC)
Guidance on the use of this procurement data sheet
To be used in conjunction with :
IOGP S-560 Supplementary Specification to IEC 61439-1 and IEC 61439-2 for Low-voltage Switchgear and Controlgear.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data