## Addendum 1
Date of issue:
October 2025
Affected publication:
IOGP S-701D, Procurement Data Sheet for DC Uninterruptible Power Systems (UPS) (IEC 62040-3), Second Edition, January 2024
ADDENDUM 1
This addendum (Version 2.01) replaces Edition 2.0 published in January 2024.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Row | Column | Update
| 29 | Description | Embedded guidance note amended
| 37 | All | New data sheet item "Main protective earthing arrangement"
| 38 | All | New data sheet item "Conformal printed circuit board coating"
| 52 | All | New data sheet item "Internal lighting required"
| 53 | All | New data sheet item "Anti-condensation heaters required"
| 54 | All | New data sheet item "UPS enclosure access type - front side"
| 55 | All | New data sheet item "UPS enclosure access type - rear side"
| 56 | All | New data sheet item "Busbar material"
| 59 | Description | Embedded guidance note amended
| 68 | All | New data sheet item "Thermal monitoring of internal connections and terminations required"
| 86 | Purchaser requirement / Supplier offered value | Default value "Modbus TCP/IP" added
|  | Purchaser requirement / Supplier offered value - options | Option "RS485" deleted
| 91 | Purchaser requirement / Supplier offered value - options | Second list option amended to "potential free contacts"
| 113 | All | New data sheet item "Overvoltage category as per IEC 60364-4-44"
| 117 | All | New data sheet item "Restored energy time (recharge time to 80 % capacity)"
| 131 | Description | Embedded guidance note amended
| 177 | Purchaser requirement / Supplier offered value | Default value "separate adjacent compartment" added
|  | Purchaser requirement / Supplier offered value - options | Second list option amended to "remote compartment"
| 178 through 180 | All | New section "Inspection and testing" including new data sheet items "Additional testing required" and "Routine full load test duration"
| Various | Row | Numbering updated as per new and deleted rows

## Front & Preliminaries
[5 empty] | SPECIFICATION | October 2025
[5 empty] | IOGP S-701D | Version 2.01
ADDENDUM 1 TO SECOND EDITION (JANUARY 2024)
Procurement Data Sheet for
AC Uninterruptible Power Systems
(UPS) (IEC)
Revision history
| VERSION | DATE | PURPOSE
| 2.01 | October 2025 | Addendum 1
| 2 | January 2024 | Second Edition
| 1 | August 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-701D (2.01) Procurement Data Sheet for
AC Uninterruptible Power Systems (UPS) (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
This second edition cancels and replaces the first edition published in August 2020.
Due to technical writing requirements leading to extensive changes, this second edition should be treated as a new document.
IOGP S-701D (2.01) Procurement Data Sheet for
AC Uninterruptible Power Systems (UPS) (IEC)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of AC uninterruptible power systems (UPSs) in accordance with IOGP S-701 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-701), information requirements specification (IOGP S-701L) and quality requirements specification (IOGP S-701Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)

## Procurement Data Sheet
Row | IOGP S-701D (2.01) Procurement Data Sheet for AC Uninterruptible Power Systems (UPS) (IEC) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 | 1 paragraph 2 sentence 1 | Project country : | input data |  | input data
7 | 1 paragraph 2 sentence 1 | Project region : | input data |  | input data
8 | D.5,5.1.2 | Supplier : | input data |  | input data
9 | 5.1.2 | Purchase order reference and date : | input data |  | input data
10 | 5.1.2,D.5 | Model number : | input data |  | input data
11 | 5.2.3 | Application : | industrial |  | industrial | [5 empty] | select | industrial | other
12 | 5.3.3 | Purchaser-specified rated output power (apparent) : | input data | kVA | input data | kVA
13 | 5.1.1 | Quantity : | input data |  | input data
14 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
15 |  | Configuration
16 | K.3,Table K.1 | Reliability integrity level (RIL) : | 1 |  | 1 | [5 empty] | select | 1 | 2 | other
17 | 5.1.1,A.1,Figure A.1,Figure A.2,Figure A.3 a,Figure A.3 b,Figure A.4,Figure A.5,Figure A.6,Figure A.7 | AC UPS configuration : | select |  | select | [5 empty] | select | simplified single AC UPS with bypass - Figure A.2 | simplified parallel AC UPS with common bypass and common output - Figure A.3 a) | simplified parallel AC UPS with common bypass and separate output - Figure A.3 b) | simplified dual bus AC UPS with bypass - Figure A.6 | other
18 | 5.1.1,B.1,Figure B.1,Figure B.2,Figure B.3 | AC UPS topology : | double conversion |  | double conversion | [5 empty] | select | double conversion | other
19 | 5.1.1,C.1,C.2 | Static switch configuration : | in bypass path only |  | in bypass path only | [5 empty] | select | in bypass path only | in both inverter and bypass paths
20 | 5.4.2.3 | Battery configuration : | 1 x 100 % |  | 1 x 100 % | [5 empty] | select | 1 x 100 % | 2 x 100 % | other
21 | 5.3.2,5.3.4.1,5.3.4.2.2,5.3.4.2.3,5.3.4.2.4,5.3.4.3.4,5.3.4.4.1,6.4.1.2,6.4.1.3,6.4.2.10.1,6.4.2.10.2,6.4.2.10.3,6.4.2.10.4,6.4.2.10.5,6.4.2.10.6 | Performance classification : | VFI SS 11 |  | VFI SS 11 | [5 empty] | select | VFI SS 11 | VFD | VI | manufacturer to advise
22 | 8.1.1.2 | Bi-directional rectifier : | no |  | no | [5 empty] | select | yes | no
23 | 8.1.1.3 | On-line battery monitoring facility required : | no |  | no | [5 empty] | select | no | string monitoring | cell monitoring
24 | 8.1.2.10 | Temperature compensated battery charging facility : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | yes | no
25 | 8.1.2.10 | Hazardous area classification for temperature sensor : | not applicable |  | not applicable | [5 empty] | select | not applicable | Zone 1 | Zone 2
26 | 5.4.2.3 | On-line battery capacity testing by discharging battery into load : | not required |  | not required | [5 empty] | select | not required | automatic | manual
27 | 5.4.2.3 | Battery test load interface : | no |  | no | [5 empty] | select | yes | no
28 | 5.4.2.2,5.4.2.3 | Battery earth condition/isolation : | select |  | select | [5 empty] | select | floating | positive earthed | negative earthed
29 | 5.4.2.3 | DC earth leakage monitoring required : | no |  | no | [5 empty] | select | yes | no
30 |  | AC UPS cooling system design : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | convection | fan assisted forced air
31 | 7.7.4 | Cooling fan replacement while AC UPS in service : | no |  | no | [5 empty] | select | yes | no
32 | 8.4.1.2,8.4.1.4,8.4.1.5 | Single line diagram and status display : | on HMI |  | on HMI | [5 empty] | select | on HMI | on mimic at front panel | on both HMI and mimic at front panel
33 | 8.1.2.11 | Black start feature required : | no |  | no | [5 empty] | select | yes | no
34 | 8.1.2.11 | ESD override feature required : | no |  | no | [5 empty] | select | yes | no
35 |  | Potential free contacts for common alarm wired to terminal block : | 1NO+1NC |  | 1NO+1NC | [5 empty] | select | 1NO+1NC | 2NO+2NC | other
36 |  | Earth screen required for isolation transformer : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | yes | no
37 | 7.6.1 | Main protective earthing arrangement : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | copper bar | conductor | terminal
38 |  | Conformal printed circuit board coating : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | yes
39 |  | Physical aspects
40 | 7.2.1 | AC UPS mounting : | floor mounting |  | floor mounting | [5 empty] | select | floor mounting | wall mounting
41 | D.5,7.2.1 | Overall cabinet dimensions - length : | input data | mm | input data | mm
42 | D.5,7.2.1 | Overall cabinet dimensions - depth : | input data | mm | input data | mm
43 | D.5,7.2.1 | Overall cabinet dimensions - height : | input data | mm | input data | mm
44 | D.5,7.2.1 | Total AC UPS cabinet mass : | input data | kg | input data | kg
45 | D.5,7.2.1 | Total AC UPS mass with batteries (if integrated) : | input data | kg | input data | kg
46 |  | Insulation material of internal wiring : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | low smoke zero halogen (LSZH)
47 |  | Cable entry location : | select |  | select | [5 empty] | select | bottom | top | both bottom and top
48 | 7.2.3,7.2.4 | Cable entry type : | removable - undrilled plate |  | removable - undrilled plate | [5 empty] | select | removable - undrilled plate | multi-cable transit (MCT)
49 | 7.2.3,7.2.4 | Gland plate material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | non-magnetic plate
50 |  | Paint colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
51 |  | Document holder required : | no |  | no | [5 empty] | select | yes | no
52 |  | Internal lighting required : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | yes
53 | 7.4.11 | Anti-condensation heaters required : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | yes
54 |  | UPS enclosure access type - front side : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | hinged doors
55 |  | UPS enclosure access type - rear side : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | hinged doors
56 |  | Busbar material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | electrolytic copper
57 |  | Installation
58 | 4.1 | Site : | select |  | select | [5 empty] | select | onshore | offshore - fixed | offshore - floating | marine (ship) | other
59 | 4.1 | Location of AC UPS cabinet installation : | indoor |  | indoor | [5 empty] | select | indoor | outdoor
60 | D.5,7.3.1 | Front access clearance dimensions for operation and maintenance : | input data | mm | input data | mm
61 | D.5,7.3.1 | Side clearance for access/ventilation (if required) : | input data | mm | input data | mm
62 | D.5,7.3.1 | Rear clearance for access/ventilation (if required) : | input data | mm | input data | mm
63 | 5.4.2.1 | Installation location of battery : | select |  | select | [5 empty] | select | battery room | inside UPS room | inside UPS enclosure | separate indoor battery cabinet | outdoor (battery enclosure) | outdoor (hazardous area battery enclosure)
64 |  | Safety
65 | 7.3.1 | Key required for cabinet : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | yes | no
66 | 7.2.2 | Degree of protection (with closed doors) : | IP31 |  | IP31 | [5 empty] | select | IP31 | manufacturer's standard | other
67 | 5.1.2 | Additional language for caution/danger/warning labels : | input data |  | input data
68 |  | Thermal monitoring of internal connections and terminations required : | no |  | no | [5 empty] | select | yes | no
69 |  | Electromagnetic compatibility
70 | 5.1.3 | Emission : | Category C3 UPS |  | Category C3 UPS | [5 empty] | select | Category C3 UPS | Category C2 UPS | Category C1 UPS | Category C4 UPS
71 | 5.1.3 | Immunity : | Category C3 UPS |  | Category C3 UPS | [5 empty] | select | Category C3 UPS | Category C2 UPS | Category C1 UPS | Category C4 UPS
72 |  | Environmental conditions
73 | 4.2.2.1 | Minimum ambient temperature - operation : | 0 | °C | 0 | °C |  |  |  |  | select | 0 | other
74 | 4.2.2.1 | Maximum ambient temperature - operation : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | other
75 | 4.2.2.1 | Maximum non-condensing relative humidity - operation : | 80 | % | 80 | % |  |  |  |  | select | 80 | other
76 | 4.2.2.2 | Maximum altitude - operation : | up to and including 1 000 | m | up to and including 1 000 | m |  |  |  |  | select | up to and including 1 000 | other
77 | 4.2.3,9 | Minimum ambient temperature - storage and transportation : | -25 | °C | -25 | °C |  |  |  |  | select | -25 | other
78 | 4.2.3,9 | Maximum ambient temperature - storage and transportation : | 55 | °C | 55 | °C |  |  |  |  | select | 55 | other
79 | 4.2.3,9 | Maximum non-condensing relative humidity - storage and transportation : | 95 | % | 95 | % |  |  |  |  | select | 95 | other
80 | 4.3.2 | Seismic activity zone in accordance with IEC 60721-2-6 : | select |  | select | [5 empty] | select | Zone 1 | Zone 2 | Zone 3 | Zone 4 | not applicable
81 | 4.2.3 | Storage site of AC UPS : | select |  | select | [5 empty] | select | indoor - climate controlled (humidity and temperature) | indoor - temperature controlled only | indoor - natural ventilation | outdoor | other
82 |  | Transport and storage environmental conditions : | select |  | select | [5 empty] | select | within defined site service conditions | outside defined site service conditions
83 | 5.1.4,6.5.4 | Acoustic noise at 1,00 m - normal mode : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
84 |  | Communication interfaces
85 | 5.6,Figure 6 | Interface media for ECMS : | Ethernet (Cu) |  | Ethernet (Cu) | [5 empty] | select | not required | hardwired discrete | serial | Ethernet (Cu) | Ethernet (fiber) | wireless | other
86 | 5.6,Figure 6 | Interface protocol for ECMS : | Modbus TCP/IP |  | Modbus TCP/IP | [5 empty] | select | not applicable | potential free contact | Modbus TCP/IP | Profinet | Ethernet IP | other
87 | 5.6,Figure 6 | Interface network redundancy for ECMS : | select |  | select | [5 empty] | select | not required | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
88 | 8.4.1.9,Figure 6 | AC UPS remote access (via interface for ECMS) : | no |  | no | [5 empty] | select | no | yes - read only | yes - read/write
89 | 8.4.1.9 | Hardware required for remote access : | no |  | no | [5 empty] | select | yes | no
90 | 5.6,Figure 6 | Interface media for PCS : | not required |  | not required | [5 empty] | select | not required | hardwired discrete | other
91 | 5.6,Figure 6 | Interface protocol for PCS : | not applicable |  | not applicable | [5 empty] | select | not applicable | potential free contacts | other
92 | 5.6,Figure 6 | Interface media for SIS/ESD and FGS to AC UPS : | not required |  | not required | [5 empty] | select | not required | hardwired discrete
93 | 5.6,Figure 6 | Interface media for SIS/ESD and FGS to battery isolator : | not required |  | not required | [5 empty] | select | not required | hardwired discrete
94 |  | AC input specifications
95 | 5.2.1,5.2.2,6.4.1.1,6.4.1.2,6.4.1.3 | Voltage (steady state, R.M.S) - rated : | select | V | select | V |  |  |  |  | select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | other
96 | 5.2.1,5.2.2,6.4.1.1,6.4.1.2,6.4.1.3 | Voltage (steady state, R.M.S) - tolerance : | ±10 | % | ±10 | % |  |  |  |  | select | ±10 | other
97 | 5.2.1,5.2.2,6.4.1.1,6.4.1.3 | Frequency - rated : | 50 | Hz | 50 | Hz |  |  |  |  | select | 50 | 60
98 | 5.2.1,5.2.2,6.4.1.1,6.4.1.3 | Frequency - tolerance : | ±2 | % | ±2 | % |  |  |  |  | select | ±2 | other
99 | 5.2.2 | Phases required : | 3 |  | 3 | [5 empty] | select | 1 | 3
100 | 5.2.2 | Neutral required : | no |  | no | [5 empty] | select | yes | no
101 | D.5,5.2.2,6.4.1.4 | Rated input current (R.M.S) with energy storage device charged : | input data | A | input data | A
102 | D.5,5.2.2,6.4.1.5 | Maximum input current (with minimum input volt and energy storage device charging) : | input data | A | input data | A
103 | D.5,5.2.2,6.4.1.6 | In-rush (% of rated current) : | input data | % | input data | %
104 | D.5,5.2.2,6.4.1.6 | in-rush (time) : | input data | s | input data | s
105 | 5.2.1,D.5,5.2.2,6.4.1.1,6.4.1.7 | Total harmonic distortion of current (THD p.u.) : | input data | % | input data | %
106 | 5.2.2 | Short circuit current of the input supply (minimum and maximum) : | input data | kA | input data | kA
107 | 5.2.2,6.4.1.1 | AC power distribution system compatibility : | select |  | select | [5 empty] | select | TT | TN-C | TN-C-S | IT | TN-S | other
108 | 5.2.3,7.5.3 | Cable size (cross-section area) - input mains : | input data | mm² | input data | mm²
109 | 5.2.3,7.5.3 | Cable size (cross-section area) - input bypass : | input data | mm² | input data | mm²
110 | 5.2.3,7.5.3 | Cable size (cross-section area) - input maintenance bypass : | input data | mm² | input data | mm²
111 | 7.4.10,7.4.9 | Input isolation transformer required : | select |  | select | [5 empty] | select | yes | no
112 |  | Input isolation transformer winding : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | copper | aluminium
113 |  | Overvoltage category as per IEC 60364-4-44 : | select |  | select | [5 empty] | select | I | II | III | IV
114 |  | Battery and battery room specifications
115 | 7.1.5 | Energy storage device (battery) requirements : | IOGP S-740 |  | IOGP S-740 | [5 empty] | select | IOGP S-740 | not applicable | other
116 | 7.1.5 | Battery room requirements : | IOGP S-740 |  | IOGP S-740 | [5 empty] | select | IOGP S-740 | not applicable | other
117 | 8.1.2.3 | Restored energy time (recharge time to 80 % capacity) : | input data | hours | input data | hours
118 |  | External battery isolator box specifications
119 | 5.4.2.3,7.9.1,7.9.2,7.9.3,7.9.4,7.9.5,7.9.6 | External battery isolation box required : | select |  | select | [5 empty] | select | yes | no
120 |  | Enclosure material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
121 |  | Mounting : | on wall |  | on wall | [5 empty] | select | on wall | on structural steel pedestal | on stainless steel frame
122 |  | Internal earth bar : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | copper | tinned copper | manufacturer's standard
123 | 4.2.2.1 | Minimum design temperature : | 0 | °C | 0 | °C |  |  |  |  | select | 0 | other
124 | 4.2.2.1 | Maximum design temperature : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | other
125 | 4.2.2.1 | Maximum relative humidity : | 80 | % | 80 | % |  |  |  |  | select | 80 | other
126 | 7.9.2 | Degree of protection : | IP31 |  | IP31 | [5 empty] | select | IP31 | manufacturer's standard | other
127 |  | Area classification : | non-hazardous |  | non-hazardous | [5 empty] | select | non-hazardous | hazardous
128 |  | Hazardous area certification required : | none |  | none | [5 empty] | select | none | ATEX | IECEx | EAC | other
129 |  | Hazardous area classification : | not applicable |  | not applicable | [5 empty] | select | not applicable | Zone 1 | Zone 2
130 |  | Primary hazardous area level of protection : | not applicable |  | not applicable | [5 empty] | select | not applicable | Ex-db IIB T3 Gb | Ex-db IIB+H2 T3 Gb | Ex-db IIC T3 Gb | Ex-db IIB T4 Gb | Ex-db IIC T4 Gb | Ex-db IIB T6 Gb | Ex-db IIC T6 Gb
131 | 7.9.3 | Cable indirect entry via "ex e" enclosure : | no |  | no | [5 empty] | select | yes | no
132 |  | Cable entry : | select |  | select | [5 empty] | select | bottom | top | bottom and side | top and side | all sides
133 | 5.4.2.2 | Cable volt drop recommendation (≤ % at nominal discharge current) : | input data | % | input data | %
134 | 7.5.3,7.9.3 | Battery cable size (cross-section area) : | input data | mm² | input data | mm²
135 | 7.9.3 | Cable entry diameter in battery isolator box (ISO metric) : | input data | mm | input data | mm
136 | 5.4.2.2 | Battery isolator type : | MCCB |  | MCCB | [5 empty] | select | MCCB | switch fuse unit
137 | 5.4.2.2,7.9.4 | Rated current of breaker / switch fuse unit : | input data | A | input data | A
138 | 5.4.2.2,7.9.4 | Rated breaking current (Icu) - if breaker used : | input data | kA | input data | kA
139 | 7.9.6 | Breaker status potential free contact (NO) : | none |  | none | [5 empty] | select | none | 1 | 2
140 | 7.9.5 | Under-voltage trip required : | no |  | no | [5 empty] | select | yes | no
141 | 7.9.5 | ESD trip required : | no |  | no | [5 empty] | select | yes - via under-voltage trip | yes - via shunt trip | no
142 | 8.1.2.11 | ESD override key switch : | not required |  | not required | [5 empty] | select | not required | yes - key captive in overridden position and with status contact
143 | 7.9.5 | Over-voltage trip required : | no |  | no | [5 empty] | select | yes | no
144 |  | AC output specifications
145 | D.5,5.3.2,6.4.2.6 | Rated output power - apparent : | input data | kVA | input data | kVA
146 | D.5,5.3.2,6.4.2.6 | Rated output power - active : | input data | kW | input data | kW
147 | 5.3.2 | AC power distribution system - compatibility : | select |  | select | [5 empty] | select | TT | TN-C | TN-C-S | IT | TN-S | other
148 | 5.3.2 | Phases available : | 1 |  | 1 | [5 empty] | select | 1 | 3
149 | 5.3.2 | Neutral available : | yes |  | yes | [5 empty] | select | yes | no
150 | 5.3.2,5.3.4.2.3,5.3.4.4.2,5.3.4.4.3,5.3.4.4.4,6.4.2.10.2,6.4.2.10.3,6.4.2.10.4,6.4.2.10.5,6.4.2.10.6,6.4.2.2,6.4.2.3,6.4.2.5,6.4.2.7,6.4.2.8,6.4.2.9.1,8.2.2 | Voltage (steady state, R.M.S) - rated : | input data | V | input data | V
151 | 5.3.2,5.3.4.2.3,5.3.4.4.2,5.3.4.4.3,5.3.4.4.4,6.4.2.10.1,6.4.2.10.2,6.4.2.10.3,6.4.2.10.4,6.4.2.10.5,6.4.2.10.6,6.4.2.2,6.4.2.7,6.4.2.8,6.4.2.9.1,8.2.2,8.2.6 | Voltage variation - static : | ±1 | % | ±1 | % |  |  |  |  | select | ±1 | other
152 | 5.3.2,5.3.4.1,6.4.2.10.1,6.4.2.3,6.4.2.7,8.2.6 | Voltage variation - dynamic : | ±5 | % | ±5 | % |  |  |  |  | select | ±5 | other
153 | 5.3.2,6.4.2.2,6.4.2.3,8.2.3 | Total harmonic distortion (V), 100 % load - linear : | 4 | % | 4 | % |  |  |  |  | select | 4 | other
154 | 5.3.2,6.4.2.2,6.4.2.3,8.2.3 | Total harmonic distortion (V), 100 % load - non-linear : | 5 | % | 5 | % |  |  |  |  | select | 5 | other
155 | 5.3.2 | Frequency (steady state) - rated : | 50 | Hz | 50 | Hz |  |  |  |  | select | 50 | 60
156 | 5.3.2,8.2.4,8.2.5,8.2.6 | Frequency (steady state) - free running variation : | ±0,1 | % | ±0,1 | % |  |  |  |  | select | ±0,1 | other
157 | D.5,5.3.2 | Current (R.M.S) - rated : | input data | A | input data | A
158 | 5.1.6.1,D.5,5.3.2 | Current (R.M.S) - overload capability (% of rated current for 10 min) : | input data | % | input data | %
159 | 5.1.6.2,D.5,5.3.2 | Current (R.M.S) - overload capability (% of rated current for 1 min) : | input data | % | input data | %
160 | 5.1.6.3,D.5 | Current (R.M.S) - short circuit capability (% of rated current) : | input data | % | input data | %
161 | 5.1.6.3,D.5 | Current (R.M.S) - short circuit capability (time duration) : | input data | ms | input data | ms
162 | D.5,5.3.2,6.4.2.1 | Load power factor - rated : | 0,8 (lag) |  | 0,8 (lag) | [5 empty] | select | 0,8 (lag) | other
163 | D.5,5.2.2,5.3.2,6.4.1.9,I.3,Table I.2 | Minimum weighted AC UPS efficiency : | input data | % | input data | %
164 | 7.4.10,7.4.9 | Output isolation transformer required : | select |  | select | [5 empty] | select | yes | no
165 |  | Output isolation transformer winding : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | copper | aluminium
166 | 5.3.3,7.6.4 | AC output neutral earth link : | select |  | select | [5 empty] | select | earthed | floating
167 | 5.3.3,7.5.3 | Cable size (cross-section area) - output : | input data | mm² | input data | mm²
168 |  | AC distribution board specifications
169 |  | AC distribution board required : | select |  | select | [5 empty] | select | yes | no
170 | 5.3.3 | Reference document to AC output distribution board : | input data |  | input data
171 |  | Bypass specifications
172 | D.5,C.1,C.2 | Bypass transfer time : | input data | ms | input data | ms
173 | D.5,8.3.1,C.1,C.2 | Bypass static switch rated current : | input data | A | input data | A
174 | D.5,8.3.1,8.3.4,C.1,C.2 | Bypass protection fuse or circuit breaker rating : | input data | A | input data | A
175 | 7.4.10,7.4.9 | Bypass transformer required : | select |  | select | [5 empty] | select | yes | no
176 |  | Bypass transformer winding : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | copper | aluminium
177 | 7.3.3,7.3.5 | Maintenance bypass switch and bypass transformer location : | separate adjacent compartment |  | separate adjacent compartment | [5 empty] | select | separate adjacent compartment | remote compartment
178 |  | Inspection and testing
179 |  | Additional testing required : | no |  | no | [5 empty] | select | yes (see "Supplement" sheet) | no
180 | 6.2.2.5 | Routine full load test duration : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
Note on C4: Specify the unique tag number of the equipment to be supplied.
Note on C5: Specify the functional description of the equipment to be supplied.
Note on C6: Specify the country in which the project is located, in accordance with ISO 3166-1 for the final installation of the AC UPS to enable the supplier to provide the required product marking and certification for the region.
Note on C7: Specify the geographic location of the project within the country which determines the applicability of local regulatory requirements.
Note on C8: Specify the name of the supplier.
Note on C9: Specify purchase order reference and date.
Note on C10: Specify the product series, range or model number.
Note on C11: Select the intended application of the UPS. If "other" is selected, specify in the "Additional notes" column (e.g. information technology). Default value : industrial
Note on C12: Specify the rated output power (apparent) requirement in kVA.
Note on C13: Specify the quantity of AC UPSs required and align with the UPS configuration specified in row 17 "AC UPS configuration".
Note on C14: Select the CAS level as applied in IOGP S-701Q, Annex A. Default value : D
Note on C16: Select the required target level of reliability integrity based on the intended AC UPS application. If "other" is selected, specify in the "Additional notes" column. Default value : 1
Note on C17: Select the required UPS configuration. If "other" is selected, specify in the "Additional notes". Each AC UPS configuration has to be considered as a single equipment, e.g. "simplified - Figure A.3b)" is one equipment and specify the quantity accordingly.
Note on C18: Select the required AC UPS topology. If "other" is selected, specify in the "Additional notes" column. Default value : double conversion
Note on C19: Select the required static switch configuration. Default value : in bypass path only
Note on C20: Select the required battery configuration. If "other" is selected, specify in the "Additional notes" column. Default value : 1 x 100 %
Note on C21: Select the required performance classification based on the intended AC UPS application. Default value : VFI SS 11
Note on C22: Select "yes" if the battery is to be discharged and fed back into the source supply using a bi-directional rectifier. Default value : no
Note on C23: Select "string monitoring" or cell "monitoring" if an on-line monitoring system is required for the battery. Default value : no
Note on C24: Select "yes" if the rectifier unit is to have provision for accepting temperature compensation input to control the battery charging voltage with an accuracy of ±1 %. Default value : manufacturer's standard
Note on C25: Check the battery room specifications for applicable hazardous area classification and specify accordingly. Default value : not applicable
Note on C26: Select this feature if on-line testing is required for allowing the battery to supply load for a specified time by blocking the rectifier. If "automatic" is selected, check whether automatic battery testing is applicable for the selected battery type. Default value : not required
Note on C27: Select this feature if an interface is required to connect a load bank for battery testing. Default value : no
Note on C28: Select the provision of isolation of the DC link from the input side and/or output side.
Note on C29: Select this feature if earth leakage monitoring is required for the battery. If "yes" is selected, specify the earth leakage monitoring sensitivity in the "Additional notes" column. Default value : no
Note on C30: Select the required cooling system design for the AC UPS. Default value : manufacturer's standard
Note on C31: Select whether the cooling fan replacement while the AC UPS is in service is required. Default value : no
Note on C32: Select the required option for the single line diagram and status display. Default value : on HMI
Note on C33: Select whether a black start feature (delivering power to load with only batteries connected, no mains supply) is required. Default value : no
Note on C34: Select "yes" if "yes" has been selected in row 33 "Black start feature required". Default value : no
Note on C35: Select the required number of wired breaker status potential free contacts for the common alarm. If "other" is selected, specify in the "Additional notes" column. Default value : 1NO+1NC
Note on C36: Select the isolation transformer earth screen requirement. Default value : manufacturer's standard
Note on C37: Select the main protective earthing arrangement. Default value : manufacturer's standard
Note on C38: Select whether conformal PCB coating is required PCBs from the effects of tropical or offshore area installation, such as moisture, salt spray, chemicals and temperature extremes to prevent such corrosion, mould growth and electrical failures. Default value : manufacturer's standard
Note on C40: Select the required AC UPS mounting option. Default value : floor mounting
Note on C41: Specify the overall cabinet length in mm.
Note on C42: Specify the overall cabinet depth in mm.
Note on C43: Specify the overall cabinet height in mm.
Note on C44: Specify the overall cabinet mass (excluding batteries) in kg.
Note on C45: Specify the overall cabinet mass including batteries (if batteries are integral to the cabinet) in kg.
Note on C46: Select the required insulation material of the AC UPS internal wiring. Default value : manufacturer's standard
Note on C47: Select the required cable entry location based on the installation planned.
Note on C48: Select the required type of cable entry (gland plate or MCT). Default value : removable - undrilled plate
Note on C49: Select the required gland plate material based on the selected power cable type (single core or multi core). "Non-magnetic plate" should be selected for single core cable termination. Default value : manufacturer's standard
Note on C50: Select the required option for the cabinet external paint shade. If "other" is selected, specify the required shade in the "Additional notes" column. Default value : manufacturer's standard
Note on C51: Select whether a document holder inside the cabinet is required or not. Default value : no
Note on C52: Select whether internal lighting in the AC UPS enclosure is required. Default value : manufacturer's standard
Note on C53: Select whether thermostatically controlled anti-condensation heaters are required for each column. Default value : manufacturer's standard
Note on C54: Select whether hinged doors for front access to the UPS enclosure are required. Default value : manufacturer's standard
Note on C55: Select whether hinged doors for rear access to the UPS enclosure are required. Default value : manufacturer's standard
Note on C56: Select the material of construction for the busbar. Default value : manufacturer's standard
Note on C58: Select the location of the facility where the equipment will be permanently installed.
Note on C59: Select the location where the equipment will be permanently installed. If "outdoor" is selected, specify additional requirements in the "Supplement" sheet. Default value : indoor
Note on C60: Specify the required front access clearance in mm.
Note on C61: Specify the dimension in mm when side clearance is required for access or ventilation.
Note on C62: Specify the dimension in mm when rear clearance is required for access or ventilation.
Note on C63: Select the location of installation for the battery.
Note on C65: Select the required option for cabinet access using a key. Default value : manufacturer's standard
Note on C66: Select the required degree of protection based on the installation location with the enclosure doors closed. IP31 is still the minimum requirement even if "manufacturer's standard" option is selected. If "other" is selected, specify in "Additional notes". Default value : IP31
Note on C67: Specify whether a local/native language is to be used in addition to English for caution/danger/warning information on equipment labels.
Note on C68: Specify whether an integrated thermal monitoring system is required. This may require additional hardware, software control wiring or network cabling to be installed. Specify details of the system in the 'Additional notes' column. Default value : no
Note on C70: Select the category applicable for EMC emission. Default value : Category C3 UPS
Note on C71: Select the category applicable for EMC immunity. Default value : Category C3 UPS
Note on C73: Select the minimum ambient temperature expected during operation. If "other" is selected, specify in the "Additional notes" column. Default value : 0
Note on C74: Select the maximum ambient temperature expected during operation. If "other" is selected, specify in the "Additional notes" column. Default value : +40
Note on C75: Select the maximum non-condensing relative humidity expected during operation. If "other" is selected, specify in the "Additional notes" column. Default value : 80
Note on C76: Select the installation altitude above sea level. If "other" is selected, specify in the "Additional notes" column. Default value : up to and including 1 000
Note on C77: Select the minimum ambient temperature expected during storage and transportation. If "other" is selected, specify in the "Additional notes" column. Default value : -25
Note on C78: Select the maximum ambient temperature expected during storage and transportation. If "other" is selected, specify in the "Additional notes" column. Default value : +55
Note on C79: Select the maximum relative humidity expected during storage and transportation. If "other" is selected, specify in the "Additional notes" column. Default value : 95
Note on C80: Where seismic certification in accordance with IEC 60068-3-3 is required, select the seismic activity zone as defined in IEC 60721-2-6 for the location where the equipment is used. Where seismic certification is not required, select "not applicable".
Note on C81: Select the location of the AC UPS storage site. If "other" is selected, specify in the "Additional notes" column.
Note on C82: If "outside defined site service conditions" is selected, provide details in the "Additional notes" column. "Outside defined site service conditions" may require additional preservation provisions at the supplier's discretion.
Note on C83: Select the acoustic noise at 1,00 m during operation in normal mode. If "other" is selected, specify in the "Additional notes" column. Default value : manufacturer's standard
Note on C85: Select the required network connectivity interface media based on time synchronization, remote access and configuration of the ECMS. If "other" is selected, specify in the "Additional notes" column. Default value : Ethernet (Cu)
Note on C86: Select the required interface protocol to the ECMS as per project requirements. If "other" is selected, specify in the "Additional notes" column. Default value : Modbus TCP/IP
Note on C87: The UPS interface device should facilitate required network redundancy. If "other" is selected, specify in the "Additional notes" column the less preferred redundancy protocols such as Rapid Spanning Tree Protocol (RSTP) - IEEE 802.3.
Note on C88: Select "yes" if the AC UPS needs to be accessed from a central location or a remote location through intranet or internet. Default value : no
Note on C89: Select "yes" to notify that specific hardware (adapters, connectors, cables, etc.) is required for interface with existing installation or other third-party systems. Default value : no
Note on C90: Direct interface for critical / safety critical status and alarms to PCS where ECMS is not present. If "other" is selected, specify in the "Additional notes" column. Default value : not required
Note on C91: Select the required interface protocol to the PCS. If "other" is selected, specify in the "Additional notes" column. Default value : not applicable
Note on C92: Direct interface for the safety instrumented system (SIS) / emergency shutdown (ESD) and fire and gas (FGS) system trips to the AC UPS. Select the required option. Default value : not required
Note on C93: Direct interface for the safety instrumented system (SIS) / emergency shutdown (ESD) and fire and gas (FGS) system trips to the battery isolator. Select the required option. Default value : not required
Note on C95: Refer to the project electrical design basis to specify rated steady state R.M.S input voltage. If "other" is selected, specify in the "Additional notes" column.
Note on C96: Specify the steady state R.M.S input voltage tolerance. If "other" is selected, specify in the "Additional notes" column. Default value : ±10
Note on C97: Specify the rated input frequency. Default value : 50
Note on C98: Specify input frequency tolerance. If "other" is selected, specify in the "Additional notes" column. Default value : ±2
Note on C99: Specify the number of phases of input supply. Default value : 3
Note on C100: Specify whether neutral is available for the input supply. Default value : no
Note on C101: Specify the rated input current drawn with the energy storage device already fully charged.
Note on C102: Specify the maximum input current drawn at minimum input voltage (with negative tolerance applied) and simultaneous charging of the energy storage device.
Note on C103: Specify current inrush as % of rated current.
Note on C104: Specify the duration of the in-rush current.
Note on C105: Specify the total harmonic distortion of current that will be fed back to the incoming supply.
Note on C106: Specify the input supply short circuit current capacity (minimum and maximum).
Note on C107: Select the type of system earthing in accordance with IEC 61439-2:2020, Table AA.1 and IEC 60364-1. If "other" is selected, specify in the "Additional notes" column.
Note on C108: Specify the cross-sectional area of the power cable in mm² for input mains.
Note on C109: Specify the cross-sectional area of the power cable in mm² for the input bypass.
Note on C110: Specify the cross-sectional area of the power cable in mm² for the input maintenance bypass.
Note on C111: Select whether the isolation transformer is required at the input side.
Note on C112: Select the required material of the winding for the transformer. Default value : manufacturer's standard
Note on C113: Select the overvoltage category in accordance with IEC 60364-4-44.
Note on C115: Select the option in accordance with the project requirement. If a battery is not supplied as part of the AC UPS package, select "not applicable". If "other" is selected, specify the applicable document reference in the "Additional notes" column. Default value : IOGP S-740
Note on C116: Select the option in accordance with the project requirement. If the battery is not supplied as part of the AC UPS package, select "not applicable". If "other" is selected, specify the applicable document reference in the "Additional notes" column. Default value : IOGP S-740
Note on C117: Specify the duration of charging time required to restore 80 % capacity of the battery bank.
Note on C119: This isolation box is located external (outside) to AC UPS. If "yes" is selected, complete the other rows in this section (rows 110 to 133). If "no" is selected, specify "not applicable" in the "Additional notes" column in this section (rows 110 to 133).
Note on C120: Select the required enclosure material for the battery isolator box. If "other" is selected, specify in the "Additional notes" column. Default value : manufacturer's standard
Note on C121: Select the required battery isolator box mounting. Default value : on wall
Note on C122: Select the battery isolator box internal earth bar material. Default value : manufacturer's standard
Note on C123: Select the minimum ambient temperature expected. If "other" is selected, specify in the "Additional notes" column. Default value : 0
Note on C124: Select the maximum ambient temperature expected. If "other" is selected, specify in the "Additional notes" column. Default value : +40
Note on C125: Select the maximum relative humidity expected. If "other" is selected, specify in the "Additional notes" column. Default value : 80
Note on C126: Select the required degree of protection based on the installation location. IP31 is still the minimum requirement even if "manufacturer's standard" option is selected. Default value : IP31
Note on C127: Select the area classification (non-hazardous or hazardous) for the battery isolator box installation location. Default value : non-hazardous
Note on C128: Select the required hazardous area certification for the battery isolator box. If "other" is selected, specify in the "Additional notes" column. Default value : none
Note on C129: Select the applicable hazardous area zone classification for the installation location of the battery isolator box. Default value : not applicable
Note on C130: Select the required primary level of hazardous area protection for the battery isolator box. Default value : not applicable
Note on C131: Select the indirect cable entry via "ex-e" enclosure (if specifically required) when a hazardous classification is selected for the primary level of protection in row 127 (Area classification). Default value : no
Note on C132: Select the required cable entry location based on the planned installation.
Note on C133: Specify the value of the recommended voltage drop across battery cable (≤ % at nominal discharge current).
Note on C134: Specify the battery cable size as per cable sizing calculation considering the type of cable, discharge current, cable laying route, distance, etc.
Note on C135: Specify the required cable entry diameter to the battery isolator box in mm.
Note on C136: Select the required device type for battery isolation. Default value : MCCB
Note on C137: Specify the rated current of the battery isolation device considered.
Note on C138: Specify the maximum breaking capacity of a circuit breaker at the rated operational voltage.
Note on C139: Select the required number of wired breaker status potential free contact. Default value : none
Note on C140: Select whether an under-voltage trip feature is required in battery isolator box. Default value : no
Note on C141: Select whether an ESD trip feature is required in battery isolator box. Select "yes" if interface media is specified for "SIS / ESD and FGS from Battery isolator" in row 85. Default value : no
Note on C142: Select "yes" if "yes" is selected for both black start feature in row 33 and ESD trip in row 131. Default value : not required
Note on C143: Select whether an over-voltage trip is required in the battery isolator box. Default value : no
Note on C145: Specify the AC UPS output power in kVA.
Note on C146: Specify the AC UPS output power in kW.
Note on C147: Select the type of system earthing in accordance with IEC 61439-2:2020, Table AA.1 and IEC 60364-1. If "other" is selected, specify in the "Additional notes" column.
Note on C148: Select the number of phases for the output supply. Default value : 1
Note on C149: Select whether neutral is required for the output supply. Default value : yes
Note on C150: Specify the rated output voltage.
Note on C151: Specify the allowable static output voltage variation. If "other" is selected, specify in the "Additional notes" column. Default value : ±1
Note on C152: Specify the allowable dynamic output voltage variation. If "other" is selected, specify in the "Additional notes" column. Default value : ±5
Note on C153: Select the total harmonic distortion of voltage at 100 % linear load. If "other" is selected, specify in the "Additional notes" column. Default value : 4
Note on C154: Select the total harmonic distortion of voltage at 100 % non-linear load. If "other" is selected, specify in the "Additional notes" column. Default value : 5
Note on C155: Select the rated output frequency. Default value : 50
Note on C156: Specify the output frequency variation in free running mode. If "other" is selected, specify in the "Additional notes" column. Default value : ±0,1
Note on C157: Specify the value of rated output current at 100 % rated load.
Note on C158: Specify the value of additional current drawn by the increased load (overload) as a percentage of the rated current for 10 min.
Note on C159: Specify the value of additional current drawn by the increased load (overload) as a % of rated current for 1 min.
Note on C160: Specify the short circuit current in terms of % of the rated current.
Note on C161: Specify the short circuit withstand time in ms.
Note on C162: Specify the value of the rated load power factor. If “other” is selected, specify in the “Additional notes” column. Default value : 0,8 (lag)
Note on C163: Specify the value of the minimum weighted AC UPS deficiency in accordance with Table I.2.
Note on C164: Select whether an isolation transformer is required at the output side.
Note on C165: Select the required material of the winding for the transformer. Default value : manufacturer's standard
Note on C166: Select whether the output neutral is required to be earthed or kept floating.
Note on C167: Specify the cross-section area of the power cable in mm² for connection at the output side.
Note on C169: If "yes" is selected, specify the document reference in row 160 "Reference document to AC output distribution board". If "no" is selected, specify "not applicable" in the row 160 "Additional notes" column.
Note on C170: Specify the document reference of the specification to be followed by the supplier for the supply of the AC output distribution board. If "no" is selected in row 159, specify "not applicable" in the "Additional notes" column.
Note on C172: Specify the time for the transfer from the inverter to the bypass path in synchronized condition.
Note on C173: Specify the current rating of the static bypass switch.
Note on C174: Specify the current rating of the protection device used (fuse or circuit breaker).
Note on C175: Select whether an isolation transformer is required at the bypass side.
Note on C176: Select the required material of the winding for the transformer. Default value : manufacturer's standard
Note on C177: Select the location for the maintenance bypass switch and bypass transformer. If "remote compartment" is selected, specify the location in the "Additional notes" column. Default value : separate adjacent compartment
Note on C179: Select whether testing is required in addition to that specified in Table 5. If "yes" is selected, specify the additional testing requirements in the "Supplement" sheet. Default value : no
Note on C180: Select the duration for the routine full load test. If "other" is selected, specify the duration in the "Additional notes". This test is also referred to as a "burn-in" test. Default value : manufacturer's standard

## Supplement
Row |  | IOGP S-701D (2.01) Procurement Data Sheet for AC Uninterruptible Power Systems (UPS) (IEC) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-701D (2.01) Procurement Data Sheet for
AC Uninterruptible Power Systems (UPS) (IEC)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-701 Supplementary Specification to IEC 62040-3 for AC Uninterruptible Power Systems (UPS).
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data