## Addendum 1
Date of issue:
October 2025
Affected publication:
IOGP S-702D, Data Sheet for DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3), First Edition, August 2020
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in August 2020.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Row | Column | Update
| 23 * | All | Data sheet item "Performance classification" deleted
| 33 | All | New data sheet item "Conformal printed circuit board coating"
| 45 | Purchaser requirement / Supplier offered value | Default value amended to "supplier’s standard"
| 48 | All | New data sheet item "Busbar material"
| 49 | All | New data sheet item "Anti-condensation heaters required"
| 50 | All | New data sheet item "UPS enclosure access type - front side"
| 51 | All | New data sheet item "UPS enclosure access type - rear side"
| 52 | All | New data sheet item "Insulation material of internal wiring"
| 53 | All | New data sheet item "Internal lighting required"
| 97 | Description | Embedded guidance note amended
|  | Purchaser requirement / Supplier offered value | Default value amended to "Modbus TCP/IP"
|  | Purchaser requirement / Supplier offered value - options | List of options replaced with "not applicable, potential free contact, Modbus TCP/IP, Profinet, Ethernet IP, other"
| 100 | Description | Description amended
|  | Purchaser requirement / Supplier offered value | Default value amended to "Modbus TCP/IP"
|  | Purchaser requirement / Supplier offered value - options | List of options replaced with "not applicable, potential free contact, Modbus TCP/IP, Profinet, Ethernet IP, other"
| 105 | All | New data sheet item "Supervisory (common) alarm"
| 164 | All | New data sheet item "AC component (ripple voltage)"
| 172 | All | New data sheet item "Battery room requirements"
| 233 | All | New data sheet section "Testing" including new data sheet item "Additional testing required"
| Various | Row | Numbering updated as per new and deleted rows

## Front & Preliminaries
|  |  |  | SPECIFICATION | October 2025
|  |  |  | IOGP S-702D | Version 1.01
ADDENDUM 1 TO FIRST EDITION (AUGUST 2020)
Data Sheet for DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3)
Revision history
VERSION | DATE | PURPOSE
1.01 | October 2025 | Addendum 1
1 | August 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-702D (1.01) Data Sheet for DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-702D (1.01) Data Sheet for DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3)
Introduction
The purpose of this equipment data sheet is to define buyer specific requirements for the procurement of DC uninterruptible power systems (UPS) in accordance with IOGP S-702, for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-702, information requirements specification IOGP S-702L and quality requirements specification IOGP S-702Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet

## Data Sheet
Row | IOGP S-702D (1.01) Data Sheet for DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3) | [5 empty] | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description | [5 empty] | Default
4 | Ref. Clause | Description | Purchaser Identified Values | Manufacturer Declared Values |  | Additional notes
5 |  | GENERAL
6 | 5.1.2 | Vendor : | Input Data
7 | 5.1.2 | Order status : | Select |  |  |  |  | Select | for enquiry | for purchase
8 | 5.1.2 | Purchase order number, date : | Input Data
9 | 5.1.2 | Manufacturer : | Input Data
10 | 5.1.2 | Model number : | Input Data
11 | 5.1.2 | Serial number : | Input Data
12 | 5.2.3 | Application : | Input Data
13 | 5.3.2 | Purchaser specified rated output current : | Input Data |  | A
14 | 5.1.1 | Quantity : | Input Data
15 |  | Conformity assessment system (CAS) level : | D |  |  |  |  | Select | A | B | C | D
16 |  | CONFIGURATION
17 | 5.1.1, A.1, Figure A.1, Figure A.3, Figure A.5 | DC UPS configuration : | Select |  |  |  |  | Select | simplified single DC UPS with blocking diode -Figure A.1 | simplified dual DC UPS with independent output bus -Figure A.5A | simplified dual DC UPS with common output bus -Figure A.5B | other
18 | A.2.2 | Blocking diode required at output of single DC UPS : | Select |  |  |  |  | Select | not applicable | no | yes
19 | A.2.3 | Scalability : | Select |  |  |  |  | Select | not applicable | modular | manufacturer's standard
20 | 5.1.1 | DC UPS topology : | Select |  |  |  |  | Select | direct energy storage connect | series converter connect | shunt converter connect
21 | B.2.3 | Series converter connect option : | Select |  |  |  |  | Select | not applicable | with DC-DC converter | with dropper diode
22 | 5.4.2.3 | Battery configuration : | Select |  |  |  |  | Select | 1 x 100% | 2 x 100% | 2 x 50% | 2 x 50% (with interconnector) | other
23 | 8.1.1.3 | Bi-directional rectifier : | Select |  |  |  |  | Select | yes | no
24 | 8.2.2.11 | Remote access required : | no |  |  |  |  | Select | no | yes (read/write) | yes (read only)
25 | 8.2.2.11 | Hardware (adapters, connectors, cables, etc.) required for remote monitor : | no |  |  |  |  | Select | no | yes
26 | 8.1.1.5, 8.1.1.6 | On-line battery monitoring facility required : | no |  |  |  |  | Select | no | string monitoring | cell monitoring
27 | 8.1.1.4 | On-line battery testing feature required : | Select |  |  |  |  | Select | yes | no
28 | 8.1.1.4 | Battery test load interface : | no |  |  |  |  | Select | no | yes
29 | 5.4.2.3 | DC earth leakage monitoring required : | no |  |  |  |  | Select | no | yes
30 | 7.4.14 | Single line diagram and status display : | Select |  |  |  |  | Select | on mimic | on HMI | on both mimic and HMI
31 | 8.1.2.11 | Black Start feature required : | Select |  |  |  |  | Select | yes | no
32 | 8.1.1.1 | Earth screen required for isolation transformer : | Select |  |  |  |  | Select | yes | no | manufacturer to advise
33 |  | Conformal printed circuit board coating : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | yes
34 |  | PHYSICAL ASPECTS
35 | 7.2.1 | Mounting : | Select |  |  |  |  | Select | floor mounting | wall mounting
36 | 7.2.1 | Overall cabinet dimensions - length : | Input Data | Input Data | mm
37 | 7.2.1 | Overall cabinet dimensions - depth : | Input Data | Input Data | mm
38 | 7.2.1 | Overall cabinet dimensions - height : | Input Data | Input Data | mm
39 | 7.2.1 | Reference Outline Drawing number : | Input Data
40 | 7.2.1 | Total DC UPS cabinet mass : | Input Data |  | kg
41 | 7.2.1 | Total DC UPS mass with batteries (if integrated) : | Input Data |  | kg
42 | 7.2.4, 7.2.5 | Cable entry location : | Select |  |  |  |  | Select | bottom | top | both bottom and top
43 | 7.2.4, 7.2.5 | Cable entry type : | Select |  |  |  |  | Select | removable - undrilled plate | multi cable transit (MCT)
44 | 7.2.4, 7.2.5 | Gland plate material : | Select |  |  |  |  | Select | manufacturer's standard | non-magnetic plate
45 | 7.2.1 | Paint colour : | supplier's standard |  |  |  |  | Select | supplier's standard | other
46 | 7.2.1 | Canopy for cabinet required : | no |  |  |  |  | Select | no | yes
47 | 7.3.5 | Document holder : | yes |  |  |  |  | Select | yes | no
48 |  | Busbar material : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | electrolytic copper
49 | 7.4.15 | Anti-condensation heaters required : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | yes
50 |  | UPS enclosure access type - front side : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | hinged doors
51 |  | UPS enclosure access type - rear side : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | hinged doors
52 |  | Insulation material of internal wiring : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | low smoke zero halogen (LSZH)
53 |  | Internal lighting required : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | yes
54 |  | INSTALLATION
55 | 4.1 | Site : | Select |  |  |  |  | Select | onshore - coastal | onshore - desert | onshore - inland | offshore - fixed | offshore - floating | marine (ship)
56 | 4.1 | Location of DC UPS cabinet installation : | Select |  |  |  |  | Select | indoor | outdoor
57 | 7.3.1, 7.3.2 | Front access clearance dimensions for operation and maintenance : | Input Data |  | mm
58 | 7.3.2 | Side clearance for ventilation (if required) : | Input Data |  | mm
59 | 7.3.2 | Rear clearance for ventilation (if required) : | Input Data |  | mm
60 | 7.2.3, 7.9.3 | Installed location of battery : | Select |  |  |  |  | Select | battery room | inside DC UPS room | inside DC UPS enclosure | separate indoor battery cabinet | outdoor (battery enclosure) | outdoor (hazardous area battery enclosure)
61 | 7.2.3 | Maximum battery assembly dimensions (L x D x H) : | Input Data |  | mm
62 |  | SAFETY
63 | 5.1.1 | Accessibility : | Select |  |  |  |  | Select | operator access area | service access area | restricted access location
64 | 5.1.1 | Key required for cabinet : | Select |  |  |  |  | Select | yes | no
65 | 7.2.2 | Degree of protection (with closed doors) : | IP31 | IP31 |  |  |  | Select | IP31 | IP32 | IP42 | IP44 | IP55 | manufacturer standard
66 | 7.2.2 | Degree of protection (with open doors) : | IP2X | IP2X |  |  |  | Select | IP2X | IP3X
67 | 4.3.2 | Area classification : | Select |  |  |  |  | Select | safe | hazardous
68 | 4.3.2 | Hazardous area certification required : | Select |  |  |  |  | Select | none | ATEX | IECEx
69 | 4.3.2 | Level of protection : | Select |  |  |  |  | Select | not applicable | Ex-db | Ex-db eb
70 | 4.3.2 | Gas group : | Select |  |  |  |  | Select | IIA | IIB | IIB + H2 | IIC
71 | 4.3.2 | Temperature class : | Select |  |  |  |  | Select | T3 | T4 | T5 | T6 | T1 | T2
72 | 4.3.2 | Equipment protection level : | Select |  |  |  |  | Select | Ga | Gb | Gc
73 | 7.7.5 | Cooling fan replacement while DC UPS in service : | no |  |  |  |  | Select | no | yes
74 | 5.1.2 | Local language for caution/danger/warning labels : | Input Data
75 |  | ELECTROMAGNETIC COMPATIBLITY
76 | 5.1.4 | Emission : | UPS Cat C3 |  |  |  |  | Select | UPS Cat C3 | UPS Cat C2 | UPS Cat C1 | UPS Cat C4
77 | 5.1.4 | Immunity : | UPS Cat C3 |  |  |  |  | Select | UPS Cat C3 | UPS Cat C2 | UPS Cat C1 | UPS Cat C4
78 |  | ENVIRONMENTAL CONDITIONS
79 | 4.2.1.1 | Minimum ambient temperature (operation) : | Input Data |  | °C
80 | 4.2.1.1 | Maximum ambient temperature (operation) : | Input Data |  | °C
81 | 4.2.1.1 | Maximum relative humidity (operation) : | Input Data |  | %
82 | 4.2.1.1 | Temperature at which relative humidity is specified (operation) : | Input Data |  | °C
83 | 4.2.1.2 | Maximum altitude (operation) : | Input Data |  | m
84 | 4.2.2 | Minimum ambient temperature (storage and transportation) : | Input Data |  | °C
85 | 4.2.2 | Maximum ambient temperature (storage and transportation) : | Input Data |  | °C
86 | 4.2.2 | Maximum relative humidity (storage and transportation) : | Input Data |  | %
87 | 4.2.2 | Temperature at which relative humidity is specified (storage and transportation) : | Input Data |  | °C
88 | 4.3.2 | Seismic requirement data : | Input Data
89 | 4.2.2 | Storage site of DC UPS : | Select |  |  |  |  | Select | indoor – climate controlled (humidity and temperature) | indoor – temperature controlled only | indoor – natural ventilation | outdoor | refer abnormal or unusual conditions below
90 | 4.3.2 | Additional or unusual conditions (operation) : | Input Data
91 | 4.3.3 | Additional or unusual conditions (storage and transportation) : | Input Data
92 | 5.1.5 | Acoustic noise at 1 m - normal mode : | Select |  | dBA |  |  | Select | 70 | other
93 | 5.1.5 | Acoustic noise at 1 m - stored energy mode : | Select |  | dBA |  |  | Select | 70 | other
94 |  | COMMUNICATION INTERFACE(S)
95 | 5.6 | (1) Interface media for SCADA (ICSS / DCS) : | Select |  |  |  |  | Select | none | hardwired discrete | serial | Ethernet (Cu) | Ethernet (fiber) | wireless | other
96 | 5.6 | (1) Maximum allowable length of communication cable (for copper) : | Input Data |  | m
97 | 5.6 | (1) Interface protocol for SCADA (ICSS / DCS) : | Modbus TCP/IP |  |  |  |  | Select | not applicable | potential free contact | Modbus TCP/IP | Profinet | Ethernet IP | other
98 | 5.6 | (2) Interface media for Electrical Management / Control System : | Select |  |  |  |  | Select | none | hardwired discrete | serial | Ethernet (Cu) | Ethernet (fiber) | wireless
99 | 5.6 | (2) Maximum allowable length of communication cable (for copper) : | Input Data |  | m
100 | 5.6 | (2) Interface protocol for ECMS : | Modbus TCP/IP |  |  |  |  | Select | not applicable | potential free contact | Modbus TCP/IP | Profinet | Ethernet IP | other
101 | 5.6 | (3) Remote access / monitoring software required : | Select |  |  |  |  | Select | yes | no
102 | 5.6 | (3) Interface media for Remote access / monitoring : | Select |  |  |  |  | Select | none | Ethernet (Cu) | Ethernet (fiber) | wireless
103 | 5.6 | (3) Maximum allowable length of communication cable (for copper) : | Input Data |  | m
104 | 5.6 | (3) Interface protocol for Remote access / monitoring : | Select |  |  |  |  | Select | not applicable | SNMP | HTTPS | RDP | SFTP | Modbus | Profinet | other / supplier standard
105 | 8.2.4.5 | Supervisory (common) alarm : | 1 |  |  |  |  | Select | 1 | 2 | other
106 |  | AC INPUT SPECIFICATIONS
107 | 5.2.1 | Voltage (steady state, R.M.S) - rated : | Input Data |  | V
108 | 5.2.1 | Voltage (steady state, R.M.S - tolerance : | Input Data |  | %
109 | 5.2.1 | Frequency - rated : | Select |  |  |  |  | Select | 50 Hz | 60 Hz
110 | 5.2.1 | Frequency - tolerance : | Input Data |  | %
111 | 5.2.2 | Phases required : | Select | Select |  |  |  | Select | 1 | 2 | 3
112 | 5.2.2 | Neutral required : | Select | Select |  |  |  | Select | yes | no
113 | 5.2.2 | Current (R.M.S) - rated (with the energy storage device charged) : | Input Data |  | A
114 | 5.2.2 | Power factor : | Input Data | Input Data
115 | 5.2.2 | In-rush (% of rated current) : | Input Data | Input Data | %
116 | 5.2.2 | In-rush (time) : | Input Data | Input Data | s
117 | 5.2.2 | Maximum current (with low input volt and energy storage device charging) : | Input Data |  | A
118 | 5.2.2 | Time for overload (125 % of rated current) : | Input Data | Input Data | s
119 | 5.2.2 | Time for overload (150 % of rated current) : | Input Data | Input Data | s
120 | 5.2.2 | Total harmonic distortion (THD p.u.) : | Input Data |  | %
121 | 5.2.3 | Short circuit current of the input supply : | Input Data |  | kA
122 | 5.2.2 | Minimum prospective short circuit current : | Input Data |  | kA
123 | 5.2.2 | Earth leakage current : | Input Data |  | mA
124 | 5.2.2 | AC power distribution system - compatibility : | Select |  |  |  |  | Select | TN-C | TN-S | TN-C-S | TT | IT
125 | 5.2.3 | Additional or unusual conditions : | Input Data
126 | 5.2.3, 7.5.4 | Cable Size (cross-section area) - input mains (Float) : | Input Data |  | sq.mm.
127 | 7.5.4 | Cable Size (cross-section area) - input mains (Boost) : | Input Data |  | sq.mm.
128 | 7.4.8, 8.1.1.1 | Input isolation transformer required : | Select |  |  |  |  | Select | yes | no
129 | 7.4.10 | Input isolation transformer winding : | Select |  |  |  |  | Select | copper | aluminum | copper or aluminum
130 |  | DC AND BATTERY SPECIFICATIONS
131 | 5.4.2.2 | DC voltage level : | Select |  | V d.c. |  |  | Select | 110 | 220 | 380 | other
132 | 5.4.2.2 | Design life : | Input Data |  | years
133 | 5.4.2.2 | Float service life : | Input Data |  | years
134 | 5.4.2.2 | Shelf life of battery : | Input Data |  | months
135 | 5.4.2.2 | Quantity of cells and strings : | Input Data |  | nos.
136 | 5.4.2.2 | Nominal voltage (total) : | Input Data |  | V d.c.
137 | 5.4.2.2 | Battery technology : | Select |  |  |  |  | Select | nickel cadmium partial gas recombination | vented nickel cadmium | sealed nickel cadmium | valve regulated lead acid - AGM | valve regulated lead acid - gel | vented lead acid | other
138 | 5.4.2.2 | Nominal AH capacity : | Input Data |  | AH
139 | 5.4.2.2 | Discharge rate (C-rate) : | Select |  |  |  |  | Select | C5 | C10
140 | 5.4.2.2 | Electrolyte fill status : | Select | Select |  |  |  | Select | manufacturer standard | dry-uncharged | dry-charged | wet-charged | filled-uncharged | filled-charged
141 | 8.1.2.3 | Purchaser's requirement (% of battery recharge level - 1) : | 80 |  | % |  |  | Select | 80 | 85 | 90 | 100
142 | 8.1.2.3 | Purchaser's requirement (time for battery recharge level - 1) : | 10 |  | Hours |  |  | Select | 10 | 12 | 8 | 24
143 | 8.1.2.3 | Purchaser's requirement (% of battery recharge level - 2) : | 100 |  | % |  |  | Select | 80 | 85 | 90 | 100
144 | 8.1.2.3 | Purchaser's requirement (time for battery recharge level - 2) : | 24 |  | Hours |  |  | Select | 10 | 12 | 8 | 24
145 | 5.4.2.2 | Stored energy time (back-up time at 100% rated load) : | Input Data | Input Data | min
146 | 5.4.2.2 | Restored energy time (recharge time to 80% capacity) : | Input Data |  | hours
147 | 5.4.2.2 | Ambient reference temperature : | Input Data |  | °C
148 | 5.4.2.2 | Earth condition/isolation : | Select | Select |  |  |  | Select | floating | positive earthed | negative earthed
149 | 5.4.2.2 | Ripple current (R.M.S) : | Select |  | % |  |  | Select | battery manufacturer standard | 5 | 2 | 1
150 | 5.4.2.2 | Maximum discharge current : | Input Data |  | A
151 | 5.4.2.2 | DC Fault current rating : | Input Data |  | A d.c.
152 | 5.4.2.2 | Cable volt drop recommendation (≤ % at nominal discharge current) : | Input Data |  | %
153 | 5.4.2.2 | Charging regime : | Input Data
154 | 5.4.2.2 | Charge voltage (float) and tolerance band : | Input Data |  | V d.c.
155 | 5.4.2.2 | Charge voltage (boost) and tolerance band : | Input Data |  | V d.c.
156 | 5.4.2.2 | Charge voltage (equalising) and tolerance band : | Input Data |  | V d.c.
157 | 5.4.2.2 | Minimum end of discharge voltage : | Input Data |  | V d.c.
158 | 5.4.2.2 | Charge current limit (or range) : | Input Data |  | A d.c.
159 | 5.4.2.2 | Temperature compensated charging required : | Select |  |  |  |  | Select | yes | no
160 | 5.4.2.3 | Battery isolation box required : | Select |  |  |  |  | Select | yes | no
161 | 5.4.2.3 | Additional or unusual conditions : | Input Data
162 | 5.4.2.3 | Load profile for battery design, attached : | yes |  |  |  |  | Select | yes | no
163 | 5.4.2.3 | Battery rack design : | Select |  |  |  |  | Select | standard | seismic rated
164 | 6.4.2, 8.1.1.4, 8.1.2.13 | AC component (ripple voltage) | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | other
165 |  | BATTERY ROOM
166 | 4.2.1.1 | Minimum ambient reference temperature : | Input Data |  | °C
167 | 4.2.1.1 | Maximum ambient reference temperature : | Input Data |  | °C
168 | 5.4.2.1 | Area classification : | Select |  |  |  |  | Select | safe | hazardous
169 | 5.4.2.1 | Hazardous area classification : | Select |  |  |  |  | Select | not applicable | Zone 1 | Zone 2
170 | 5.4.2.1 | Minimum Gas Subdivision and Temperature Class (for equipment in Battery room) : | Select |  |  |  |  | Select | not applicable | IIB+H2 T3 | IIC T3
171 | 8.1.2.10 | Temperature sensor (for VRLA / partial gas recombination batteries) : | Select |  |  |  |  | Select | yes | no
172 |  | Battery room requirements | IOGP S-740 |  |  |  |  | Select | IOGP S-740 | not applicable | other
173 |  | BATTERY ISOLATOR BOX SPECIFICATIONS
174 | 7.9.1 | Enclosure material : | Select | Select |  |  |  | Select | manufacturer standard | sheet steel | light alloy | stainless steel
175 | 7.9.1 | Mounting : | Select |  |  |  |  | Select | on wall | on structural steel pedestal | on stainless steel frame
176 | 7.9.1 | Breathing valve required : | Select | Select |  |  |  | Select | yes | no | manufacturer to advise
177 | 7.9.1 | Internal earth bar : | Select |  |  |  |  | Select | copper | tinned copper
178 | 7.9.3 | Minimum design temperature : | Input Data |  | °C
179 | 7.9.3 | Maximum design temperature : | Input Data |  | °C
180 | 7.9.3 | Maximum relative humidity : | Input Data |  | %
181 | 7.9.3 | Temperature at which relative humidity is specified : | Input Data |  | °C
182 | 7.9.4 | Degree of protection : | Select |  |  |  |  | Select | IP44 | IP55 | IP66 | other
183 | 7.9.5 | Area classification : | Select |  |  |  |  | Select | safe | hazardous
184 | 7.9.5 | Hazardous Area Certification required : | Select |  |  |  |  | Select | none | ATEX | IECEx | EAC
185 | 7.9.5 | Hazardous area classification : | Select |  |  |  |  | Select | not applicable | Zone 1 | Zone 2
186 | 7.9.5 | Hazardous area level of protection : | Select |  |  |  |  | Select | not applicable | Refer to section "SAFETY" above | Ex-db eb IIB T3 Gb | Ex-db eb IIB+H2 T3 Gb | Ex-db eb IIC T3 Gb | Ex-db eb IIB T4 Gb | Ex-db eb IIC T4 Gb | Ex-db eb IIB T6 Gb | Ex-db eb IIC T6 Gb
187 | 7.9.6 | Cable entry : | Select |  |  |  |  | Select | bottom | top | bottom & side | top & side | all sides
188 | 7.9.6 | Cable indirect entry via 'ex e' enclosure : | Select |  |  |  |  | Select | yes | no
189 | 7.9.6 | Battery cable size (cross-section area) : | Input Data |  | sq.mm.
190 | 7.9.6 | Cable entry diameter in battery isolator box (ISO metric) : | Input Data
191 | 7.9.7 | Battery isolator type : | Select |  |  |  |  | Select | MCCB | switch fuse unit
192 | 7.9.8 | Rated current of breaker / switch fuse unit : | Input Data |  | A
193 | 7.9.8 | Rated breaking current (Icu) - (if breaker used) : | Input Data |  | kA
194 | 7.9.10 | Breaker status potential free contact (NO) : | Select |  |  |  |  | Select | two | one | none
195 | 7.9.9 | Under Voltage trip feature required : | no |  |  |  |  | Select | yes | no
196 | 7.9.9 | Under Voltage trip coil for : | not applicable |  |  |  |  | Select | not applicable | deep discharge protection | black start reserve
197 | 8.1.2.12 | ESD trip required : | Select |  |  |  |  | Select | no | yes - via undervoltage trip | yes - via shunt trip
198 | 8.1.2.12 | ESD override key switch : | Select |  |  |  |  | Select | not applicable | key captive in overridden position and with status contact
199 | 7.9.9 | Over voltage trip required : | no |  |  |  |  | Select | no | yes
200 |  | DC OUTPUT SPECIFICATIONS
201 | 5.3.2 | DC power distribution system - compatibility : | Select |  |  |  |  | Select | TN-C | TN-S | TN-C-S | TT | IT
202 | 5.3.2 | Voltage (steady state) - rated : | Input Data | Input Data | V d.c.
203 | 5.3.2 | Voltage - normal mode variation at no load : | Input Data | Input Data | %
204 | 5.3.2 | Voltage - normal mode variation at full load : | Input Data | Input Data | %
205 | 5.3.2 | Voltage - storage energy mode variation at no load : | Input Data | Input Data | %
206 | 5.3.2 | Voltage - storage energy mode variation at full load : | Input Data | Input Data | %
207 | 5.3.2 | % Voltage transient - transfer normal mode to storage energy mode : | Input Data |  | %
208 | 5.3.2 | Voltage transient time - transfer normal mode to storage energy mode : | Input Data |  | s
209 | 5.3.2 | % Voltage transient - transfer storage energy mode to normal mode : | Input Data |  | %
210 | 5.3.2 | Voltage transient time - transfer storage energy mode to normal mode : | Input Data |  | s
211 | 5.3.2 | % Voltage variation - normal mode at step load : | Input Data |  | %
212 | 5.3.2 | Duration of voltage variation - normal mode at step load : | Input Data |  | s
213 | 5.3.2 | % Voltage variation - storage energy mode at step load : | Input Data |  | %
214 | 5.3.2 | Duration of voltage variation - storage energy mode at step load : | Input Data |  | s
215 | 5.3.2 | Current - rated : | Input Data |  | A d.c.
216 | 5.3.2 | Current - overload capability (% of rated current for ten minutes) : | Input Data |  | %
217 | 5.3.2 | Current - overload capability (% of rated current for one minute) : | Input Data |  | %
218 | 5.3.2 | Current - short circuit capability (% of rated current) : | Input Data | Input Data | %
219 | 5.3.2 | Current - short circuit capability (time duration) : | Input Data | Input Data | s
220 | 5.3.2 | Current - limitation (% of rated current) : | Input Data |  | %
221 | 5.3.2 | Current - limitation (time duration) : | Input Data |  | s
222 | 5.3.2 | Current - fault clearing capability (normal mode) : | Input Data |  | A
223 | 5.3.2 | Current - fault clearing capability (stored energy mode) : | Input Data |  | A
224 | 5.3.2 | AC / DC efficiency in normal mode - 100% load : | Input Data |  | %
225 | 5.3.2 | AC / DC efficiency in normal mode - 75% load : | Input Data |  | %
226 | 5.3.2 | AC / DC efficiency in normal mode - 50% load : | Input Data |  | %
227 | 5.3.2 | AC / DC efficiency in normal mode - 25% load : | Input Data |  | %
228 | 5.3.2 | No load losses : | Input Data |  | W
229 | 7.1.6 | Reference document to DC output distribution board : | Input Data
230 | 5.3.3 | Additional or unusual conditions : | Input Data
231 | 5.3.3 | Cable size (cross-section area) - output : | Input Data |  | sq.mm.
232 |  | TESTING
233 | Table 3 | Additional testing : | no |  |  |  |  | Select | no | yes (see "Supplement" sheet)
Note on C6: Specify supplier's name, if supplier is not the manufacturer
Note on C7: Select the stage of procurement that this datasheet is being issued. (Default - Select)
Note on C8: Specify confirmed purchase order details
Note on C9: Supplier's Name
Note on C10: Specify the Product Series, Range or Model number, etc.
Note on C11: Specify the Product Serial number
Note on C12: Purchaser to select the intended application of the DC UPS.
Note on C13: Purchaser to specify the rated output current requirement
Note on C14: Specify quantity of DC UPS system being procured
Note on C15: Select CAS level as applied in S-702Q, Annex A. (Default - D)
Note on C17: Specify the DC UPS configuration. If other selected, use Additional notes to specify. (Default - Select)
Note on C18: Select whether blocking diode is required at output of single DC UPS. (Default - Select)
Note on C19: Select the scalability option. (Default - Select)
Note on C20: Select the desired UPS topology. (Default - Select)
Note on C21: Select the option for component / sub-assembly used on the output side. (Default - Select)
Note on C22: Select the desired battery configuration (where 50% implies 50% load for 100% autonomy time). If other selected, use Additional notes to specify. (Default - Select)
Note on C23: Select this feature (active front end), if battery is to be discharged and fed back in to source supply. (Default - Select)
Note on C24: Select if DC UPS system needs to be accessed from a central location or a remote location through intranet or internet. (Default - No)
Note on C25: Select if any specific hardware is required for interface with existing installation or other third party systems. (Default - No)
Note on C26: Select if additional system is envisaged for monitoring of storage energy batteries. (Default - No)
Note on C27: Select if feature is required for allowing rectifier to be blocked and battery to be drained for a specified time for on-line testing of storage energy batteries. (Default - Select)
Note on C28: Select the requirement if an interface (connection to load bank) is required. (Default - No)
Note on C29: Select if earth leakage protection is required for storage energy batteries. (Default - No)
Note on C30: Select the way in which Single line diagram and status shall be displayed. (Default - Select)
Note on C31: Select whether black start feature (deliver specified output voltage to load with only batteries connected) is required or not. (Default - Select)
Note on C32: Select option for use of earth screen in isolation transformer. (Default - Select)
Note on C33: Select whether conformal PCB coating is required PCBs from the effects of tropical or offshore area installation, such as moisture, salt spray, chemicals and temperature extremes to prevent such corrosion, mould growth and electrical failures. Default value - manufacturer's standard
Note on C35: Purchaser to select preferred mounting option of UPS (whether wall or floor mounting). (Default - Select)
Note on C36: Specify the overall cabinet dimensions - Length
Note on C37: Specify the overall cabinet dimensions - Width
Note on C38: Specify the overall cabinet dimensions - Height
Note on C39: Supplier to specify the GA drawing number for cross reference.
Note on C40: Specify the overall cabinet mass (excluding batteries)
Note on C41: Specify the overall cabinet mass including batteries (if batteries are integral to the cabinet)
Note on C42: Select cable entry location based on the installation planned. (Default - Select)
Note on C43: Supplier to select the type of cable entry considered for the cabinet (gland plate or MCT). (Default - Select)
Note on C44: Select the gland plate material type considering type of input power cable (1C or 3C). (Default - Select)
Note on C45: Select choice of external paint shade for cabinet. If other selected, use Additional notes to specify. (Default - supplier's standard)
Note on C46: Select choice of canopy for cabinet. (Default - No)
Note on C47: Purchaser to specify requirement of document holder inside cabinet. (Default - Yes)
Note on C48: Select the material of construction for the busbar. Default value - manufacturer's standard
Note on C49: Select whether thermostatically controlled anti-condensation heaters are required for each column. Default value - manufacturer's standard
Note on C50: Select whether hinged doors for front access to the UPS enclosure are required. Default value - manufacturer's standard
Note on C51: Select whether hinged doors for rear access to the UPS enclosure are required. Default value - manufacturer's standard
Note on C52: Select the required insulation material of the AC UPS internal wiring. Default value - manufacturer's standard
Note on C53: Select whether internal lighting in the AC UPS enclosure is required. Default value - manufacturer's standard
Note on C55: Select choice of UPS installation site. (Default - Select)
Note on C56: Select choice of location for installation of UPS. (Default - Select)
Note on C57: Specify front clearance dimension required in mm.
Note on C58: Specify side clearance dimension required in mm
Note on C59: Specify rear clearance dimension required in mm.
Note on C60: Select as per location of storage energy battery. (Default - Select)
Note on C61: Purchaser to specify the allocated space for DC UPS, in case of space constraint
Note on C63: Select the accessibility permitted for the area where DC UPS is installed. (Default - Select)
Note on C64: Select whether key is required for gaining access to the cabinet. (Default - Select)
Note on C65: Select ingress protection as per the installation location with cabinet doors closed. (Default - IP31)
Note on C66: Select ingress protection as per the installation location with cabinet doors opened. (Default - IP2X)
Note on C67: Select whether cabinet is installed in Safe or Hazardous area. (Default - Select)
Note on C68: Select which certification is required for DC UPS. (Default - Select)
Note on C69: Select the hazardous area level of protection, (Default - Select)
Note on C70: Select the gas group. (Default - Select)
Note on C71: Select temperature class. (Default - Select)
Note on C72: Specify equipment protection level. (Default - Select)
Note on C73: Purchaser to select whether it is required for the UPS cooling fan to be replaced while UPS is in service. (Default - No)
Note on C74: Purchaser to specify additional local / Native language to be used for describing Caution / Danger / Warning information on the labels of equipment.
Note on C76: Select category applicable for EMC emission. (Default - UPS Cat C3)
Note on C77: Select category applicable for EMC immunity. (Default - UPS Cat C3)
Note on C79: Specify minimum ambient temperature expected during operation
Note on C80: Specify maximum ambient temperature expected during operation
Note on C81: Specify maximum relative humidity expected during operation
Note on C82: Specify temperature at which relative humidity is specified while in operation
Note on C83: Specify installation altitude above mean sea level
Note on C84: Specify minimum ambient temperature expected during storage and transportation
Note on C85: Specify maximum ambient temperature expected during storage and transportation
Note on C86: Specify maximum relative humidity expected during storage and transportation
Note on C87: Specify temperature at which relative humidity is specified during storage and transportation
Note on C88: Specify seismic data in terms of 'g'force or acceleration.
Note on C89: Select choice of DC UPS storage site. (Default - Select)
Note on C90: Specify additional or unusual conditions expected during operation
Note on C91: Specify additional or unusual conditions expected during storage and transportation
Note on C92: Select acoustic noise at 1 m - during operation in normal mode. If other selected, use Additional notes to specify. (Default - Select)
Note on C93: Specify acoustic noise at 1 m - during operation in storage energy mode. If other selected, use Additional notes to specify. (Default - Select)
Note on C95: Select the Interface media as per project requirement. If other selected, use Additional notes to specify. (Default - Select)
Note on C96: Specify the limitation of communication cable length, if any.
Note on C97: Select the required interface protocol to the SCADA (ICSS / DCS) as per project requirements. If "other" is selected, specify in the "Additional notes" column.
Note on C98: Select the Interface media as per project requirement. (Default - Select)
Note on C99: Specify the limitation of communication cable length, if any.
Note on C100: Select the required interface protocol to the ECMS as per project requirements. If "other" is selected, specify in the "Additional notes" column. (Default - Modbus TCP/IP)
Note on C101: Select whether Remote access / monitoring software is required or not. (Default - Select)
Note on C102: Select the Interface media as per project requirement. (Default - Select)
Note on C103: Specify the limitation of communication cable length, if any.
Note on C104: Select interface protocol as per project requirement. If other selected, use Additional notes to specify. (Default - Select)
Note on C105: Specify the number of common supervisory alarm contact (NO/NC), minimum. If "other" is selected, specify in the "Additional notes" column. Default value - 1
Note on C107: Specify rated input voltage
Note on C108: Specify input voltage tolerance
Note on C109: Select rated input frequency. (Default - Select)
Note on C110: Specify input frequency tolerance
Note on C111: Select number of phases of input supply. (Default - Select)
Note on C112: Select whether neutral available for input supply. (Default - Select)
Note on C113: Specify rated input current drawn with the energy storage device charged
Note on C114: Specify input power factor
Note on C115: Specify current inrush as % of rated current.
Note on C116: Specify current inrush time.
Note on C117: Specify maximum current drawn with the input voltage at the minimum (-ve) tolerance and the energy storage device getting charged
Note on C118: Specify the time for which 125 % overload current can be sustained
Note on C119: Specify the time for which 150 % overload current can be sustained
Note on C120: Specify the total harmonic distortion of current
Note on C121: Specify the input supply short circuit current capacity
Note on C122: Specify the prospective short circuit current on the input side
Note on C123: Specify the earth leakage current characteristics (where in excess of 3.5mA)
Note on C124: Select applicable power system earthing schemes. (Default - Select)
Note on C125: Specify additional or unusual conditions expected at the input supply end
Note on C126: Mention input power cable details for Float module
Note on C127: Mention input power cable details of Boost module
Note on C128: Select whether isolation transformer is required at the input side. (Default - Select)
Note on C129: Select the transformer winding material. (Default - Select)
Note on C131: Select the DC Voltage level. If other selected, use Additional notes to specify. (Default - Select)
Note on C132: Specify the design life as declared for the batteries
Note on C133: Specify the float service life as declared for the batteries
Note on C134: Supplier to specify the shelf life (storage) of the selected battery
Note on C135: Specify the quantity of cells and strings as per the battery bank arrangement
Note on C136: Specify the rated battery bank voltage
Note on C137: Select the battery type as per project requirement. If other selected, use Additional notes to specify. (Default - Select)
Note on C138: Specify the nominal AH capacity of the selected cell to form the battery bank
Note on C139: Specify the discharge rate of the selected cell. (Default - Select)
Note on C140: Select the status (electrolyte fill and charge) of battery before it is transported. (Default - Select)
Note on C141: Purchaser to select the intermediate level of state of charge which needs to be achieved following a discharge at rated load. (Default - 80%).
Note on C142: Purchaser to select the time to attain the intermediate level of state of charge following a discharge at rated load. (Default - 10 Hours).
Note on C143: Purchaser to select the final level of state of charge which needs to be achieved following a discharge at rated load. (Default - 100%).
Note on C144: Purchaser to select the time to attain the final level of state of charge following a discharge at rated load. (Default - 24 Hours).
Note on C145: Specify the duration of back up available from battery bank feeding 100% rated load
Note on C146: Specify the duration of charging time required to restore 80% capacity of the battery bank
Note on C147: Specify the value of ambient temperature considered as reference value
Note on C148: Specify the polarities, if any, that are earthed by the installer (remote battery only). (Default - Select)
Note on C149: Select the value of ripple current as % of the numerical AH (C10) capacity of batteries. (Default - Select)
Note on C150: Specify the value of maximum discharge current at the end of the discharge during stored energy mode of operation
Note on C151: Specify the value of d.c. fault current rating
Note on C152: Specify the value of recommended voltage drop across battery cable (≤ % at nominal discharge current).
Note on C153: Specify one or more of the charging methods, namely, constant voltage, constant current, boost, equalization, two-state charging.
Note on C154: Specify the charging voltage (float) with tolerance band
Note on C155: Specify the charging voltage (boost) with tolerance band
Note on C156: Specify the charging voltage (equalising) with tolerance band
Note on C157: Specify the minimum value of end of discharge voltage
Note on C158: Specify the value of current limit during charging or range of charging current
Note on C159: Select whether charging rate shall be controlled using the temperature feedback from batteries. (Default - Select)
Note on C160: Select as required. (Default - Select)
Note on C161: Specify additional or unusual conditions expected at the input supply end
Note on C162: Select whether the battery load profile is attached or not. (Default - Yes)
Note on C163: Select the basis for battery rack design. (Default - Select)
Note on C164: Select the level of AC component (ripple voltage) output filtering if the DC UPS is required to operate with the battery disconnected. Additional filtering limits of 2 % Vrms or more depending on the nominal DC output voltage are typical. (Default - manfacturers standard)
Note on C166: Specify minimum ambient reference temperature expected in battery room
Note on C167: Specify maximum ambient reference temperature expected in battery room
Note on C168: Select the area classification of the battery room. (Default - Select)
Note on C169: Select the Hazard zone classification within the battery room. (Default - Select)
Note on C170: Select the minimum gas subdivision and Temperature Class for equipment in the battery room other than batteries. (Default - Select)
Note on C171: Select inclusion of temperature sensor in scope of supply, if temperature controlled charging is envisaged. (Default - Select)
Note on C172: Select the option in accordance with the project requirement. If the battery is not supplied as part of the AC UPS package, select "not applicable". If "other" is selected, specify the applicable document reference in the "Additional notes" column. Default value - IOGP S-740
Note on C174: Select the material of construction for Isolator box. (Default - Select)
Note on C175: Select the mounting provision required for the isolator box. (Default - Select)
Note on C176: Select whether breathing valve is required for Isolator box. (Default - Select)
Note on C177: Select the material of construction for internal busbars of Isolator box. (Default - Select)
Note on C178: Specify minimum design temperature for the Isolator box
Note on C179: Specify maximum design temperature for the Isolator box
Note on C180: Specify maximum relative humidity of area where Isolator box is installed
Note on C181: Specify temperature at which relative humidity is specified where battery box is installed
Note on C182: Select ingress protection as per the installation location. If other selected, use Additional notes to specify. (Default - Select)
Note on C183: Select whether cabinet is installed in Safe or Hazardous area. (Default - Select)
Note on C184: Select which certification is required for battery isolator box. (Default - Select)
Note on C185: Select Hazardous area classification type. (Default - Select)
Note on C186: Select Hazardous area certification type. (Default - Select)
Note on C187: Select cable entry location based on the installation planned. (Default - Select)
Note on C188: Select whether the cable entry is via 'ex-e' enclosure. (Default - Select)
Note on C189: Supplier to specify battery cable size as per cable sizing calculation considering type of cable, discharge current, cable laying route, distance, etc.
Note on C190: Specify the metric size of entry in battery isolator box for cable entry
Note on C191: Purchaser to select option as per project philosophy. (Default - Select)
Note on C192: Specify the standard (rated) ampere value of battery breaker
Note on C193: Specify the maximum breaking capacity of a circuit breaker at an associated rated operational voltage
Note on C194: Select whether potential free contact is required as wired out contacts. (Default - Select)
Note on C195: Purchaser to select whether Undervoltage trip feature is required in the Battery Isolator Box. (Default - No)
Note on C196: Purchaser to select the purpose for which Under voltage trip coil is considered in the Battery isolator box. (Default - N/A)
Note on C197: Purchaser to select whether ESD trip feature is required in the Battery Isolator box. (Default - Select)
Note on C198: Purchaser to select whether ESD override switch key switch is required and with captive feature. (Default - Select)
Note on C199: Purchaser to select whether Over voltage trip is required in the Battery Isolator box. (Default - No)
Note on C201: Select applicable DC power system earthing schemes. (Default - Select)
Note on C202: Specify rated steady state output voltage
Note on C203: Specify output voltage variation while in normal mode operation at no load
Note on C204: Specify output voltage variation while in normal mode operation at full load
Note on C205: Specify output voltage variation while in storage energy mode operation at no load
Note on C206: Specify output voltage variation while in storage energy mode operation at full load
Note on C207: Specify the % voltage transient (output) during transfer from normal mode to storage energy mode
Note on C208: Specify the output voltage transient time during transfer from normal mode to storage energy mode
Note on C209: Specify the % voltage transient (output) during transfer from storage energy mode to normal mode
Note on C210: Specify the output voltage transient time during transfer from storage energy mode to normal mode
Note on C211: Specify % voltage variation (output) while in normal mode operation when a step load in two steps (20% and then 80%) is applied.
Note on C212: Specify duration of voltage variation (output) while in normal mode operation when a step load in two steps (20% and then 80%) is applied.
Note on C213: Specify % voltage variation (output) while in storage energy mode operation when a step load in two steps (20% and then 80%) is applied.
Note on C214: Specify duration of voltage variation (output) while in storage energy mode operation when a step load in two steps (20% and then 80%) is applied.
Note on C215: Specify value of rated output current drawn by the 100% rated load
Note on C216: Specify value of additional current drawn by the increased load (overload) as a % of rated current for ten minutes
Note on C217: Specify value of additional current drawn by the increased load (overload) as a % of rated current for one minute
Note on C218: Specify the short circuit current (%of rated current)
Note on C219: Specify the time duration (time in seconds) to withstand the short circuit current.
Note on C220: Specify value of maximum current that can be drawn by the load.
Note on C221: Specify value of time duration for which the maximum current that can be drawn by the load.
Note on C222: Specify the fuse type and its rating for the maximum value of output current that shall be cleared by this protection device with normal mode operation
Note on C223: Specify the fuse type and its rating for the maximum value of output current that shall be cleared by this protection device with stored energy mode operation
Note on C224: Specify value of efficiency at 100% load during normal mode of operation
Note on C225: Specify value of efficiency at 75% load during normal mode of operation
Note on C226: Specify value of efficiency at 50% load during normal mode of operation
Note on C227: Specify value of efficiency at 25% load during normal mode of operation
Note on C228: Specify value of no load losses during normal mode of operation
Note on C229: Specify reference details to documents of DC distribution board
Note on C230: Specify additional or unusual conditions expected at the input supply end
Note on C231: Specify power cable details of output side.
Note on C233: Select whether additional testing is required in addition to the testing specified in Table 3. If "yes" is selected, specify the additional testing requirements in the "Supplement" sheet. Default value - no

## Supplement
Row |  | IOGP S-702 (1.01) Data Sheet for DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3) | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95

## Guidance
IOGP S-702 (1.01) Data Sheet for
DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3)
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-702 Supplementary Specification to IEC 62040-5-3 DC Uninterruptible Power Systems (UPS).
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.