## Addendum 1
Date of issue:
November 2025
Affected publication:
IOGP S-723D, Data Sheet for Electric Process Heaters, First Edition, December 2020
ADDENDUM 1
This addendum (Version 1.02) replaces Edition 1.0 published in December 2020 and Errata 1 (Version 1.01) published in May 2021.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Row | Column | Update
| 58 | All | New data sheet item "Standoff configuration"
| 63 | All | New data sheet item "Trial fit / factory assembly"
| 69 | Description | Embedded guidance note amended
|  | Purchaser requirement / Supplier offered value | Default value amended to "10%"
|  | Purchaser requirement / Supplier offered value - options | List of options "required, not required" * replaced with "not required, 10%, 20%"
| 73 | All | New data sheet item "Heater element service life"
| 103 | All | New data sheet item "Vessel scope"
| 104 | All | New data sheet item "Vessel specification"
| 105 | All | New data sheet item "Vessel data sheet"
| 106 | All | New data sheet item "Vessel tag number"
| 110 | All | New data sheet item "Vessel inlet nozzle flange size"
| 111 | All | New data sheet item "Vessel inlet nozzle flange rating and facing"
| 112 | All | New data sheet item "Vessel outlet nozzle flange size"
| 113 | All | New data sheet item "Vessel outlet nozzle flange rating and facing"
| 115 | All | New data sheet item "Minimum ambient temperature"
| 116 | All | New data sheet item "Maximum ambient temperature"
| 117 | All | New data sheet item "Auxiliary supply"
| 118 | All | New data sheet item "Auxiliary supply voltage"
| 149 | Ref. Clause | List of references amended
| Various | Row | Numbering updated in accordance with new rows

## Front & Preliminaries
|  |  |  | SPECIFICATION | November 2025
|  |  |  | IOGP S-723D | Version 1.02
ADDENDUM 1 TO FIRST EDITION (DECEMBER 2020)
Data Sheet for Electric Process Heaters
Revision history
VERSION | DATE | PURPOSE
1.02 | November 2025 | Addendum 1
1.01 | May 2021 | Errata 1
1 | December 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-723D (1.02) Data Sheet for Electric Process Heaters
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-723D (1.02) Data Sheet for Electric Process Heaters
Introduction
The purpose of this equipment data sheet is to define purchaser specific requirements for the procurement of electric process heaters in accordance with IOGP S-723 for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the specification require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheet, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the specification (IOGP S-723), information requirements specification (IOGP S-723L) and quality requirements specification (IOGP S-723Q) which together comprise the full set of specification documents. The Introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet

## Data Sheet
Row | IOGP S-723D (1.02) Data Sheet for Electric Process Heaters |  |  |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  |  |  |  | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | General
6 |  | Conformity assessment system (CAS) level : | D |  |  |  | Select | A | B | C | D
7 | 5.1.12, 5.1.2 | Pressure vessel design code : | Input Data
8 |  | Thermal and hydraulic design : | Select |  |  |  | Select | not required | design | check rate
9 |  | Applicable electrical standard : | Select |  |  |  | Select | IEC | NEMA/IEEE | CSA | other
10 |  | Power and control assembly : | Select |  |  |  | Select | required | heater only
11 |  | Incoming supply step down transformer : | Select |  |  |  | Select | permitted | not permitted
12 |  | Power transformer specification : | Input Data
13 |  | Mode of heater stage control : | manufacturer's standard |  |  |  | Select | manufacturer's standard | on/off | semiconductor | on/off plus semiconductor
14 |  | Semiconductor firing mode : | manufacturer's standard |  |  |  | Select | manufacturer's standard | zero cross only | zero cross and phase angle | phase angle only | none (on/off only)
15 | 4.1.4, 7.11.3 | Heater stage redundancy : | Select |  |  |  | Select | N+0 | N+1 | N+2 | other
16 | 5.4.10, 7.5.3 | Label plate and warning notice language : | Input Data
17 |  | Process data
18 |  | Fluid to be heated : | Input Data
19 |  | Temperature at inlet : | Input Data | Select |  |  | Select | °C | °F
20 |  | Temperature at outlet : | Input Data | Select |  |  | Select | °C | °F
21 |  | Pressure at inlet : | Input Data | Select |  |  | Select | kPa (ga) | psig
22 |  | Pressure drop allowable : | Input Data | Select |  |  | Select | kPa | psi
23 |  | Inlet flow rate : | Input Data | Select |  |  | Select | kg/s | lb/h
24 |  | Fouling resistance : | Input Data | Select |  |  | Select | m²·K/W | h·ft²·°F/Btu
25 |  | Minimum design heat duty : | Input Data | Select |  |  | Select | kW | Btu/h
26 |  | Maximum design heat duty : | Input Data | Select |  |  | Select | kW | Btu/h
27 |  | Margin on design heat duty : | Input Data
28 |  | Design pressure : | Input Data | Select |  |  | Select | kPa (ga) | psig
29 |  | Maximum design temperature : | Input Data | Select |  |  | Select | °C | °F
30 |  | Minimum design temperature : | Input Data | Select |  |  | Select | °C | °F
31 |  | Tubesheet corrosion allowance : | Input Data | Select |  |  | Select | mm | in
32 |  | Sour service : | Select |  |  |  | Select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not required
33 |  | Cyclic service : | Select |  |  |  | Select | Yes | No
34 |  | Site conditions
35 |  | Location environment : | Select |  |  |  | Select | onshore – coastal | onshore – desert | onshore – inland | offshore – fixed | offshore – floating | marine (ship) | interior location
36 | 4.3 | Maximum altitude : | 1 000 | m
37 | 4.3 | Heater minimum ambient temperature : | -15 | °C |  |  | Select | -15 | -20 | -40 | other
38 | 4.3 | Heater maximum ambient temperature : | 40 | °C |  |  | Select | 40 | 45 | 50 | other
39 | 4.3 | Heater maximum relative humidity : | Select | % |  |  | Select | 90 | 95 | 100
40 | 4.3 | Transport and storage conditions : | Select |  |  |  | Select | within defined site conditions | outside defined site conditions (see notes)
41 | 4.3 | Standstill period : | Select |  |  |  | Select | ≤ 6 months | ≤ 9 months | ≤ 12 months | other
42 |  | Main power supply
43 | 4.1.1, 4.1.2 | Main power supply voltage : | Input Data | kV
44 | 4.1.1, 4.1.2 | Main power supply frequency : | Select | Hz |  |  | Select | 50 | 60
45 |  | Space heater power supply voltage : | Input Data | V
46 |  | System earthing arrangement : | Select |  |  |  | Select | solidly earthed | low resistance earthed | high resistance earthed | unearthed | TN | IT
47 | 4.1.7 | Maximum steady-state voltage limit : | Select | % |  |  | Select | +5 | +6 | +10 | other
48 | 4.1.7 | Minimum steady-state voltage limit : | Select | % |  |  | Select | -5 | -10 | other
49 | 7.4.2 | Maximum prospective phase-to-earth short-circuit current : | Input Data | kA rms
50 | 7.2.2 | Maximum prospective three-phase short-circuit current : | Input Data | kA rms
51 | 7.16.1, 7.2.2 | Minimum prospective three-phase short-circuit current : | Input Data | kA rms
52 | 7.2.2, 7.4.2 | Prospective short-circuit fault duration : | Input Data | s
53 |  | Heater bundle
54 |  | General
55 |  | Bundle quantity : | Input Data | Select |  |  | Select | - | stacked
56 |  | Bundle orientation : | Select |  |  |  | Select | horizontal | vertical
57 | 5.1.1, 5.3.4 | Sheath-to-tubesheet sealing method : | Select |  |  |  | Select | manufacturer's standard | seal welding | strength welding | bite coupling
58 | 5.1.16, Figure 1 a), Figure 1 b), Figure 1 c) | Standoff configuration : | manufacturer's standard |  |  |  | Select | manufacturer's standard | Figure 1 a) - standard | Figure 1 b) - double tube | Figure 1 c) - cap design
59 | 9.2.4 | Pressure testing method for sheath-to-tubesheet joint : | Select |  |  |  | Select | pneumatic test | hydrostatic test | helium leak test
60 |  | Bundle weight : | Input Data | Select |  |  | Select | kg | lb
61 |  | Bundle installation location : | Input Data
62 | 5.2.2 | Baffle support spacing as per TEMA : | Select |  |  |  | Select | Yes | No
63 |  | Trial fit /factory assembly : | Select |  |  |  | Select | required - by heater supplier | required - by vessel supplier | not required
64 |  | Heater element
65 |  | Maximum allowable watt density (heat flux) : | Input Data | Select |  |  | Select | W/cm² | W/in²
66 |  | Quantity of non-withdrawable heater elements : | Input Data
67 |  | Quantity of withdrawable heater elements : | Input Data
68 | 5.1.5 | Quantity of spare withdrawable heater elements : | Input Data
69 | 5.1.6 | Non-withdrawable spares in operation from outset : | 10% |  |  |  | Select | not required | 10% | 20%
70 |  | Maximum allowable sheath temperature : | Input Data | Select |  |  | Select | °C | °F
71 |  | Sheath material thickness : | Input Data | Select |  |  | Select | mm | in
72 |  | Sheath tube construction : | Select |  |  |  | Select | seamless | welded
73 |  | Heater element service life : | Input Data | hours
74 |  | Overtemperature control
75 | 4.2.6, 5.3.6 | Overtemperature detector type : | manufacturer's standard |  |  |  | Select | manufacturer's standard | type K thermocouple | PT 100 resistance temperature detector
76 |  | Method of connection of overtemperature detector to element sheath : | manufacturer's standard |  |  |  | Select | manufacturer's standard | clamped | welded | thermowell
77 | 5.3.1 | Minimum number of overtemperature detectors : | Select | Select |  |  | Select | 1 | 2 | 3 | 4 | Select | per bundle | per stage
78 |  | Heaters rated for use in hazardous areas - zonal method
79 | 4.2.1, 4.2.4 | Heater bundle rated for use in a hazardous area - zonal method : | Select |  |  |  | Select | Yes | No
80 | 4.2.2 | Hazardous area equipment certifying scheme : | Input Data
81 |  | Equipment protection level : | Select |  |  |  | Select | EPL Ga | EPL Gb | EPL Gc | EPL Da | EPL Db | EPL Dc
82 |  | Main terminal box type of protection : | manufacturer's standard |  |  |  | Select | manufacturer's standard | Ex db | Ex eb | Ex ec | Ex db eb
83 |  | Auxiliary terminal box type of protection : | manufacturer's standard |  |  |  | Select | manufacturer's standard | Ex db | Ex eb | Ex ec | Ex db eb
84 |  | Temperature class : | Select |  |  |  | Select | T1 | T2 | T3 | T4 | T5 | T6
85 |  | Gas or dust group : | Select |  |  |  | Select | IIA | IIB | IIC | IIIA | IIIB | IIIC | IIB + hydrogen
86 |  | Heaters rated for use in hazardous areas - division method
87 | 4.2.3 | Heater bundle rated for use in a hazardous area - division method : | Select |  |  |  | Select | Yes | No
88 | 4.2.5 | Hazardous area equipment certifying scheme : | Input Data
89 |  | Equipment area classification : | Select |  |  |  | Select | Class 1 Division 1 | Class 1 Division 2 | Class 2 Division 1 | Class 2 Division 2
90 |  | Temperature class : | Select |  |  |  | Select | T1 | T2 | T2A | T2B | T2C | T2D | T3 | T3A | T3B | T3C | T4 | T4A | T5 | T6
91 |  | Gas or dust group : | Select |  |  |  | Select | A | B | C | D | E | F | G
92 |  | Terminal boxes
93 | 5.4.1, 5.4.2 | Ingress protection of terminal boxes : | Select |  |  |  | Select | IP55 | IP56 | IP66 | NEMA 4X
94 | 5.4.12, 5.4.4, 5.4.5 | Main terminal box cable entries : | Input Data
95 | 5.4.4, 5.4.5 | Auxiliary terminal box cable entries : | Input Data
96 | 5.4.6 | Line conductor specification : | Input Data | Select |  |  | Select | mm² | AWG
97 | 5.4.13, 5.4.14, 5.4.15, 5.4.16 | Protective paint system : | Input Data
98 |  | Portable earth connection point : | Select |  |  |  | Select | manufacturer's standard | 20 mm ball connection | 25 mm ball connection | not required
99 | 5.4.18 | Main terminal box process fluid breach detection : | not required |  |  |  | Select | not required | gas detector | other
100 |  | Partial discharge
101 |  | On-line partial discharge measurement : | Select |  |  |  | Select | required | not required
102 |  | Pressure vessel
103 |  | Vessel scope : | Select |  |  |  | Select | required | not required
104 |  | Vessel specification : | Input Data
105 |  | Vessel data sheet : | Input Data
106 |  | Vessel tag number : | Input Data
107 |  | Dimensions of the vessel or tank flange connected to heater tubesheet : | Input Data
108 |  | Vessel diameter : | Input Data | Select |  |  | Select | mm | in
109 |  | Vessel length : | Input Data | Select |  |  | Select | mm | in
110 |  | Vessel inlet nozzle flange size : | Input Data | Select |  |  | Select | DN | NPS
111 |  | Vessel inlet nozzle flange rating and facing : | Input Data
112 |  | Vessel outlet nozzle flange size : | Input Data | Select |  |  | Select | DN | NPS
113 |  | Vessel outlet nozzle flange rating and facing : | Input Data
114 |  | Power and control assembly
115 |  | Minimum ambient temperature : | Input Data | Select |  |  | Select | °C | °F
116 |  | Maximum ambient temperature : | Input Data | Select |  |  | Select | °C | °F
117 |  | Auxiliary supply : | Select |  |  |  | Select | internally derived | externally derived
118 |  | Auxiliary supply voltage : | Input Data | V
119 |  | Incoming isolator : | manufacturer's standard |  |  |  | Select | manufacturer's standard | required | not required
120 | 7.5.1, 7.5.2, 7.5.3 | Space heater : | Select |  |  |  | Select | required | not required
121 |  | Incoming cable entry direction : | Select |  |  |  | Select | bottom | top
122 | 7.14 | Incoming cable entries : | Input Data
123 | 7.14 | Incoming cable specification : | Input Data | Select |  |  | Select | mm² | in²
124 |  | Outgoing cable entry direction : | Select |  |  |  | Select | bottom | top
125 | 7.14 | Outgoing cable entries : | Input Data
126 | 7.14 | Outgoing cable specification : | Input Data | Select |  |  | Select | mm² | in²
127 |  | Outgoing cable earthing provision : | Select |  |  |  | Select | manufacturer's standard | earth switch | 20 mm ball connection | 25 mm ball connection | not required
128 | 7.4.4 | Main assembly external earth point size : | Input Data | Select |  |  | Select | mm | in
129 |  | Internal wiring specification : | Select |  |  |  | Select | manufacturer's standard | low smoke zero halogen
130 |  | Core balance current transformers on each heater stage : | Select |  |  |  | Select | required | not required
131 |  | Insulated busbar : | not required |  |  |  | Select | required | not required
132 | 7.13.2 | MV/HV voltage detecting or indicating system : | Select |  |  |  | Select | manufacturer's standard | capacitive voltage detecting system to IEC 61243-5 | capacitive voltage presence indicating system to IEC 62271-206 | not required
133 | 8.3.1 | Voltage display : | Select |  |  |  | Select | manufacturer's standard | incoming voltage only | outgoing voltage per heater stage | incoming voltage and outgoing voltage per heater
134 | 9.3.6 | North American MV/HV power and control assembly certification : | Select |  |  |  | Select | self-certified | 3rd party certified | NRTL certified | not applicable
135 | 7.2.6, 7.2.7 | LV arc resistance testing : | not required |  |  |  | Select | required | not required
136 |  | Additional testing : | Select |  |  |  | Select | required | not required
137 |  | Site interfaces
138 |  | Emergency shutdown interface relay : | Select |  |  |  | Select | SIL 2 required | SIL 3 required | not required
139 |  | Interface media for SCADA (ICSS / DCS) : | Select |  |  |  | Select | none | hardwired | serial | ethernet (Cu) | ethernet (fiber) | wireless | other
140 |  | Interface protocol for SCADA (ICSS / DCS) : | Select |  |  |  | Select | not applicable | 4-20 mA + potential free contact | RS485 | Modbus | Profinet | other
141 |  | Interface media for electrical management and control system : | Select |  |  |  | Select | none | hardwired discrete | serial | ethernet (Cu) | ethernet (fiber) | wireless
142 |  | Interface protocol for electrical management and control system : | Select |  |  |  | Select | not applicable | potential free contact | RS485 | Modbus | Profinet | IEC 61850 | other
143 |  | Remote access and monitoring software : | Select |  |  |  | Select | required | not required
144 | 8.2.4 | Remote manual reset : | Select |  |  |  | Select | required | not required
145 | 8.3.2 | Remote indication for each heater stage : | Select |  |  |  | Select | required | not required
146 |  | Material
147 |  | Element sheath material : | Input Data
148 | 5.1.12, 5.6.3 | Tubesheet material : | Input Data
149 | 5.2.3, 5.2.4, 5.2.5, 5.2.6 | Baffles/element supports : | Input Data
150 | 5.4.13, 5.4.14, 5.4.15, 5.4.16, 5.4.6 | Terminal box material : | Input Data
151 |  | Tubesheet-to-vessel flange bolting material : | Input Data
152 |  | Tubesheet-to-vessel flange joint gasket : | Input Data
Note on C6: Select CAS level as applied in S-723Q, Annex A.
Note on C7: E.g. ASME Section VIII div.1 , EN 13445, etc. Where the heater bundle is not installed in a pressure vessel, then specify "not applicable".
Note on C8: Specify "design" when thermal and hydraulic design is in the scope of supply of the vendor. Specify "check-rate" when a check-rating of exchanger designs provided by the purchaser is required.
Note on C9: Specify the applicable electrical standard according to the region where the electrical equipment is to be installed.
Note on C10: Specify when it is the intention of the purchaser that a power and control assembly is to be provided in the scope of supply.
Note on C11: Specify when the heater is to be powered directly from the specified main power supply voltage or whether an incoming supply step down transformer is permitted.
Note on C12: Specification which the power transformer shall conform to. This may be a JIP33 specification, company specification or regional standard. Where a power transformer is not permitted, state "not applicable".
Note on C13: Manufacturer's standard confirms there is no purchaser preference.
Note on C14: Where semiconductor control is specified confirm firing mode. Where on/off has been specified for all heater stage control modes, select "none".
Note on C15: Specify level of heater stage redundancy required. Where the process can function within its design parameters with a reduced number of stages, then N+0 should be considered. Where other is selected, state configuration in additional notes.
Note on C16: Specify which language label plates and warning notices will be written in.
Note on C18: Specify the fluid to be heated for which the system will be designed.
Note on C19: Specify the anticipated temperature of the fluid at the heater inlet.
Note on C20: Specify the anticipated temperature of the fluid at the heater outlet.
Note on C21: Specify the anticipated pressure of the fluid at the process heater inlet.
Note on C22: Specify the allowable pressure drop of the fluid to be heated.
Note on C23: Specify the anticipated inlet flow rate of the fluid to be heated.
Note on C24: Fouling resistance represents the theoretical resistance to heat flow due to a build-up of a layer of dirt or other fouling substance on the heater element or heater element sheath.
Note on C25: Design heat duty values cover the complete range of process conditions.
Note on C26: Design heat duty values cover the complete range of process conditions.
Note on C27: Specify an addition of margin (if any) on the design duty, instead of supplying spare elements or heater stage redundancy.
Note on C28: Specify internal design pressure and external design pressure if applicable.
Note on C29: Specify the maximum acceptable design temperature of the process heater.
Note on C30: Specify the lower value of the minimum ambient temperature and lowest process temperature.
Note on C31: Corrosion allowance is not applicable for the heater element sheath.
Note on C32: Specify based on process service applicable on vessel side. This will have an impact on material selection and material testing of material in contact with the process fluid to be heated.
Note on C33: If cyclic service is applicable, specify the variation, the time for the variation and the number of cycles or frequency for this variation expected during the life of the heater.
Note on C35: Specify the location where the heater system shall be installed.
Note on C36: Specify maximum altitude above sea level. 1 000 m is default. Modify 1 000 m value only if the site conditions are of an altitude greater than this.
Note on C37: Default is -15 °C. Modify -15 °C value only if the site conditions are lower than this. -20 °C aligns with the IEC 60079 series default minimum ambient air temperature requirement.
Note on C38: Default is 40 °C. Modify 40 °C value only if the site conditions are higher than this. 40 °C aligns with the IEC 60079 series default maximum ambient air temperature requirement.
Note on C39: Specify the maximum relative humidity at the maximum ambient air temperature defined in this data sheet.
Note on C40: Where "outside defined site conditions" is specified, the supplier will document additional measures to maintain equipment preservation in handling, shipping, storage and preservation procedure.
Note on C41: Specify the anticipated maximum period of standstill, storage or transport which the purchaser is aware of, so the manufacturer can provide appropriate packing and preservation.
Note on C43: Specify the main power supply voltage from which the heater system shall be supplied.
Note on C44: Specify the main power supply frequency from which the heater system shall be supplied.
Note on C45: Specify the space heater power supply voltage, from which the space heater shall be supplied. This applies to the main terminal box space heater and the power and control assembly space heater where specified.
Note on C46: Specify the method of system earthing used at site.
Note on C47: Specify the maximum steady-state voltage limit as a percentage of main power supply voltage.
Note on C48: Specify the minimum steady-state voltage limit as a percentage of main power supply voltage.
Note on C49: Specify the maximum prospective phase-to-earth short-circuit current at point of common coupling for which the heater shall be rated.
Note on C50: Specify the maximum prospective phase-to-phase short-circuit current at point of common coupling for which the heater shall be rated.
Note on C51: Specify the minimum prospective phase-to-phase short-circuit current at point of common coupling for which the heater shall be rated.
Note on C52: Specify prospective short-circuit fault duration time.
Note on C55: In case of stacked bundles, specify "stacked" in bracket after number of bundles e.g. 2 (stacked).
Note on C56: Specify the orientation of the heater bundle with regards to the axis of which the elements run.
Note on C57: Specify method of sealing of the heater element sheath to the tubesheet.
Note on C58: Select the standoff configuration of the sheath.
Note on C59: Specify method of pressure testing for the heater element sheath to the tubesheet.
Note on C60: Confirm the empty weight of bundle assembly including terminal boxes.
Note on C61: Specify the location where the heater bundle will be installed on the asset or site e.g. indoor, outdoor, outdoor-no shade, outdoor-shaded, etc.
Note on C62: Specify where TEMA standards with regards to baffle support spacing apply. Verification of baffle support spacing (for vibration, bending, etc.) proposed by the supplier is the purchaser's responsibility.
Note on C63: Select whether trial fit and removal of the heater units is required and if required, who is the responsible party.
Note on C65: Specify or confirm the maximum allowable watt density of the heater.
Note on C66: Confirm the number of non-withdrawable heater elements provided.
Note on C67: Confirm the number of withdrawable heater elements provided.
Note on C68: Specify the number of spare withdrawable elements required.
Note on C69: Caution: When a value other than "not required" is specified, this may result in a heater which is higher rated than where the spares are not in operation from the outset. Seek clarification from supplier(s) where necessary.
Note on C70: Specify or confirm maximum allowable sheath temperature.
Note on C71: Specify or confirm sheath material thickness.
Note on C72: Specify sheath tube construction as per selection field.
Note on C73: Specify the number of hours of continuous service at the maximum power.
Note on C75: Specify required temperature detection device type.
Note on C76: Specify method of connection of temperature detector with element sheath.
Note on C77: Specify the minimum amount of overtemperature detectors, select either per bundle or per stage, depending on user requirements.
Note on C79: Specify when the heater is to be rated for use in a hazardous area - zonal method. Zonal method refers to IEC 60079 compliance.
Note on C80: Specify which certification or notified scheme shall be accepted for heater bundles to be located in a hazardous area. Typically IECEx, ATEX, etc.
Note on C81: Specify the required equipment protection level (EPL) according to IEC 60079-14.
Note on C82: Specify the main terminal box type of protection according to IEC 60079 for which the heater bundle main terminal box shall be rated.
Note on C83: Specify the main terminal box type of protection according to IEC 60079 for which heater bundle auxiliary terminal boxes shall be rated.
Note on C84: Specify temperature group according to IEC 60079-0 for which the heater bundle shall be rated. In oil and gas applications, this will typically be a minimum of T3.
Note on C85: Specify gas or dust group for which the heater assembly is to be rated.
Note on C87: Specify when the heater is to be rated for use in a hazardous area - division method. Division method refers typically to North American and Canadian applications where area classification is defined as Division 1 or 2.
Note on C88: Specify which certification or notified scheme shall be accepted for heater bundles to be located in a hazardous area.
Note on C89: Specify equipment area classification in accordance with equipment certifying scheme.
Note on C90: Specify the required temperature class of equipment as per equipment certifying scheme.
Note on C91: Specify the gas or dust group for which the heater assembly is to be rated.
Note on C93: Specify the ingress protection method for terminal boxes.
Note on C94: Specify the number, size and type of cable entries in main terminal box e.g. State "undrilled" where applicable. Where cable entry requirements are not specified by the purchaser, the supplier will confirm their standard offering.
Note on C95: Specify the number, size and type of cable entries in auxiliary terminal box e.g. State "undrilled" where applicable. Where cable entry requirements are not specified by the purchaser, the supplier will confirm their standard offering.
Note on C96: Specify line conductor cable size, type and number of cables where known. State where singles are proposed.
Note on C97: IOGP S-723 makes reference to ISO 12944-2 for paint system. The purchaser can specify equivalent of ISO 12944-2 optionality. For stainless steel junction boxes, state "none".
Note on C98: For HV/MV applications, specify when the manufacturer is to provide a connection point on each phase and earth for the attachment of a portable earthing device.
Note on C99: Specify if a means of detection is required for a process fluid breach into the main terminal box. If other is selected, use additional notes to provide further information.
Note on C101: Specify when on-line partial discharge measurement is required. Where further detail is necessary use the notes field to advise.
Note on C103: Specify if the vessel or tank is in the scope of the heater supplier.
Note on C104: Specify the applicable specification for the vessel or tank.
Note on C105: Specify the vessel or tank data sheet number.
Note on C106: Specify the vessel or tank tag number.
Note on C107: Specify necessary dimensions (such as inside/ outside diameter, number of bolt holes with orientation, flange bolt size) of the connected vessel flange required for the design of heater tubesheet.
Note on C108: Specify vessel or tank internal diameter to enable the manufacturer to determine bundle specification.
Note on C109: Specify vessel or tank internal length to enable the manufacturer to determine bundle specification.
Note on C110: Specify the vessel inlet nozzle flange size. Vendor to confirm the nozzle inlet flange size.
Note on C111: Specify the vessel inlet nozzle flange rating and facing. Vendor to confirm the inlet nozzle flange rating and facing.
Note on C112: Specify the vessel outlet nozzle flange size. Vendor to confirm the nozzle outlet flange size.
Note on C113: Specify the vessel outlet nozzle flange rating and facing. Vendor to confirm the outlet nozzle flange rating and facing.
Note on C115: Specify the minimum ambient temperature for the power and control assembly. The heater bundle which also has an ambient temperature rating and the power and control assembly can be installed in different areas with different functional requirements.
Note on C116: Specify the maximum ambient temperature for the power and control assembly. The heater bundle which also has an ambient temperature rating and the power and control assembly can be installed in different areas with different functional requirements.
Note on C117: Select the auxiliary supply for controls, which is normally expected to be internally derived, but can also be external or from external UPS.
Note on C118: Specify the auxiliary supply voltage for the control assembly.
Note on C119: Specify where the supplier is to provide an incoming isolator as part of the power and control assembly.
Note on C120: Specify when a space heater is required in the power and control assembly.
Note on C121: Specify required incoming cable entry direction. This will be dependent on site cable routing.
Note on C122: Specify number, size and type of incoming cable entries State "undrilled" where applicable. Where cable entry requirements are not specified by the purchaser, the supplier will confirm their standard offering.
Note on C123: Specify the incoming cable specification, type and number of cables. State where singles are proposed.
Note on C124: Specify required outgoing cable entry direction. This will be dependent on site cable routing.
Note on C125: Specify number, size and type of outgoing cable entries State "undrilled" where applicable. Where cable entry requirements are not specified by the purchaser, the supplier will confirm their standard offering.
Note on C126: Specify outgoing cable specification, type and number of cables. State where singles are proposed.
Note on C127: For HV/MV applications, specify where the manufacturer is to provide a connection point on each phase and earth for the attachment of a portable earthing device.
Note on C128: Specify where external earth point stud size must be greater than that stated in IOGP S-723, 7.4.4.
Note on C129: Specify when the application requires that the power and control assembly internal wiring specification is to be low smoke zero halogen.
Note on C130: Core balance current transformers may be selected for discrete earth fault protection on each heater stage.
Note on C131: Specify when fully insulated busbars are required. Note: While providing personnel protection, this is also to address foreign bodies and rodents, etc. causing electrical breakdowns under normal operation.
Note on C132: A three-phase voltage detecting system confirms both the presence and absence of main circuit voltage, a three-phase voltage presence indicating system confirms the presence only of main circuit voltage.
Note on C133: Specify when a display of voltage is required on the front of the P&C assembly. Incoming voltage is the voltage level upstream of the switching device, outgoing voltage is that between the control circuit and the heater bundle.
Note on C134: NRTL or ACO certification may be required by the AHJ (e.g. USCG). Where NRTL or ACO certification is not required, purchaser discretion determines type of certification. Where this does not apply specify not applicable.
Note on C135: Specify when an LV power and control assembly will be provided and tested for arc containment / arc resistance.
Note on C136: Testing in addition to that defined in IOGP S-723, 10.3. Specific details of testing to be agreed between the purchaser and the supplier outside the boundaries of this specification.
Note on C138: Specify when an emergency shutdown interface relay is to be provided in the power and control assembly to facilitate equipment shutdown in the event of a site initiated emergency shutdown.
Note on C139: Specify the interface media as per project requirements. If "other" is selected, use additional notes to provide further information.
Note on C140: Specify the interface protocol as per project requirements. If "other" is selected, use additional notes to provide further information.
Note on C141: Specify the interface media as per project requirements.
Note on C142: Specify the interface protocol as per project requirements. If "other" is selected, use additional notes to provide further information.
Note on C143: Specify where remote access and monitoring software is required.
Note on C144: Remote manual reset should be considered for process heaters installed at unmanned facilities. Safety implications must be considered before specifying this facility.
Note on C145: While IOGP S-723, 9.3.2 requires remote common process heater status indication, the purchaser may specify indication for each heater stage.
Note on C147: Specify element sheath material with applicable design, material grade and class.
Note on C148: Specify or confirm tubesheet material, where the purchaser has not specified, the manufacturer is to confirm tubesheet material provided.
Note on C149: Specify or confirm baffle/element support material, where the purchaser has not specified, the manufacturer is to confirm baffle/element support material provided.
Note on C150: Specify the material from which the main terminal box is to be constructed.
Note on C151: Specify material of tubesheet to flange bolts.
Note on C152: Specify material of tubesheet to vessel flange joint gasket.

## Supplement
Row |  | IOGP S-723D (1.02) Data Sheet for Electric Process Heaters | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95

## Guidance
IOGP S-723D (1.02) Data Sheet for
Electric Process Heaters
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-723 Specification for Electric Process Heaters.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.