## Addendum 1
Date of issue:
December 2025
Affected publication:
IOGP S-615D, Procurement Data Sheet for Centrifugal Pumps (API), Second Edition, January 2023
ADDENDUM 1
This addendum (Version 2.01) replaces Edition 2.0 published in January 2023.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Row | Column | Update
| 44 | All | New data sheet item "System design pressure"
| 164 * | All | Data sheet item "Drain valve supplied by" * deleted
| 165 * | All | Data sheet item "Vent valve supplied by" * deleted
| 255 | All | New data sheet item "Inspection class"
| 263 | All | New data sheet item "PMI testing standard"
| 346 | All | New data sheet item "Mechanical run test until oil temperature stable"
| 347 | All | New data sheet item "4-hour mechanical run after oil temperature stable"
* Data from Edition 2.0.

## Front & Preliminaries
[5 empty] | SPECIFICATION | December 2025
[5 empty] | IOGP S-615D | Version 2.01
ADDENDUM 1 TO FIRST EDITION (JANUARY 2023)
Procurement Data Sheet for
Centrifugal Pumps (API)
Revision history
| VERSION | DATE | PURPOSE
| 2.01 | December 2025 | Addendum 1
| 2 | January 2023 | Second Edition
| 1 | January 2019 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-615D (2.01) Procurement Data Sheet for
Centrifugal Pumps (API)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
This second edition cancels and replaces the first edition published in January 2019. Due to technical writing requirements leading to extensive changes, this second edition should be treated as a new document.
IOGP S-615D (2.01) Procurement Data Sheet for
Centrifugal Pumps (API)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of centrifugal pumps in accordance with IOGP S-615 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-615), information requirements specification (IOGP S-615L) and quality requirements specification (IOGP S-615Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Procurement Data Sheet
Row | IOGP S-615D (2.01) Procurement Data Sheet for Centrifugal Pumps (API) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
5 |  | Tag number : | input data |  | input data
6 |  | Tag description : | input data |  | input data
7 |  | Applicable to : | select |  | select | [5 empty] | select | enquiry | purchase
8 | 5.1 | Units : | select |  | select | [5 empty] | select | US customary | SI
9 |  | Manufacturer : | input data |  | input data
10 |  | Pump model and size : | input data |  | input data
11 |  | Number of stages : | input data |  | input data
12 |  | Number of pump units : | input data |  | input data
13 |  | Service type : | select |  | select | [5 empty] | select | continuous | intermittent
14 |  | Number of starts : | input data | select | input data | select |  |  |  |  | select | per hour | per day | per week | other
15 |  | Instantaneous start-up : | select |  | select | [5 empty] | select | required | not required
16 | 6.1.13, 6.1.15, 8.3.3.4.3 | Pump operational mode : | select |  | select | [5 empty] | select | parallel | series | singly
17 | 7.1.7, 7.1.2 | Pump start-up mode : | select |  | select | [5 empty] | select | minimum continuous stable flow | minimum thermal flow | closed discharge valve | fully open discharge valve | open system
18 | 6.1.13, 6.1.15, 8.3.3.4.3 | Individual pump flow control : | select |  | select | [5 empty] | select | yes | no
19 |  | Site data
20 |  | Project country : | input data |  | input data
21 |  | Project region : | input data |  | input data
22 | 6.1.36 | Plant environmental location : | select |  | select | [5 empty] | select | offshore (fixed) | offshore (floating) | coastal | subsea | buried | onshore
23 | 6.1.36 | Equipment location : | select |  | select | [5 empty] | select | indoors | outdoors | other
24 | 6.1.3, 6.1.36, 7.1.1 | Location climate : | select |  | select | [5 empty] | select | heated | unheated | other
25 | 6.1.3, 6.1.36, 7.1.1 | Location sunlight protection : | select |  | select | [5 empty] | select | under roof | partial sides | direct sunlight | other
26 |  | Mounting : | select |  | select | [5 empty] | select | grade | mezzanine | other
27 | 6.1.3, 6.1.36, 7.1.1 | Special weather protection : | select |  | select | [5 empty] | select | tropicalization | winterization | not required
28 | 6.1.3, 6.1.36, 7.1.1, 7.1.6 | Elevation : | input data | select | input data | select |  |  |  |  | select | ft | m
29 | 6.1.3, 6.1.36, 7.1.1 | Barometer : | input data | select | input data | select |  |  |  |  | select | psi a | bar a
30 | 6.1.22, 6.10.2.7, 6.1.3, 6.1.36, 7.1.1 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °F | °C
31 | 6.1.3, 6.1.36, 7.1.1, 7.1.6 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °F | °C
32 | 6.1.3, 6.1.36, 7.1.1 | Maximum relative humidity : | input data | % | input data | %
33 | 6.1.3, 6.1.36, 7.1.1 | Minimum relative humidity : | input data | % | input data | %
34 | 6.1.3, 6.1.36, 7.1.1 | Unusual conditions : | select |  | select | [5 empty] | select | dust | fumes | dust and fumes | other | not applicable
35 | 6.1.36 | Floating applications motion design criteria : | input data |  | input data
36 | 6.1.3, 6.1.36, 7.1.1 | Hazardous area certification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
37 | 6.1.3, 6.1.36, 7.1.1, 7.1.6 | Explosion hazard classification (IEC) : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0
38 | 6.1.3, 6.1.36, 7.1.1 | Explosion gas group (IEC) : | select |  | select | [5 empty] | select | IIA | IIB | IIC
39 | 6.1.3, 6.1.36, 7.1.1 | Temperature class (IEC) : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
40 | 6.1.3, 6.1.36, 7.1.1, 7.1.6 | Explosion hazard classification (NFPA) : | select |  | select | [5 empty] | select | non-hazardous | division 2 | division 1
41 | 6.1.3, 6.1.36, 7.1.1 | Explosion gas group (NFPA) : | select |  | select | [5 empty] | select | Class I Group A | Class I Group B | Class I Group C | Class I Group D
42 | 6.1.3, 6.1.36, 7.1.1 | Temperature class (NFPA) : | select |  | select | [5 empty] | select | T1 | T2 | T2A | T2B | T2C | T2D | T3 | T3A | T3B | T3C | T4 | T4A | T5 | T6
43 | 7.3.2.2, 7.3.3.4 | Ignition hazard assessment : | select |  | select | [5 empty] | select | required | not required
44 | 6.1.15 | System design pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
45 |  | Utility conditions
46 | 6.1.3, 7.1.1 | Drivers voltage : | input data | V | input data | V
47 | 6.1.3, 7.1.1 | Drivers phase : | select |  | select | [5 empty] | select | 1 | 3
48 | 6.1.3, 7.1.1 | Driver frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
49 | 6.1.3 | Heating medium : | select |  | select | [5 empty] | select | steam | electric heat tracing | other
50 | 6.1.3, 7.1.1 | Heating voltage : | input data | V | input data | V
51 | 6.1.3, 7.1.1 | Heating phase : | select |  | select | [5 empty] | select | 1 | 3
52 | 6.1.3, 7.1.1 | Heating frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
53 | 6.1.3 | Heating steam minimum temperature : | input data | select | input data | select |  |  |  |  | select | °F | °C
54 | 6.1.3 | Heating steam maximum temperature : | input data | select | input data | select |  |  |  |  | select | °F | °C
55 | 6.1.3 | Heating steam minimum pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
56 | 6.1.3 | Heating steam maximum pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
57 | 6.1.3 | Cooling water maximum inlet temperature : | input data | select | input data | select |  |  |  |  | select | °F | °C
58 | 6.1.3 | Cooling water design temperature : | input data | select | input data | select |  |  |  |  | select | °F | °C
59 | 6.1.3 | Cooling water maximum inlet pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
60 | 6.1.3 | Cooling water design pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
61 | 6.1.3 | Cooling water type : | input data |  | input data
62 | 6.1.3 | Fouling factor : | input data | select | input data | select |  |  |  |  | select | hft²°R/btu | m²K/kW
63 | 6.1.3 | Cooling water chloride concentration : | input data | ppm | input data | ppm
64 | 6.1.3 | Instrument air minimum pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
65 | 6.1.3 | Instrument air maximum pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
66 |  | Liquid characteristics
67 | 6.1.3 | Liquid name : | input data |  | input data
68 | 6.1.3 | Liquid type : | select |  | select | [5 empty] | select | extremely hazardous | hazardous | flammable | toxic | non-hazardous | other
69 | 6.1.3 | Vapor pressure at rated temperature : | input data | select | input data | select |  |  |  |  | select | psi a | bar a
70 | 6.1.3 | Vapor pressure maximum : | input data | select | input data | select |  |  |  |  | select | psi a | bar a
71 | 6.1.3 | Vapor pressure minimum : | input data | select | input data | select |  |  |  |  | select | psi a | bar a
72 | 6.1.3 | Relative density rated : | input data |  | input data
73 | 6.1.3 | Relative density maximum : | input data |  | input data
74 | 6.1.3 | Relative density minimum : | input data |  | input data
75 | 6.1.3 | Specific heat rated : | input data | select | input data | select |  |  |  |  | select | Btu/lb°R | kJ/kgK
76 | 6.1.3 | Specific heat maximum : | input data | select | input data | select |  |  |  |  | select | Btu/lb°R | kJ/kgK
77 | 6.1.3 | Specific heat minimum : | input data | select | input data | select |  |  |  |  | select | Btu/lb°R | kJ/kgK
78 | 6.1.3 | Viscosity rated : | input data | select | input data | select |  |  |  |  | select | cP | Pa s
79 | 6.1.3 | Viscosity maximum : | input data | select | input data | select |  |  |  |  | select | cP | Pa s
80 | 6.1.3 | Viscosity minimum : | input data | select | input data | select |  |  |  |  | select | cP | Pa s
81 | 6.1.3, 6.3.19, 6.12.1.9 | Corrosive constituents : | input data |  | input data
82 | 6.1.3, 6.12.1.9, 6.12.1.10, 9.3.4.3 | Erosive constituents : | input data |  | input data
83 | 6.1.3, 6.12.1.8, 6.12.1.13, 8.2.2.7 | H2S concentration : | input data | ppm | input data | ppm
84 | 6.1.3, 6.12.1.9, 6.12.1.14 | Chloride concentration : | input data | ppm | input data | ppm
85 | 6.1.3, 6.12.1.9 | Total dissolved salts : | input data | ppm | input data | ppm
86 | 6.1.3, 6.12.1.9, 6.12.1.10, 9.3.4.3 | Particulate size : | input data | μm | input data | μm
87 | 6.1.3, 6.12.1.9, 6.12.1.10, 9.3.4.3 | Particulate concentration : | input data | ppm | input data | ppm
88 |  | Operating conditions
89 | 6.1.3, 6.1.10 | NPSHA datum : | select |  | select | [5 empty] | select | centerline of impeller | top of foundation | suction-nozzle centerline | other
90 | 6.1.3, 6.1.16 | Flow rated : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
91 | 6.1.3 | Flow normal : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
92 | 6.1.3 | Flow maximum : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
93 | 6.1.3 | Flow minimum : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
94 | 6.1.3 | Flow alternative condition : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
95 | 6.1.3, 6.1.10 | NPSHA rated : | input data | select | input data | select |  |  |  |  | select | ft | m
96 | 6.1.3 | NPSHA normal : | input data | select | input data | select |  |  |  |  | select | ft | m
97 | 6.1.3 | NPSHA maximum : | input data | select | input data | select |  |  |  |  | select | ft | m
98 | 6.1.3 | NPSHA minimum : | input data | select | input data | select |  |  |  |  | select | ft | m
99 | 6.1.3 | NPSHA alternative condition : | input data | select | input data | select |  |  |  |  | select | ft | m
100 | 6.1.3 | NPSHA at 120 % of rated flow : | input data | select | input data | select |  |  |  |  | select | ft | m
101 | 6.1.3 | Pumping temperature rated : | input data | select | input data | select |  |  |  |  | select | °F | °C
102 | 6.1.3 | Pumping temperature normal : | input data | select | input data | select |  |  |  |  | select | °F | °C
103 | 6.1.3, 8.3.2.7 | Pumping temperature maximum : | input data | select | input data | select |  |  |  |  | select | °F | °C
104 | 6.1.3 | Pumping temperature minimum : | input data | select | input data | select |  |  |  |  | select | °F | °C
105 | 6.1.3 | Pumping temperature alternative condition : | input data | select | input data | select |  |  |  |  | select | °F | °C
106 | 6.1.3 | Discharge pressure rated : | input data | select | input data | select |  |  |  |  | select | psi a | psi g | bar a | bar g
107 | 6.1.3, 6.3.1, 6.3.2 | Discharge pressure maximum : | input data | select | input data | select |  |  |  |  | select | psi a | psi g | bar a | bar g
108 | 6.1.3, 6.3.2 | Discharge pressure alternative condition : | input data | select | input data | select |  |  |  |  | select | psi a | psi g | bar a | bar g
109 | 6.1.3 | Suction pressure rated : | input data | select | input data | select |  |  |  |  | select | psi a | psi g | bar a | bar g
110 | 6.1.3 | Suction pressure normal : | input data | select | input data | select |  |  |  |  | select | psi a | psi g | bar a | bar g
111 | 6.1.3 | Suction pressure maximum : | input data | select | input data | select |  |  |  |  | select | psi a | psi g | bar a | bar g
112 | 6.1.3 | Suction pressure minimum : | input data | select | input data | select |  |  |  |  | select | psi a | psi g | bar a | bar g
113 | 6.1.3 | Suction pressure alternative condition : | input data | select | input data | select |  |  |  |  | select | psi a | psi g | bar a | bar g
114 | 6.1.3 | Differential pressure rated : | input data | select | input data | select |  |  |  |  | select | psi | bar
115 | 6.1.3 | Differential pressure alternative condition : | input data | select | input data | select |  |  |  |  | select | psi | bar
116 | 6.1.3 | Differential head rated : | input data | select | input data | select |  |  |  |  | select | ft | m
117 | 6.1.3 | Differential head alternative condition : | input data | select | input data | select |  |  |  |  | select | ft | m
118 | 6.1.3 | Hydraulic power : | input data | select | input data | select |  |  |  |  | select | hp | kW
119 |  | Performance
120 | 6.1.12, 6.1.14 | Proposal curve number : | input data |  | input data
121 |  | Impeller diameter rated : | input data | select | input data | select |  |  |  |  | select | in. | mm
122 |  | Impeller diameter maximum : | input data | select | input data | select |  |  |  |  | select | in. | mm
123 |  | Impeller diameter minimum : | input data | select | input data | select |  |  |  |  | select | in. | mm
124 | 6.1.6 | Rated speed : | input data | rpm | input data | rpm
125 | 6.1.12, 6.1.14 | Rated power : | input data | select | input data | select |  |  |  |  | select | hp | kW
126 | 6.1.12, 6.1.14 | Efficiency : | input data | % | input data | %
127 | 6.1.16 | Proposal curve BEP flow (at rated impeller diameter) : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
128 |  | Minimum flow thermal : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
129 |  | Minimum flow stable : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
130 | 6.1.6 | Start of preferred operating region : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
131 | 6.1.6 | End of preferred operating region : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
132 | 6.9.4.1 | Start of allowable operating region : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
133 | 6.9.4.1 | End of allowable operating region : | input data | select | input data | select |  |  |  |  | select | usgpm | m3/h
134 | 6.1.15 | Maximum head at rated impeller : | input data | select | input data | select |  |  |  |  | select | ft | m
135 | 6.1.12, 6.1.14 | Maximum power at rated impeller : | input data | select | input data | select |  |  |  |  | select | hp | kW
136 | 6.1.9 | NPSH3 at rated flow : | input data | select | input data | select |  |  |  |  | select | ft | m
137 |  | NPSH3 at 120 % of flow : | input data | select | input data | select |  |  |  |  | select | ft | m
138 |  | NPSHA-NPSH3 margin at rated flow : | input data | select | input data | select |  |  |  |  | select | ft | m
139 |  | NPSHA-NPSH3 margin in allowable operating region : | input data | select | input data | select |  |  |  |  | select | ft | m
140 | 6.1.17, Annex A, Equation A.1 | Specific speed : | input data | select | input data | select |  |  |  |  | select | usgpm rpm ft | m3/s rpm m
141 | 6.1.11, 6.1.17, Annex A, Equation A.2 | Suction-specific speed : | input data | select | input data | select |  |  |  |  | select | usgpm rpm ft | m3/s rpm m
142 | 6.1.19 | Maximum allowable sound pressure level : | input data | dB(A) | input data | dB(A)
143 |  | Maximum allowable sound power level : | input data | dB(A) | input data | dB(A)
144 |  | Construction
145 | 1.2, 4.2, Figure 1-Figure 18, Table 1 | API pump type : | select |  | select | [5 empty] | select | OH1 | OH2 | OH5 | OH5 BS 4082-1 | OH6 | BB1 | BB2 | BB3 | VS1 | VS2 | VS3 | VS4 | VS5 | VS6 | VS7
146 | 4.2, Figure 1-Figure 18, Table 1 | Mounting : | select |  | select | [5 empty] | select | foot | centerline | near centerline | vertical in-line | OH6: vertical sump cover plate / rectangular; BB1: vertical sump cover plate / flanged; BB2: vertical main body flange; BB3: vertical mounting plate separate from main body flange
147 | 1.2, 4.2.2.13-4.2.2.19 | Casing type : | select |  | select | [5 empty] | select | single volute | multiple volute | diffuser
148 | 6.6.1 | Impeller type : | select |  | select | [5 empty] | select | enclosed | open | semi-open
149 |  | Rotation (viewed from coupling end) : | select |  | select | [5 empty] | select | clockwise | counterclockwise
150 | 6.9.3.4 | Component balance to ISO 21940-11, Grade G1.0 : | select |  | select | [5 empty] | select | required | not required | other
151 | 6.6.14.2 | Impeller number of vanes : | input data |  | input data
152 |  | Suction size : | input data | in. | input data | in.
153 |  | Suction facing : | select |  | select | [5 empty] | select | RF | RTJ
154 |  | Suction rating : | select |  | select | [5 empty] | select | 150 | 300 | 600 | 900 | OH6: 1500
155 |  | Suction position : | select |  | select | [5 empty] | select | top | side | in-line | end | OH6: bottom; BB1: bell
156 |  | Discharge size : | input data | in. | input data | in.
157 |  | Discharge facing : | select |  | select | [5 empty] | select | RF | RTJ
158 |  | Discharge rating : | select |  | select | [5 empty] | select | 150 | 300 | 600 | 900 | OH6: 1500
159 |  | Discharge position : | select |  | select | [5 empty] | select | top | side | in-line | end | OH6: bottom; BB1: bell
160 | 6.3.3, 6.5.1, 7.4.23, Table 5 | Nozzle loads : | select |  | select | [5 empty] | select | as per API | other
161 | 6.4.3.1, 7.6.1.1 | Auxiliary process-liquid piping construction : | select |  | select | [5 empty] | select | flanged | socket welded | flanged | butt welded
162 | 6.12.3.4.2, 9.2.1.4 | Connection design approval prior to fabrication : | select |  | select | [5 empty] | select | required | not required
163 | 9.3.13.4 | Pressure casing drain size : | input data | in. | input data | in.
164 | 9.3.13.2, 9.3.13.3 | Pressure casing vent size : | input data | in. | input data | in.
165 |  | Pump warm-up or cooldown line : | select |  | select | [5 empty] | select | warm-up line | cooldown line | not applicable
166 | 6.4.3.6 | Machined and studded connections : | select |  | select | [5 empty] | select | required | not required
167 | 6.4.3.2 | Pipe threads specification : | select |  | select | [5 empty] | select | tapered ASME B1.20.1 | tapered ISO 7-1 | cylindrical ISO 228-1
168 | 6.3.6, 6.3.8, 6.3.9 | Case pressure rating maximum allowable working temperature : | input data | select | input data | select |  |  |  |  | select | °F | °C
169 | 6.3.6, 6.3.8, 6.3.9 | Case pressure rating maximum allowable working pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
170 | 6.1.22 | Bearing housing cooling method : | fan |  | fan | [5 empty] | select | fan | water | oil-circulating system | other
171 | 6.1.22 | Cooling water piping plan : | select |  | select | [5 empty] | select | A | K | M | not applicable
172 | 6.1.42 | Heat tracing and/or insulation : | select |  | select | [5 empty] | select | required | not required
173 | 6.1.42 | Purpose of insulation : | select |  | select | [5 empty] | select | personnel protection | cold conservation | heat conservation
174 | 6.1.42 | Extent of heat tracing and insulation : | input data |  | input data
175 | 6.1.42 | Heat tracing and/or insulation supplied and installed by : | select |  | select | [5 empty] | select | vendor | purchaser | not applicable
176 | 6.1.42 | Heating tracing and/or insulation specification : | select |  | select | [5 empty] | select | purchaser's standard | vendor's standard | not applicable
177 |  | Total package estimated mass : | input data | select | input data | select |  |  |  |  | select | lb | kg
178 | 9.1.1.3 | Shaft flexibility index reported by vendor : | select |  | select | [5 empty] | select | required | not required
179 | 9.1.1.3 | Shaft flexibility index (OH2 pumps only) : | input data |  | input data
180 | 9.1.2.6 | OH3 back-pullout lifting device : | select |  | select | [5 empty] | select | required | not required
181 | 9.2.2.3 | Shrink fit limited movement impellers : | select |  | select | [5 empty] | select | required | not required
182 |  | Vertical pump construction
183 | 9.3.2.9, 9.3.2.10, 9.3.12.3 | Head maximum allowable working pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
184 | 9.3.12.3, 9.3.13.1 | Column maximum allowable working pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
185 | 9.3.12.3, 9.3.13.1 | Bowl maximum allowable working pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
186 | 9.3.2.10 | Suction barrel or can maximum allowable working pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
187 | 9.3.6.2 | Pump thrust bearing location : | select |  | select | [5 empty] | select | in pump | in motor
188 |  | Suction strainer type : | input data |  | input data
189 |  | Level control by : | select |  | select | [5 empty] | select | float switch | level transmitter | not applicable
190 |  | Line shaft connection : | select |  | select | [5 empty] | select | sleeve and key | threaded
191 | 9.3.10.1 | Line shaft configuration : | select |  | select | [5 empty] | select | open | enclosed
192 | 9.3.10.1, 9.3.12.6 | Line shaft bearing lube : | select |  | select | [5 empty] | select | pumpage | water | oil | other
193 |  | Line shaft bearing quantity : | input data |  | input data
194 | 9.3.10.4, 9.3.13.6 | Hardened sleeves under line shaft bearings : | select |  | select | [5 empty] | select | required | not required
195 |  | Vertical pump sump dimensions
196 |  | Grade (underside of pump mounting plate or top of foundation) elevation : | input data | select | input data | select |  |  |  |  | select | in. | mm
197 |  | Low liquid level elevation : | input data | select | input data | select |  |  |  |  | select | in. | mm
198 |  | Sump floor elevation : | input data | select | input data | select |  |  |  |  | select | in. | mm
199 |  | Sump diameter : | input data | select | input data | select |  |  |  |  | select | in. | mm
200 |  | Grade to top of pump discharge connection dimension : | input data | select | input data | select |  |  |  |  | select | in. | mm
201 |  | Pump length (grade to underside of pump inlet bell or strainer dimension) : | input data | select | input data | select |  |  |  |  | select | in | mm
202 |  | Grade to first stage impeller centerline dimension : | input data | select | input data | select |  |  |  |  | select | in. | mm
203 |  | Grade to liquid minimum submergence level dimension : | input data | select | input data | select |  |  |  |  | select | in. | mm
204 |  | Bearings and lubrication
205 | 6.10.1.1, 6.10.1.2 | Radial bearing type : | select |  | select | [5 empty] | select | rolling element | hydrodynamic | other
206 | 6.10.1.1, 6.10.1.2 | Thrust type bearing : | select |  | select | [5 empty] | select | rolling element | other
207 | 9.2.5.2.6 | Review and acceptance of thrust bearing size : | select |  | select | [5 empty] | select | required | not required
208 | 6.10.1.11 | Rolling element bearing life calculations : | select |  | select | [5 empty] | select | required | not required
209 | 6.11.1, 6.11.3, 6.11.4 | Lubrication : | select |  | select | [5 empty] | select | flood | ring oil | flinger | purge oil mist | OH6: pure oil mist; BB1: grease
210 | 6.11.1, 6.11.5 | Oil viscosity ISO grade : | input data | ISO VG | input data | ISO VG
211 | 6.11.1, 6.11.5 | Oil type : | select |  | select | [5 empty] | select | mineral | synthetic
212 | 6.11.4, 9.1.2.7 | Grease type : | input data |  | input data
213 | 6.11.4, 9.1.2.7 | Grease grade : | input data |  | input data
214 | 6.10.2.9 | Bearing housing sealing type/model : | input data |  | input data
215 | 6.10.2.10.5 | Oil mist reclassifiers supplied by : | select |  | select | [5 empty] | select | purchaser | vendor
216 |  | Materials
217 | 6.12.1.1, Table H.1 | Annex H class : | select |  | select | [5 empty] | select | S-4 | S-5 | S-6 | S-8 | S-9 | C-6 | A-7 | A-8 | D-1 | D-2 | other
218 | 6.12.4.1 | Minimum design metal temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
219 | 6.12.1.14 | Reduced-hardness materials : | select |  | select | [5 empty] | select | required | not required
220 | 6.12.1.14 | Applicable hardness standard : | select |  | select | [5 empty] | select | not applicable | NACE MR0175 | NACE MR0103 | ISO 15156
221 | 6.12.1.10 | Special coating for impellers and other wetted parts : | select |  | select | [5 empty] | select | required | not required
222 | 6.12.1.3 | Case and case cover material : | input data |  | input data
223 | 6.12.1.3 | Nonwetted pressure-retaining fasteners material : | input data |  | input data
224 | 6.12.1.3 | Diffuser material : | input data |  | input data
225 | 6.12.1.3 | Impeller material : | input data |  | input data
226 | 6.12.1.3 | Inducer material : | input data |  | input data
227 | 6.12.1.14.4, 6.7.1 | Impeller wear component type : | select |  | select | [5 empty] | select | replaceable wear rings | hub integrally hardened | hub hard faced
228 | 6.12.1.3 | Impeller wear component material : | input data |  | input data
229 | 6.12.1.14.3, 6.7.2 | Impeller wear component hardness : | input data | select | input data | select |  |  |  |  | select | BHW | HRC
230 | 6.12.1.3 | Case wear ring material : | input data |  | input data
231 | 6.12.1.14.3, 6.7.2 | Wear parts hardnesses : | input data | select | input data | select |  |  |  |  | select | BHW | HRC
232 | 6.12.1.3 | Shaft material : | input data |  | input data
233 | 6.4.2.6, 7.6.1.2, Table H.4 | Auxiliary process-liquid lines, fittings and other connections to casing, including seal plans material : | select |  | select | [5 empty] | select | equivalent to casing | other
234 |  | Materials (additional for vertical pumps)
235 | 6.12.1.3, 9.3.2.7 | Suction barrel/can material : | input data |  | input data
236 | 6.12.1.3, 9.3.2.7 | Discharge head material : | input data |  | input data
237 |  | Discharge column material : | input data |  | input data
238 |  | Head column material : | input data |  | input data
239 | 6.12.1.3 | Discharge elbow and pipe material : | input data |  | input data
240 |  | Bowl/casing material : | input data |  | input data
241 |  | Bellmouth/suction cover material : | input data |  | input data
242 |  | Strainer material : | input data |  | input data
243 |  | Line shaft material : | input data |  | input data
244 |  | Shaft enclosing tube material : | input data |  | input data
245 |  | Bowl shaft material : | input data |  | input data
246 | Table H.1 | Process wetted fasteners material : | input data |  | input data
247 |  | Bearing retainer or spider material : | input data |  | input data
248 |  | Line shaft bearing material : | input data |  | input data
249 |  | Line shaft hard facing material : | input data |  | input data
250 |  | Line shaft sleeves material : | input data |  | input data
251 |  | Bearing lubrication lines material : | input data |  | input data
252 |  | Bowl bearing material : | input data |  | input data
253 |  | Material inspection
254 | 8.2.2.1, Table 14 | Material inspection requirements : | select |  | select | [5 empty] | select | default to Table 14 | alternative
255 | 8.2.2.1, Table 14 | Inspection class : | select |  | select | [5 empty] | select | Class I | Class II | Class III
256 | 6.12.4.3 | Impact test as per : | select |  | select | [5 empty] | select | EN 13445 | ASME BPVC Section VIII | other
257 | 8.2.2.7, 6.4.3.10 | Hardness testing of parts, welds and heat-affected zones : | select |  | select | [5 empty] | select | required | not required
258 | 6.12.1.6, 6.12.3.4.1, 8.2.1.3 | Additional surface/sub-surface examination : | select |  | select | [5 empty] | select | required | not required
259 | 6.12.3.4.1, 8.2.1.3 | Additional surface/sub-surface examination for : | input data |  | input data
260 | 6.12.3.4.1, 8.2.1.3 | Additional surface magnetic particle or liquid penetrant examination : | select |  | select | [5 empty] | select | magnetic particle | liquid penetrant | not required
261 | 6.12.3.4.1, 8.2.1.3 | Additional sub-surface ultrasonic or radiographic examination : | select |  | select | [5 empty] | select | radiographic | ultrasonic | not required
262 | 8.2.2.8 | Additional components PMI tested : | input data |  | input data
263 | 8.2.2.8 | PMI testing standard : | select |  | select | [5 empty] | select | ASME BPVC Section VIII Division 2 | MSS SP-137 | NORSOK M-601:2016 Section 12
264 | 8.2.1.1 | Repair and heat treatment records : | select |  | select | [5 empty] | select | required | not required
265 |  | Baseplate
266 | 7.4.4 | API baseplate number : | select |  | select | [5 empty] | select | 2.5 | 3 | 3.5 | 4 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 9 | 9.5 | 10 | 11 | 11.5 | 12 | not applicable
267 | 7.6.1.4 | Sized to accommodate seal piping systems : | select |  | select | [5 empty] | select | required | not required | not applicable
268 | 7.4.1, Figure 37, Figure 38, Figure 39 | Baseplate type : | select |  | select | [5 empty] | select | flat deck plate with sloped gutter / grouted | full sloped deck plate inside base plate / grouted | partial sloped deck plate inside base plate / grouted | flat deck plate with sloped gutter / nongrouted | OH6: full sloped deck plate inside base plate / nongrouted; BB1: partial sloped deck plate inside base plate / no-grouted
269 | 7.4.1, Figure 37, Figure 38, Figure 39 | Mounting : | select |  | select | [5 empty] | select | foundation grouted | foundation nongrouted | bolted on steel work | three point mount | OH6: four point mount; BB1: stilt mounted; BB2: other
270 | 7.4.10 | Stainless steel plate, thickness 0.2 in. (5 mm) minimum, under all pump feet : | select |  | select | [5 empty] | select | required | not required
271 |  | Mechanical seal
272 | 6.8.1 | API Standard 682 mechanical seal code : | input data |  | input data
273 |  | API Standard 682 data sheet attached : | select |  | select | [5 empty] | select | required | not required | not applicable
274 |  | Mechanical seal primary plan : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 11 | 12 | 13 | 14 | 21 | 23 | 31 | 32 | 41 | other
275 | 7.6.1.1 | Mechanical seal primary plan construction : | select |  | select | [5 empty] | select | piping - flanged socket welded | piping - flanged butt welded | tubing | other
276 |  | Mechanical seal secondary plan : | select |  | select | [5 empty] | select | 51 | 52 | 53A | 53B | 53C | 54 | 55 | 61 | 62 | 65A | 65B | 66A | 66B | 71 | 72 | 74 | 75 | 76 | other
277 |  | Tubing fittings manufacturer : | input data |  | input data
278 | 6.8.9 | Additional central flush port : | select |  | select | [5 empty] | select | required | not required
279 | 6.8.11 | Heating jacket required : | select |  | select | [5 empty] | select | required | not required
280 | 6.8.13 | Static sealing pressure maximum : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
281 | 6.8.13 | Static sealing pressure minimum : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
282 | 6.8.13 | Dynamic sealing pressure maximum : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
283 | 6.8.13 | Dynamic sealing pressure minimum : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
284 |  | Seal design temperature maximum : | input data | select | input data | select |  |  |  |  | select | °F | °C
285 |  | Seal design temperature minimum : | input data | select | input data | select |  |  |  |  | select | °F | °C
286 |  | Coupling
287 | 7.2.4 | Coupling specification : | API Standard 610 |  | API Standard 610
288 |  | Coupling manufacturer : | input data |  | input data
289 |  | Coupling type/model/size : | input data |  | input data
290 | 7.2.2, 7.2.3 | Coupling rating (power/100 rpm) : | input data | select | input data | select |  |  |  |  | select | hp/100 rpm | kW/100 rpm
291 | 7.2.2 | Coupling components balance grade : | select |  | select | [5 empty] | select | G1.0 | G2.5 | G6.3
292 | 7.2.9 | Coupling with hydraulic fit : | select |  | select | [5 empty] | select | required | not required
293 | 7.2.10 | Coupling with proprietary clamping device : | not required |  | not required | [5 empty] | select | required | not required
294 | 7.3.2 | Coupling guard specification : | input data |  | input data
295 | 7.3.2 | Coupling and exposed shaft guard material : | input data |  | input data
296 |  | Driver and gear
297 |  | Driver type : | select |  | select | [5 empty] | select | electric motor | steam turbine | diesel engine | HPRT
298 | 7.1.4, 7.1.10 | Driver specification : | input data |  | input data
299 |  | Driver manufacturer : | input data |  | input data
300 | 7.1.2, 7.1.5, Table 12, 7.1.10, 7.2.2 | Driver rating : | select |  | select | [5 empty] | select | Table 12 (motor) | end of curve | other
301 |  | Driver sized for testing on water : | select |  | select | [5 empty] | select | yes - full curve | yes - rated duty point only | other | no
302 |  | Driver frame or model : | input data |  | input data
303 | 7.1.2, 7.1.5, Table 12, 7.1.10 | Driver nameplate power : | input data | select | input data | select |  |  |  |  | select | hp | kW
304 |  | Driver nominal speed : | input data | rpm | input data | rpm
305 |  | Driver rated load speed : | input data | rpm | input data | rpm
306 |  | Driver lubrication method : | select |  | select | [5 empty] | select | flood | ring oil | flinger | purge oil mist | OH6: pure oil mist; BB1: grease
307 | 7.1.9 | Driver radial bearing type : | select |  | select | [5 empty] | select | rolling element | hydrodynamic | other
308 | 7.1.9 | Driver thrust bearing type : | select |  | select | [5 empty] | select | rolling element | hydrodynamic | tilt pad | other
309 | 7.1.7, 7.1.6 | Motor starting method : | select |  | select | [5 empty] | select | direct-on-line | soft start | other
310 |  | Adjustable speed drive : | select |  | select | [5 empty] | select | required | not required
311 |  | Source of adjustable speed drive : | select |  | select | [5 empty] | select | electrical ASD | fluid coupling | magnetically coupled ASD | other
312 |  | Required trip speed : | input data | rpm | input data | rpm
313 |  | Gear : | select |  | select | [5 empty] | select | required | not required
314 | 7.1.11 | Gear specification : | input data |  | input data
315 |  | Gear/adjustable speed drive manufacturer : | input data |  | input data
316 |  | Instrumentation
317 | 7.5.2.1 | Accelerometers : | select |  | select | [5 empty] | select | required | not required
318 |  | Number of accelerometers : | input data |  | input data
319 | 7.5.2.1 | Accelerometers mounting location : | input data |  | input data
320 | 6.10.2.13 | Threaded provision for mounting accelerometers only : | select |  | select | [5 empty] | select | required | not required
321 | 6.10.2.14 | Flat surface provision for mounting accelerometers only : | select |  | select | [5 empty] | select | required | not required
322 |  | Vibration probes : | select |  | select | [5 empty] | select | required | not required
323 |  | Number of vibration probes per radial bearing : | input data |  | input data
324 |  | Vibration probes mounting location : | input data |  | input data
325 | 7.5.2.2, 6.10.2.13 | Threaded provision for mounting vibration probe only : | select |  | select | [5 empty] | select | required | not required
326 | 6.10.2.14 | Flat surface provision for mounting vibration probes only : | select |  | select | [5 empty] | select | ​​​​​​​required | not required
327 | 7.5.2.2 | One-event-per-revolution probe (key phasor) : | select |  | select | [5 empty] | select | required | not required
328 | 7.5.2.5 | Temperature probes : | select |  | select | [5 empty] | select | required | not required
329 |  | Number of temperature probes per radial bearing : | input data |  | input data
330 |  | Temperature probes mounting location : | input data |  | input data
331 | 6.10.2.2 | Provision for mounting temperature probes only : | select |  | select | [5 empty] | select | required | not required
332 | 9.1.3.5 | Temperature gauges (with thermowells) : | select |  | select | [5 empty] | select | required | not required
333 | 7.5.2.6 | Monitors and cables supplied by : | select |  | select | [5 empty] | select | purchaser | vendor
334 |  | Testing
335 | 9.3.13.1 | Hydrostatic test of VS6/VS7 bowls and column : | select |  | select | [5 empty] | select | required | not required
336 | 9.2.4.2.4, J.4.1 | Residual unbalance test method : | select |  | select | [5 empty] | select | trial mass 6 positions | trial mass 12 positions
337 | 8.2.2.6 | Cleanliness prior to final assembly : | select |  | select | [5 empty] | select | required | not required
338 | 7.4.24 | Nozzle load test : | select |  | select | [5 empty] | select | required | not required
339 | 9.3.9.2 | Structural resonance test : | select |  | select | [5 empty] | select | required | not required
340 |  | Driver to be used for testing : | select |  | select | [5 empty] | select | contract | shop
341 | 8.1.1.3 | Notification of successful shop performance test : | select |  | select | [5 empty] | select | required | not required
342 | 8.3.3.7 | Performance test NPSHA limited to 110 % site NPSHA : | select |  | select | [5 empty] | select | required | not required
343 | 8.3.3.7 | Performance test at minimum submergence for vertical submerged pumps : | select |  | select | [5 empty] | select | required | not required
344 | 6.9.4.2, Figure 32, Figure 33, Figure 34 | Vibration test measurement locations : | select |  | select | [5 empty] | select | as per 6.9.4.2 | other
345 | 8.3.3.8.2 | Retest after final head adjustment : | select |  | select | [5 empty] | select | required | not required
346 | 8.3.4.2 | Mechanical run test until oil temperature stable : | select |  | select | [5 empty] | select | required | not required
347 | 8.3.4.2 | 4-hour mechanical run after oil temperature stable : | select |  | select | [5 empty] | select | required | not required
348 | 8.3.4.1, 8.3.4.3.1 | NPSH test : | select |  | select | [5 empty] | select | for all pumps | for first pump only | not required
349 | 8.3.4.3.3 | NPSH test type : | select |  | select | [5 empty] | select | valve suppression | vacuum loop
350 | 8.3.4.3.1 | NPSH test specification : | select |  | select | [5 empty] | select | HI 14.6 | ISO 9906
351 | 8.3.4.1, 8.3.4.4.1 | Complete unit test : | select |  | select | [5 empty] | select | yes | yes - including torsional measurements | no
352 |  | Duration of complete unit test : | input data | hours | input data | hours
353 | 8.3.4.1, 8.3.4.5 | Sound level test : | select |  | select | [5 empty] | select | required | not required
354 | 8.3.4.1, 8.3.4.6 | Auxiliary equipment test : | select |  | select | [5 empty] | select | required | not required
355 | 8.3.4.6 | Auxiliary equipment included in test : | input data |  | input data
356 | 8.3.4.1, 8.3.4.7 | Bearing housing resonance test : | select |  | select | [5 empty] | select | required | not required
357 | 8.3.3.9 | Disassembly after test : | not required |  | not required | [5 empty] | select | required | not required
358 | 9.2.7.4 | Hydrodynamic bearings removal and inspection after test : | select |  | select | [5 empty] | select | required | not required
359 |  | Surface preparation and painting
360 | 6.12.2.1, 7.4.16, 8.4.3.4, 9.3.8.3.2 | Surface preparation and painting specification : | input data |  | input data
361 |  | Other purchaser requirements
362 | 6.9.2.3, 6.9.2.7 | VFD steady state forced response analysis : | select |  | select | [5 empty] | select | required | not required
363 | 6.9.2.4 | Transient forced response analysis : | select |  | select | [5 empty] | select | required | not required
364 | 6.9.2.8, 6.9.2.9 | Torsional analysis report : | select |  | select | [5 empty] | select | required | not required
365 | 9.2.4.1.2 | Lateral analysis : | select |  | select | [5 empty] | select | required | not required
366 |  | Spare parts
367 | L.2.3.2 bullet f | Commissioning and start-up spares quotation : | required |  | required | [5 empty] | select | required | not required
368 | L.2.3.2 bullet f | Normal maintenance spares quotation : | not required |  | not required | [5 empty] | select | required | not required
369 | L.2.3.2 bullet f | Two-year operating spares quotation : | not required |  | not required | [5 empty] | select | required | not required
370 | L.2.3.2 bullet f | Capital spares quotation : | select |  | select | [5 empty] | select | required | not required
371 | 9.2.8.2 | Spare rotor storage orientation : | select |  | select | [5 empty] | select | horizontal | vertical
372 | 9.2.8.3 | Shipping and storage container for vertical storage of spare rotor : | select |  | select | [5 empty] | select | required | not required
373 | 9.2.8.4 | Inert gas purge for spare rotor container : | select |  | select | [5 empty] | select | required | not required
374 |  | Shipment
375 | 8.4.2, 8.4.3 | Preservation and packing specification : | input data |  | input data
376 | 8.4.2 | Preservation and packing suitable for : | select |  | select | [5 empty] | select | domestic delivery | export
377 | 8.4.2 | Export boxing : | select |  | select | [5 empty] | select | required | not required
378 | 8.4.2 | Outdoor storage : | select |  | select | [5 empty] | select | not required | required - for 6 months | required - for 12 months | required - for other duration
Note on C4: Select the CAS level to be applied in IOGP S-615Q, Annex A. Default value : D
Note on C5: Specify the unique tag number for the equipment.
Note on C6: Specify a functional description of the tag.
Note on C7: Select the procurement status of the data sheet.
Note on C8: Select the units of the entire procurement data sheet.
Note on C9: Specify the manufacturer of the proposed pump.
Note on C10: Specify the model and size of the proposed pump.
Note on C11: Specify the number of stages in the proposed pump (1 to 14 stages). Enter values in numeric format from 1 to 14.
Note on C12: Specify the number of pump units required.
Note on C13: Select the pump service type, i.e. whether the pump operation is continuous or intermittent.
Note on C14: Specify the number of starts per time unit that the pump is required to undergo.
Note on C15: Select whether instantaneous start-up is required.
Note on C16: Select the pump operational mode.
Note on C17: Select the pump start-up mode.
Note on C18: Select whether the pump has an individual flow control.
Note on C20: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C21: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C22: Select the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be installed.
Note on C23: Select the location where the equipment will be installed.
Note on C24: Select the location climate where the equipment will be installed.
Note on C25: Select the sunlight protection where the equipment will be installed.
Note on C26: Select the level at which the equipment will be installed.
Note on C27: Select the special weather protection of the location where the equipment will be installed.
Note on C28: Specify the site elevation at which the equipment will be installed.
Note on C29: Specify the atmospheric pressure of the location where the equipment will be installed.
Note on C30: Specify the maximum ambient temperature of the location where the equipment will be installed.
Note on C31: Specify the minimum ambient temperature of the location where the equipment will be installed.
Note on C32: Specify the maximum relative humidity of the location where the equipment will be installed.
Note on C33: Specify the minimum relative humidity of the location where the equipment will be installed.
Note on C34: Select the unusual conditions in the location where the equipment will be installed
Note on C35: Specify the metocean and floating facility data of the location where the equipment will be installed.
Note on C36: Select the code to be followed for the hazardous area classification.
Note on C37: Select the hazardous zone or division in which the pump will operate. To be completed when IEC is applicable.
Note on C38: Select the gas group classification of the pump in accordance with the classification. To be completed when IEC is applicable.
Note on C39: Select IEC temperature class applicable to the area where the equipment will be installed.
Note on C40: Select the hazardous zone or division in which the pump will operate. To be completed when NFPA is applicable.
Note on C41: Select the gas group classification of the pump in accordance with the classification. To be completed when NFPA is applicable.
Note on C42: Select the NFPA temperature class applicable to the area where the equipment will be installed.
Note on C43: Select whether ignition hazard assessment is required for coupling and shaft guards.
Note on C44: Specify the system design pressure.
Note on C46: Specify the driver voltage.
Note on C47: Select the driver phase.
Note on C48: Select the driver frequency.
Note on C49: Select the heating medium.
Note on C50: Specify the heating voltage.
Note on C51: Select the heating phase.
Note on C52: Select the heating frequency.
Note on C53: Specify the heating steam minimum temperature.
Note on C54: Specify the heating steam maximum temperature.
Note on C55: Specify the heating steam minimum pressure.
Note on C56: Specify the heating steam maximum pressure.
Note on C57: Specify the cooling water maximum inlet temperature.
Note on C58: Specify the cooling water design temperature.
Note on C59: Specify the cooling water maximum inlet pressure.
Note on C60: Specify the cooling water design pressure.
Note on C61: Specify the cooling water type.
Note on C62: Specify the cooling water side fouling factor.
Note on C63: Specify the cooling water chloride concentration.
Note on C64: Specify the instrument air minimum pressure.
Note on C65: Specify the instrument air maximum pressure.
Note on C67: Specify the liquid the pump will handle.
Note on C68: Select the pumped liquid characteristics.
Note on C69: Specify the normal vapor pressure.
Note on C70: Specify the maximum vapor pressure. Purchaser to state whether the pump is to be sized for the NPSHA at the maximum vapor pressure case.
Note on C71: Specify the minimum vapor pressure.
Note on C72: Specify the rated relative density.
Note on C73: Specify the maximum relative density. Purchaser to state whether the driver is to be rated for the maximum relative density case.
Note on C74: Specify the minimum relative density. Purchaser to state whether the pump is to be sized for the differential head at the minimum relative density case and casing MAWP and driver rated for the maximum relative density case.
Note on C75: Specify the rated specific heat.
Note on C76: Specify the maximum specific heat.
Note on C77: Specify the minimum specific heat. Purchaser to state whether the pump and seal cooling are to be sized for the minimum specific heat case.
Note on C78: Specify the rated viscosity.
Note on C79: Specify the maximum viscosity. Purchaser to state whether the driver is to be rated for the maximum viscosity case.
Note on C80: Specify the minimum viscosity.
Note on C81: Specify the corrosive constituents within the pumped liquid.
Note on C82: Specify the erosive constituents within the pumped liquid.
Note on C83: Specify the H2S concentration within the pumped liquid to determine if the service is sour.
Note on C84: Specify the chloride concentration within the pumped liquid.
Note on C85: Specify the total dissolved salts concentration within the pumped liquid.
Note on C86: Specify the particulate size within the pumped liquid.
Note on C87: Specify the particulate concentration within the pumped liquid. Consider as well particle size distribution and hardness.
Note on C89: Select the elevation the pump suction conditions, including NPSH3, are referenced to.
Note on C90: Specify the rated flow.
Note on C91: Specify the normal flow.
Note on C92: Specify the maximum flow.
Note on C93: Specify the minimum flow.
Note on C94: Specify any alternative flowrate the pump is to be designed for.
Note on C95: Specify the rated NPSHA.
Note on C96: Specify the normal NPSHA.
Note on C97: Specify the maximum NPSHA.
Note on C98: Specify the minimum NPSHA. Purchaser to state whether a positive margin is required between NPSHA and NPSH3 at the minimum NPSHA case.
Note on C99: Specify any alternative NPSHA the pump is to be designed for. Purchaser to state if a positive margin is required between NPSHA and NPSH3 at the alternative NPSHA case.
Note on C100: Specify the NPSHA at 120 % of rated flow. Purchaser to state whether a positive margin is required between NPSHA and NPSH3 at the NPSHA at 120 % of rated flow case.
Note on C101: Specify the rated pumping temperature.
Note on C102: Specify the normal pumping temperature.
Note on C103: Specify the maximum pumping temperature.
Note on C104: Specify the minimum pumping temperature.
Note on C105: Specify any alternative temperature for which the pump is to be designed.
Note on C106: Specify the rated discharge pressure.
Note on C107: Specify the maximum discharge pressure.
Note on C108: Specify any alternative discharge pressure for which the pump is to be designed.
Note on C109: Specify the rated suction pressure.
Note on C110: Specify the normal suction pressure.
Note on C111: Specify the maximum suction pressure.
Note on C112: Specify the minimum suction pressure.
Note on C113: Specify any alternative suction pressure for which the pump is to be designed.
Note on C114: Specify the rated differential pressure.
Note on C115: Specify any alternative differential pressure for which the pump is to be designed.
Note on C116: Specify the rated differential head.
Note on C117: Specify any alternative differential head for which the pump is to be designed.
Note on C118: Specify the hydraulic power.
Note on C120: Specify the pump proposal curve number.
Note on C121: Specify the proposed pump rated impeller diameter.
Note on C122: Specify the proposed pump maximum impeller diameter.
Note on C123: Specify the proposed pump minimum impeller diameter.
Note on C124: Specify the proposed pump rated speed.
Note on C125: Specify the proposed pump rated power.
Note on C126: Specify the proposed pump rated duty point efficiency.
Note on C127: Specify the proposed pump BEP flow with the rated impeller diameter.
Note on C128: Specify the proposed pump minimum thermal flow with the rated impeller diameter.
Note on C129: Specify the proposed pump minimum stable flow with the rated impeller diameter.
Note on C130: Specify the proposed pump start of preferred operation region flow with the rated impeller diameter.
Note on C131: Specify the proposed pump end of preferred operation region flow with the rated impeller diameter.
Note on C132: Specify the proposed pump start of allowable operation region flow with the rated impeller diameter.
Note on C133: Specify the proposed pump end of allowable operation region flow with the rated impeller diameter.
Note on C134: Specify the proposed pump maximum head with the rated impeller diameter.
Note on C135: Specify the proposed pump maximum power absorbed with the rated impeller diameter.
Note on C136: Specify the proposed pump NPSH3 at the rated flow.
Note on C137: Specify the proposed pump NPSH3 at 120 % of the rated flow.
Note on C138: Specify the proposed pump NPSHA-NPSH3 margin at the rated flow.
Note on C139: Specify the proposed pump NPSHA-NPSH3 margin in the allowable operating region.
Note on C140: Specify the proposed pump specific speed.
Note on C141: Specify the proposed pump suction-specific speed.
Note on C142: Specify the proposed pump maximum allowable sound pressure level.
Note on C143: Specify the proposed pump maximum allowable sound power level.
Note on C145: Select the proposed pump type.
Note on C146: Select the proposed pump type mounting.
Note on C147: Select the proposed pump casing type.
Note on C148: Select the proposed pump impeller type.
Note on C149: Select the proposed pump rotation (viewed from the coupling end).
Note on C150: Select whether the proposed pump rotating components are required to be dynamically balanced to ISO 21940-11, Grade G1.0.
Note on C151: Specify the proposed pump impeller number of vanes.
Note on C152: Specify the proposed pump suction nozzle flange size.
Note on C153: Select the proposed pump suction nozzle flange facing.
Note on C154: Select the proposed pump suction nozzle flange rating.
Note on C155: Select the proposed pump suction nozzle flange position.
Note on C156: Specify the proposed pump discharge nozzle flange size.
Note on C157: Select the proposed pump discharge nozzle flange facing.
Note on C158: Select the proposed pump discharge nozzle flange rating.
Note on C159: Select the proposed pump discharge nozzle flange position.
Note on C160: Select the proposed pump suction and discharge nozzle allowable forces and moments requirements sources.
Note on C161: Select the proposed pump auxiliary process-liquid piping construction required.
Note on C162: Select whether connection design approval prior to fabrication is required for the proposed pump. Applicable to any pump with welded connections.
Note on C163: Specify the proposed pump pressure casing drain size required.
Note on C164: Specify the proposed pump pressure casing vent size required.
Note on C165: Select whether a separate warm-up or cooldown line is required for instantaneous start-up of the pump.
Note on C166: Select whether machined and studded connections are required for the proposed pump casing.
Note on C167: Select the specification required for pipe threads for the proposed pump casing, if in pipeline service with maximum operating temperature below 130 °F (55 °C), if accepted.
Note on C168: Specify the proposed pump maximum allowable working temperature.
Note on C169: Specify the proposed pump maximum allowable working pressure.
Note on C170: Select the pump bearing housing cooling method required. Only applicable when cooling is required. Default value : fan
Note on C171: Select the pump cooling water plan required. Refer to Annex B for piping plans.
Note on C172: Select whether heat tracing and/or insulation is required to be applied to the pump.
Note on C173: Select the purpose of insulation.
Note on C174: Specify where heat tracing and insulation is to be applied.
Note on C175: Select who is responsible for supplying and installing heat tracing and/or insulation on the proposed pump.
Note on C176: Select the required heat tracing and/or insulation specification for the proposed pump. Only applicable if heat tracing or insulation is required.
Note on C177: Specify the proposed pump package estimated mass.
Note on C178: Select whether the proposed pump shaft flexibility index is required. Shaft flexibility index possible requirement applies to type OH2 pumps only.
Note on C179: Specify the proposed pump shaft flexibility index.
Note on C180: Select whether an OH3 back-pullout lifting device is required.
Note on C181: Select whether shrink fit limited movement impellers are required for the proposed pump.
Note on C183: Specify the proposed pump discharge head MAWP. Applicable to API pump types VS1, VS2, VS3, VS4 (flanged or vapor-tight mounting/cover plate), VS5 (flanged or vapor-tight mounting/cover plate), VS6 and VS7.
Note on C184: Specify the proposed pump column MAWP. Applicable to API pump types VS4 (discharge elbow and pipe), VS5 (discharge elbow and pipe), VS6 and VS7 when hydrostatic test is specified.
Note on C185: Specify the proposed pump bowl MAWP. Applicable to API pump types VS4 (casing and suction cover), VS5 (casing and suction cover), VS6 and VS7 when hydrostatic test is specified.
Note on C186: Specify the proposed pump suction barrel or can MAWP. Applicable to API pump types VS6 and VS7.
Note on C187: Select the required location for the pump thrust bearing.
Note on C188: Specify the suction strainer type required for the proposed pump. Applicable when required to API pump types VS1, VS4 and VS5.
Note on C189: Select the type of level control required for the proposed pump. Applicable when required to API pump types VS1, VS4 and VS5.
Note on C190: Select the type of line shaft connection required for the proposed pump.
Note on C191: Select the line shaft configuration required for the proposed pump. Applicable to API pump types VS1 and VS2.
Note on C192: Select the type of line shaft bearing lubrication required for the proposed pump. Applicable to API pump types VS1, VS2 and VS4.
Note on C193: Specify the quantity of line shaft bearings required for the proposed pump.
Note on C194: Select whether hardened sleeves under line shaft bearings are required for the proposed pump. Applicable to API pump types VS1, VS2, VS6 and VS7.
Note on C196: Specify the grade (underside of pump mounting plate or top of foundation) elevation at which the proposed pump is to be installed.
Note on C197: Specify the process liquid low level elevation.
Note on C198: Specify the sump floor elevation.
Note on C199: Specify the diameter of the sump in which the proposed pump will be installed.
Note on C200: Specify the grade to top of proposed pump discharge connection dimension.
Note on C201: Specify the proposed pump length (grade to underside of pump inlet bell or strainer dimension) below grade.
Note on C202: Specify the grade to the proposed pump first stage impeller centerline dimension.
Note on C203: Specify the grade to pump process liquid minimum submergence level dimension.
Note on C205: Select the proposed pump radial bearing type.
Note on C206: Select the proposed pump thrust bearing type.
Note on C207: Select whether the trust bearing size for the proposed pump is required to be reviewed and accepted. Applicable to API pump types BB1, BB2 and BB3.
Note on C208: Select whether the rolling element bearing life calculations are required for the proposed pump bearing arrangement.
Note on C209: Select the lubrication method for the proposed pump bearings.
Note on C210: Specify the oil viscosity ISO grade for the proposed pump bearings.
Note on C211: Select the oil type required for the proposed pump bearings.
Note on C212: Specify the grease type required for the proposed pump bearings.
Note on C213: Specify the grease grade for the proposed pump bearings.
Note on C214: Specify the bearing housing sealing type/model for the proposed pump.
Note on C215: Select who is responsible for supplying oil mist directional reclassifiers for the proposed pump.
Note on C217: Select the API Standard 610, Table H.1 materials of construction required for the proposed pump.
Note on C218: Specify the minimum design metal temperature of the proposed pump.
Note on C219: Select whether reduced-hardness materials are required for the proposed pump.
Note on C220: Select the applicable hardness standard for the proposed pump.
Note on C221: Select whether special coating for impellers and other wetted parts are required for the proposed pump.
Note on C222: Specify the casing and casing cover materials of construction required for the proposed pump.
Note on C223: Specify the nonwetted pressure-retaining fasteners materials of construction required for the proposed pump.
Note on C224: Specify the diffuser materials of construction required for the proposed pump.
Note on C225: Specify the impeller materials of construction required for the proposed pump.
Note on C226: Specify the inducer materials of construction required for the proposed pump.
Note on C227: Select the impeller wear component type required for the proposed pump.
Note on C228: Specify the impeller wear component materials of construction required for the proposed pump.
Note on C229: Specify the impeller wear component hardness required for the proposed pump.
Note on C230: Specify the case wear ring materials of construction required for the proposed pump.
Note on C231: Specify the wear parts hardnesses required for the proposed pump.
Note on C232: Specify the shaft materials of construction required for the proposed pump.
Note on C233: Select the auxiliary process-liquid lines, fittings and other connections to casing, including seal plans materials of construction required for the proposed pump.
Note on C235: Specify the suction barrel/can materials of construction required for the proposed pump. Relates to API pump types VS6 and VS7.
Note on C236: Specify the discharge head materials of construction required for the proposed pump. Relates to API pump types VS1, VS2, VS3, VS6 and VS7.
Note on C237: Specify the discharge column materials of construction required for the proposed pump. Relates to API pump types VS1, VS2, VS3, VS6 and VS7.
Note on C238: Specify the head column materials of construction required for the proposed pump. Relates to API pump types VS4 and VS5.
Note on C239: Specify the discharge elbow and pipe materials of construction required for the proposed pump. Relates to API pump types VS4 and VS5 pumps.
Note on C240: Specify the bowl/casing materials of construction required for the proposed pump. Relates to API pump types VS1, VS2, VS3, VS4 (casing), VS5 (casing), VS6 and VS7.
Note on C241: Specify the bellmouth/suction cover materials of construction required for the proposed pump. Relates to API pump types VS1, VS2, VS3, VS4 (suction cover), VS5 (suction cover), VS6 and VS7 pumps.
Note on C242: Specify the strainer materials of construction (if fitted) required for the proposed pump. Relates to API pump types VS1, VS2, VS4 and VS5.
Note on C243: Specify the line shaft materials of construction required for the proposed pump.
Note on C244: Specify the shaft enclosing tube materials of construction required for the proposed pump.
Note on C245: Specify the bowl shaft materials of construction required for the proposed pump. Relates to API pump types VS1, VS2, VS3, VS6 and VS7.
Note on C246: Specify the process wetted fasteners materials of construction required for the proposed pump.
Note on C247: Specify the bearing retainer or spider materials of construction required for the proposed pump.
Note on C248: Specify the line shaft bearing materials of construction required for the proposed pump.
Note on C249: Specify the line shaft hard facing materials of construction required for the proposed pump.
Note on C250: Specify the line shaft sleeves materials of construction required for the proposed pump.
Note on C251: Specify the bearing lubrication lines materials of construction required for the proposed pump. Relates to API pump types VS4 and VS5.
Note on C252: Specify the bowl bearing materials of construction required for the proposed pump. Relates to API pump types VS1, VS2, VS3, VS6 and VS7.
Note on C254: Select the material inspection requirements for the proposed pump.
Note on C255: Select the inspection class based on hazardous service and the design parameters outside the limits of Table 14.
Note on C256: Select the impact test standard required for the proposed pump.
Note on C257: Select whether hardness testing of parts, welds and heat-affected zones is required for the proposed pump. Hardness testing of sour service wetted parts, welds and heat-affected zones is already mandated.
Note on C258: Select whether any additional surface/sub-surface examination is required for the proposed pump.
Note on C259: Specify the proposed pump components to be subjected to additional surface/sub-surface examination. This is to describe the parts or areas that require additional examination.
Note on C260: Select the type of surface examination required for the proposed pump components to be subjected to additional surface/sub-surface examination.
Note on C261: Select the type of sub-surface examination required for the proposed pump components to be subjected to additional surface/sub-surface examination.
Note on C262: Specify the proposed pump additional components to be subjected to PMI testing.
Note on C263: Select the PMI standard for the proposed pump.
Note on C264: Select whether the vendor is required to keep repair and heat treatment records for the proposed pump.
Note on C266: Select the API baseplate number for the proposed pump.
Note on C267: Select whether the proposed pump baseplate is required to be sized to accommodate seal piping systems.
Note on C268: Select the required baseplate type for the proposed pump.
Note on C269: Select the required baseplate mounting for the proposed pump.
Note on C270: Select whether stainless steel plates, thickness 0.2 in. (5 mm) minimum, under all pump feet are required for the proposed pump,
Note on C272: Specify the API Standard 682 mechanical seal code required for the proposed pump.
Note on C273: Select whether an API Standard 682 mechanical seal data sheet is required for the proposed pump.
Note on C274: Select the mechanical seal primary piping plan required for the proposed pump.
Note on C275: Select the mechanical seal primary piping plan construction required for the proposed pump.
Note on C276: Select the mechanical seal secondary piping plan required for the proposed pump.
Note on C277: Specify, if applicable, the mechanical seal tubing fittings manufacturer required for the proposed pump.
Note on C278: Select whether an additional, centrally located, flush port on the top of the mechanical seal gland plate is required for the proposed pump.
Note on C279: Select whether a mechanical seal heating jacket is required for the proposed pump.
Note on C280: Specify the mechanical seal maximum static sealing pressure for the proposed pump.
Note on C281: Specify the mechanical seal minimum static sealing pressure for the proposed pump.
Note on C282: Specify the mechanical seal maximum dynamic sealing pressure for the proposed pump.
Note on C283: Specify the mechanical seal minimum dynamic sealing pressure for the proposed pump.
Note on C284: Specify the mechanical seal maximum design temperature for the proposed pump.
Note on C285: Specify the mechanical seal maximum design temperature for the proposed pump.
Note on C287: Specify the required coupling specification for the proposed pump. Coupling specifications could include ISO 14691, ISO 10441, API Standard 610, IOGP S-700, vendors standard. Default value : API Standard 610
Note on C288: Specify the manufacturer of the coupling for the proposed pump.
Note on C289: Specify the coupling type/model/size required for the proposed pump.
Note on C290: Specify the coupling rating power/100 rpm for the proposed pump.
Note on C291: Select the required coupling component balance grade for the proposed pump.
Note on C292: Select whether the coupling hubs for the proposed pump are required to be fitted hydraulically.
Note on C293: Select whether the coupling hubs for the proposed pump is required be fitted with a proprietary clamping device. Default value : not required
Note on C294: Specify the required coupling guard specification for the proposed pump. Coupling guard specifications could include ISO 14120, ANSI B11.19, EN 953.
Note on C295: Specify the coupling and exposed shaft guard materials required for the proposed pump. Include generic material and material specification.
Note on C297: Select the driver type required for the proposed pump.
Note on C298: Specify the required driver specification. This could include IEC 60034-1, IEEE 841, API 547, API 541, IOGP S-703, IOGP S-704, IOGP S-733D. Steam turbine specifications could include API 611. Diesel engine specifications could include IOGP S-711.
Note on C299: Specify the manufacturer of the driver for the proposed pump.
Note on C300: Select how the driver of the proposed pump is required to be rated.
Note on C301: Select whether and how the driver should be rated for water test. Applicable for pump water testing with contract driver for applications with relative density much less than 1.
Note on C302: Specify the driver frame or model required for the proposed pump.
Note on C303: Specify the driver nameplate power for the proposed pump.
Note on C304: Specify the driver nominal speed for the proposed pump.
Note on C305: Specify the driver rated load speed for the proposed pump.
Note on C306: Select the driver lubrication method for the proposed pump.
Note on C307: Select the driver radial bearing type for the proposed pump.
Note on C308: Select the driver thrust bearing type for the proposed pump.
Note on C309: Select the motor starting method required for the proposed pump.
Note on C310: Select whether adjustable speed drive is required for the proposed pump. Applicable to electrical ASD, fluid coupling, magnetically coupled ASD, steam turbine, diesel engine and HPRT drives.
Note on C311: Select the source of adjustable speed drive for the proposed pump. Applicable to electrical ASD, fluid coupling, magnetically coupled ASD, steam turbine, diesel engine and HPRT drives.
Note on C312: Specify the required trip speed if adjustable speed drive is specified for the proposed pump. Applicable to electrical ASD, fluid coupling, magnetically coupled ASD, steam turbine, diesel engine and HPRT drives.
Note on C313: Select whether a gear is required for the proposed pump.
Note on C314: Specify the required gear specification for the proposed pump. Gear specifications could include API Standard 677, IOGP S-712.
Note on C315: Specify the manufacturer of the gear/adjustable speed drive for the proposed pump.
Note on C317: Select whether accelerometers are required for the proposed pump.
Note on C318: Specify the number of accelerometers required for the proposed pump.
Note on C319: Specify the required mounting locations for the accelerometers for the proposed pump.
Note on C320: Select whether only threaded provision for mounting accelerometers is required for the proposed pump.
Note on C321: Select whether only flat surfaces for mounting portable magnetic type accelerometers are required for the proposed pump.
Note on C322: Select whether vibration proximity probes are required for the proposed pump.
Note on C323: Specify the number of vibration proximity probes per radial bearing required for the proposed pump.
Note on C324: Specify the required mounting locations for the vibration proximity probes for the proposed pump.
Note on C325: Select whether only threaded provision for mounting vibration proximity probes is required for the proposed pump.
Note on C326: Select whether only flat surface provision for mounting portable magnetic type vibration proximity probes are required for the proposed pump.
Note on C327: Select whether a one-event-per-revolution probe (key phasor) is required for the proposed pump.
Note on C328: Select whether temperature probes are required for the proposed pump.
Note on C329: Specify the number of temperature probes per radial bearing required for the proposed pump.
Note on C330: Specify the required mounting locations for the temperature probes for the proposed pump.
Note on C331: Select whether only provision for mounting temperature probes is required for the proposed pump.
Note on C332: Select whether temperature gauges (and thermowells) are required for the proposed pump. Applicable to API pump type OH6.
Note on C333: Select who is responsible for supplying and installing vibration and temperature instrument monitors and cables on the proposed pump.
Note on C335: Select whether the proposed VS6/VS7 pump bowls and column are required to be hydrostatically tested.
Note on C336: Select the residual unbalance test method required for the proposed pump. Applicable to API pump types BB1, BB2 and BB3.
Note on C337: Select whether a cleanliness check prior to final assembly is required for the proposed pump.
Note on C338: Select whether a nozzle load test is required for the proposed pump.
Note on C339: Select whether a structural resonance test is required for the proposed vertical suspended pump. Only applicable when API pump type is VS.
Note on C340: Select whether the contract or shop driver is to be used for testing.
Note on C341: Select whether a notification of successful shop performance test is required for the proposed pump.
Note on C342: Select whether the performance test NPSHA limited to 110 % site NPSHA is required for the proposed pump.
Note on C343: Select whether the performance test at minimum submergence for vertical submerged pumps is required for the proposed pump. Applicable to API pump types VS1, VS2, VS3, VS4 and VS5.
Note on C344: Select the required vibration test measurement locations for the proposed pump.
Note on C345: Select whether a retest is required after the final head adjustment of a multistage pump.
Note on C346: Select whether the mechanical run test is required to continue until stabilization of the bearing oil temperature, especially for higher energy pumps with hydrodynamic bearings.
Note on C347: Select whether the pump is to be mechanically run at the rated flow for 4 hours after the bearing oil temperature stabilizes, especially for higher energy pumps with hydrodynamic bearings.
Note on C348: Select the NPSH required testing scope, if any, for the proposed pump. For vertical submerged pumps, a minimum submergence test is to be performed in lieu of an NPSH required test if it is more restrictive.
Note on C349: Select the type of NPSH required test, if any, for the proposed pump.
Note on C350: Select the NPSH required test specification, if any, for the proposed pump.
Note on C351: Select the complete unit testing scope, if any, for the proposed pump.
Note on C352: Specify the required duration of the complete unit test for the proposed pump. Only applicable if a complete unit test is required.
Note on C353: Select whether a sound level test is required for the proposed pump.
Note on C354: Select whether any auxiliary equipment shop testing is required for the proposed pump.
Note on C355: Specify the proposed pump auxiliary equipment to be shop tested. Only applicable when auxiliary equipment testing is specified.
Note on C356: Select whether a bearing housing resonance test is required for the proposed pump.
Note on C357: Select whether the proposed pump is required to be disassembled after completion of the running tests. Default value : not required
Note on C358: Select whether the proposed pumps hydrodynamic bearings are to be removed and inspected after completion of the running tests.
Note on C360: Specify the required surface preparation and painting specification for the proposed pump. Surface preparation and painting specifications could include vendor's standard, API Standard 610, IOGP S-715, purchaser's standard.
Note on C362: Select whether a steady state forced response analysis is required for the proposed pump.
Note on C363: Select whether a transient forced response analysis is required for the proposed pump.
Note on C364: Select whether a torsional analysis report is required for the proposed pump.
Note on C365: Select whether a lateral analysis is required for the proposed pump.
Note on C367: Select whether a commissioning and start-up spares quotation is required for the proposed pump. Default value : required
Note on C368: Select whether a normal maintenance spares quotation is required for the proposed pump. Default value : not required
Note on C369: Select whether a two-year operating spares quotation is required for the proposed pump. Default value : not required
Note on C370: Select whether a capital spares quotation is required for the proposed pump.
Note on C371: Select the required spare rotor storage orientation for the proposed pump.
Note on C372: Select whether a shipping and storage container for vertical storage of spare rotor is required for the proposed pump.
Note on C373: Select whether an inert gas purge for the spare rotor container is required for the proposed pump.
Note on C375: Specify the required preservation and packing specification for the proposed pump. Preservation and packing specifications could include vendor's standard, API Standard 610, purchaser's standard.
Note on C376: Select what the preservation and packing specification for the proposed pump is to be suitable for.
Note on C377: Select whether export boxing is required for the proposed pump.
Note on C378: Select whether outdoor storage is required and for what duration for the proposed pump.

## Supplement
Row |  | IOGP S-615D (2.01) Procurement Data Sheet for Centrifugal Pumps (API) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-615D (2.01) Procurement Data Sheet for
Centrifugal Pumps (API)
Guidance on the use of this procurement data sheet
To be used in conjunction with :
IOGP S-615 Supplementary Specification to API Standard 610 for Centrifugal Pumps.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data