## Front & Preliminaries
|  |  | SPECIFICATION | January 2026
|  |  | IOGP S-753D | Version 1.0
Procurement Data Sheet for Battery Energy Storage Systems (BESS) (IEC)
Revision history
VERSION | DATE | PURPOSE
1 | January 2026 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-753D (1.0) Procurement Data Sheet for Battery Energy Storage Systems (BESS) (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-753D (1.0) Procurement Data Sheet for Battery Energy Storage Systems (BESS) (IEC)
Introduction
The purpose of this procurement data sheet (PDS) is to specify purchaser-specific requirements for the procurement of battery energy storage systems (BESSs) in accordance with IOGP S-753 for application in the petroleum and natural gas industries.
The PDS provides requirements where the specification requires the purchaser to define an application-specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser-supplied documents can be listed in the PDS to define scope and technical requirements for enquiry and purchase of the equipment.
The IOGP S-753 specification documents follow a common structure (as shown below) comprising a specification, also known as a technical requirements specification (TRS), this PDS, an information requirements specification (IRS) and a quality requirements specification (QRS). These four specification documents, together with the purchase order, define the overall technical specification for procurement.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)
This PDS is to be applied in conjunction with the specification, the IRS and the QRS, referred to in this document as IOGP S-753, IOGP S-753L and IOGP S-753Q respectively. Further information on the purpose of these documents and the order of precedence for their use is provided in the introduction of the specification.

## Procurement Data Sheet
Row | IOGP S-753D (1.0) Procurement Data Sheet for Battery Energy Storage Systems (BESS) (IEC) | [6 empty] | Issue
2 | Ref. clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | BESS tag number : | input data |  | input data
5 |  | BESS tag description : | input data |  | input data
6 | 7.5,Note | Purchase order reference and date : | input data |  | input data
7 |  | Project requirements
8 | 5.2.3.1 | Project country : | input data |  | input data
9 | 5.2.4.1,8.3.1.1,8.3.2.6,9.1.1,9.2.1 | Project region : | input data |  | input data
10 | 5.3.1,5.3.2,5.4.1,Figure 4 | Service life : | 10 | years | 10 | years |  |  |  |  | select | 10 | 15 | other
11 | 4.2.4,5.2.2.2,5.5.1.4,8.3.1.1,8.3.2.6,9.1.1,9.2.1 | Local codes or regulatory standards : | input data |  | input data
12 | 4.2.4,5.2.2.1,5.2.2.3,5.5.1.4,5.5.3 | Grid codes : | input data |  | input data
13 | 5.7.1.1 | LV AC switchgear : | select |  | select | [5 empty] | select | manufacturer's standard | other
14 | 5.7.1.1 | LV DC switchgear : | select |  | select | [5 empty] | select | manufacturer's standard | other
15 | 10 | HV AC switchgear : | select |  | select | [5 empty] | select | manufacturer's standard | other
16 | 5.7.1.1 | Isolation or coupling transformer upstream of BESS (PCS) : | not required |  | not required | [5 empty] | select | required | not required
17 | 5.7.3.1 | Isolation or coupling transformer : | select |  | select | [5 empty] | select | manufacturer's standard | other
18 | 5.7.1.1,5.7.3.1 | Distribution transformer : | select |  | select | [5 empty] | select | manufacturer's standard | other
19 | 5.8.1,5.8.2,5.8.3 | Certification marine/offshore : | not required |  | not required | [5 empty] | select | not required | DNV | Lloyds | ABS | USCG | nationally recognized testing laboratory (NRTL) | other
20 |  | Paint colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
21 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
22 |  | Site acceptance testing conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D | not required
23 |  | Installation
24 | 5.2.1,5.2.3.3,5.8.1,5.8.3,9.2.2 | Site : | select |  | select | [5 empty] | select | onshore | offshore - fixed | offshore - floating | marine (ship) | other
25 | 5.2.1,5.2.3.3,9.2.1,9.2.2 | Location of installation : | outdoor |  | outdoor | [5 empty] | select | indoor | outdoor | other
26 |  | Environmental conditions - design and operation
27 | 5.1,5.2.1,5.2.3.3,8.3.1.8,9.2.2 | Minimum ambient temperature : | ≥ −10 | °C | ≥ −10 | °C |  |  |  |  | select | ≥ −10 | ≥ −25 | ≥ −40 | other
28 | 5.1,5.2.1,5.2.3.3,8.3.1.8,9.2.2 | Maximum ambient temperature : | ≤ 40 | °C | ≤ 40 | °C |  |  |  |  | select | ≤ 40 | other
29 | 5.1,5.2.1,5.2.3.3,8.3.1.8,9.2.2 | Average ambient temperature : | ≤ 35 | °C | ≤ 35 | °C |  |  |  |  | select | ≤ 35 | other
30 | 5.1,5.2.1,5.2.3.3,8.3.1.8,9.2.2 | Design ambient temperature : | ≤ 40 | °C | ≤ 40 | °C |  |  |  |  | select | ≤ 40 | other
31 | 5.1,5.2.1,5.2.3.3,8.3.1.8,9.2.2 | Solar radiation intensity : | select | W/m2 | select | W/m2 |  |  |  |  | select | negligible | ≤ 500 (low) | < 500 to ≤ 700 (medium) | < 700 to ≤ 1120 (high) | other
32 | 5.1,5.2.1,5.2.3.3,8.3.1.8,9.2.2 | Maximum altitude : | ≤ 1 000 | m | ≤ 1 000 | m |  |  |  |  | select | ≤ 1 000 | other
33 | 5.1,5.2.1,5.2.3.3,8.3.1.8,9.2.2 | Non-condensing relative humidity - 24 h average : | ≤ 95 | % | ≤ 95 | % |  |  |  |  | select | ≤ 95 | other
34 | 5.1,5.2.1,5.2.3.3 | Condensation and precipitation : | no |  | no | [5 empty] | select | yes | no
35 | 5.1,5.2.1,5.2.3.3,5.2.3.4,5.2.3.5,5.2.3.6,5.4.1,5.8.3,9.2.2,B.3 | Special environmental conditions : | input data |  | input data
36 | Table 11 | Outdoor battery cabinet IP rating : | IP55 |  | IP55 | [5 empty] | select | IP55 | other
37 | 11.4,11.5,5.2.3.4,5.2.3.5,5.2.3.6 | Environmental contamination : | none |  | none | [5 empty] | select | none | salt-laden | H2S | salt-laden and H2S | other
38 | 5.1,5.2.1,5.2.3.2 | Seismic activity zone in accordance with IEC 60721-2-6 : | select |  | select | [5 empty] | select | Zone 1 | Zone 2 | Zone 3 | Zone 4 | not applicable | other
39 |  | Environmental conditions - transportation and storage
40 | 11.1,11.2,11.3,11.4,11.5 | Minimum ambient temperature - transportation and storage : | ≥ −10 | °C | ≥ −10 | °C |  |  |  |  | select | ≥ −10 | ≥ −25 | ≥ −40 | other
41 | 11.1,11.2,11.3,11.4,11.5 | Maximum ambient temperature - transportation and storage : | ≤ 40 | °C | ≤ 40 | °C |  |  |  |  | select | ≤ 40 | other
42 | 11.1,11.2,11.3,11.4,11.5 | Maximum non-condensing relative humidity - transportation and storage : | ≤ 95 | % | ≤ 95 | % |  |  |  |  | select | ≤ 95 | other
43 | 11.1,11.2,11.3,11.4,11.5 | Equipment preservation during transportation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
44 | 11.1,11.2,11.3,11.4,11.5 | Storage site : | select |  | select | [5 empty] | select | indoor - climate controlled (humidity and temperature) | indoor - temperature controlled only | indoor - natural ventilation | outdoor | other
45 | 11.1,11.2,11.3,11.4,11.5 | Additional or unusual conditions - transportation and storage : | input data |  | input data
46 | 11.4 | Anticondensation heater for transport and storage : | not required |  | not required | [5 empty] | select | required | not required
47 |  | Power system interface parameters
48 | 5.2.1,5.2.2.1 | Nominal voltage : | input data | kV | input data | kV
49 | 5.2.1,5.2.2.1 | Steady state voltage variation : | ±10 | kV | ±10 | kV |  |  |  |  | select | ±10 | other
50 | 5.2.1,5.2.2.1 | Temporary voltage variation : | input data | select | input data | select |  |  |  |  | select | % | min
51 | 5.2.1,5.2.2.1 | Nominal frequency : | 50 | Hz | 50 | Hz |  |  |  |  | select | 50 | 60
52 | 5.2.1,5.2.2.1 | Steady state frequency variation : | ±1 | Hz | ±1 | Hz |  |  |  |  | select | ±1 | other
53 | 5.2.1,5.2.2.1 | Temporary frequency variation : | input data | select | input data | select |  |  |  |  | select | % | min
54 | 5.2.1,5.2.2.1 | Minimum and maximum short circuit current : | input data | kA | input data | kA
55 | 5.2.1,5.2.2.1 | System earthing : | select |  | select | [5 empty] | select | solidly earthed neutral | impedance earthed neutral | isolated neutral | other
56 | 5.2.2.3 | Individual harmonic distortion of voltage compatibility level : | Class 2 |  | Class 2 | [5 empty] | select | Class 1 | Class 2 | Class 3
57 | 5.2.2.3 | Total harmonic distortion of voltage compatibility level : | Class 2 |  | Class 2 | [5 empty] | select | Class 1 | Class 2 | Class 3
58 |  | Auxiliary power supply parameters
59 | Figure 1 c | Source of auxiliary power supply : | externally derived |  | externally derived | [5 empty] | select | internally derived | externally derived
60 | 5.4.4 | Nominal voltage : | input data | V | input data | V
61 | 5.4.4 | Steady-state voltage variation : | ±10 | % | ±10 | % |  |  |  |  | select | ±10 | other
62 | 5.4.4 | Nominal frequency : | 50 | Hz | 50 | Hz |  |  |  |  | select | 50 | 60
63 | 5.4.4 | Steady state frequency variation : | ±1 | Hz | ±1 | Hz |  |  |  |  | select | ±1 | other
64 | 5.4.4 | Available short-circuit current auxiliary power : | input data | kA | input data | kA
65 | 5.4.4 | System earthing : | select |  | select | [5 empty] | select | solidly earthed neutral | impedance earthed neutral | isolated neutral | other
66 |  | BESS safety
67 | 7.2 | Additional language for safety labels and markings : | input data |  | input data
68 | 7.7 | Maximum acoustic noise level at a distance of 1 m : | manufacturer's standard | dBA | manufacturer's standard | dBA |  |  |  |  | select | manufacturer's standard | other
69 |  | Hazard identification and risk analysis documentation : | not required |  | not required | [5 empty] | select | not required | required
70 |  | System risk reduction measures documentation : | not required |  | not required | [5 empty] | select | not required | required
71 |  | BESS design data
72 | 7.1,Table 9 | BESS category : | select |  | select | [5 empty] | select | V-H E-L S-U C-A | other
73 | 5.1,5.2.1,5.4.1,5.5.1.2 | BESS application : | select |  | select | [5 empty] | select | Class A - frequency regulation | Class A - reduction of power fluctuation | Class A - voltage regulation | Class B - peak shaving / peak shifting | Class C - back-up power | other
74 | 4.2.4,5.5.2,5.5.3,5.5.4 | Operation states required : | input data |  | input data
75 | 5.1,5.3.1,5.4.2 | Rated active input power : | input data | select | input data | select |  |  |  |  | select | kW | MW
76 | 5.1,5.3.1,5.4.2 | Rated reactive input power : | input data | select | input data | select |  |  |  |  | select | kVAR | MVAR
77 | 5.1,5.3.1,5.4.2 | Rated active output power : | input data | select | input data | select |  |  |  |  | select | kW | MW
78 | 5.1,5.3.1,5.4.2 | Rated reactive output power : | input data | select | input data | select |  |  |  |  | select | kVAR | MVAR
79 | 5.5.1.2 | BESS functional description : | input data |  | input data
80 |  | BESS duty cycle
81 | 5.1,5.3.1 | BESS duty cycle profile and description : | input data |  | input data
82 |  | Accumulation subsystem (secondary batteries)
83 | 8.1,Table 9 | Battery chemistry : | lithium iron phosphate - LFP (LiFePO4) |  | lithium iron phosphate - LFP (LiFePO4) | [5 empty] | select | lithium iron phosphate - LFP (LiFePO4) | lithium nickel manganese cobalt oxide - NMC (LiNiMnCoO2) | other
84 | 8.3.1.1,8.3.2.1,8.4.1 | Battery housing : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
85 | 8.3.1.1,8.3.1.2,8.3.1.7 | Fire resistance rating for battery housing : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | A0 | A60 | A120 | other
86 |  | Power conversion subsystem
87 | 8.3.1.1 | PCS housing : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
88 |  | Fire and gas system
89 | 9.1.1 | Integrated fire suppression system for battery housing : | required |  | required | [5 empty] | select | required | not required | other
90 | B.2 | Fire and gas audible alarm : | not required |  | not required | [5 empty] | select | required | not required
91 | 8.3.2.6,8.3.2.7 | Externally mounted high-visibility strobe light : | not required |  | not required | [5 empty] | select | required | not required
92 |  | Communication interfaces
93 | 4.2.4,5.6.2,5.6.3.1,Table 3 | BESS message category for remote monitoring and control : | category II |  | category II | [5 empty] | select | category I | category II | category III
94 | 4.2.4,5.6.3.1,5.6.3.3 | Interface media for ECMS/PMS : | Ethernet (fiber) |  | Ethernet (fiber) | [5 empty] | select | not required | hardwired discrete | serial | Ethernet (Cu) | Ethernet (fiber) | wireless | RS-485 | other
95 | 4.2.4,5.6.3.1,5.6.3.3 | Interface protocol for ECMS/PMS : | Ethernet IP |  | Ethernet IP | [5 empty] | select | not applicable | potential free contact | RS-485 | Modbus TCP/IP | Modbus RTU | Profinet | Ethernet IP | other
96 | 4.2.4,5.6.3.1,5.6.3.3 | Interface network redundancy for ECMS/PMS : | not required |  | not required | [5 empty] | select | not required | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
97 | 4.2.4,5.6.3.1,5.6.3.3 | BESS remote access : | required |  | required | [5 empty] | select | required | not required
98 | 5.6.1 | Interface media for external FGS : | hardwired discrete |  | hardwired discrete | [5 empty] | select | hardwired discrete | other
99 | 5.6.1 | Interface protocol for external FGS : | not applicable |  | not applicable | [5 empty] | select | not applicable | potential free contact | Ethernet IP | other
100 | 4.2.4 | Interface media for external ESD system : | not required |  | not required | [5 empty] | select | not required | hardwired discrete | other
101 | 4.2.4 | Interface protocol for external ESD system : | not applicable |  | not applicable | [5 empty] | select | not applicable | potential free contact | other
102 | 4.2.4,5.6.3.1,5.6.3.3 | Hardware for remote access : | required |  | required | [5 empty] | select | required | not required
103 |  | Interconnecting cables
104 | 5.7.3.1 | Interconnecting cables between BESS equipment or subsystems : | required |  | required | [5 empty] | select | required | not required
105 | 5.7.3.1 | Cable type : | input data |  | input data
106 |  | Additional scope of supply
107 | 10 | HV switchgear and associated devices upstream of BESS (PCS) : | not required |  | not required | [5 empty] | select | required | not required
108 | 8.3.1.1,8.4.1 | Door locking provisions : | manufacturer standard locking facility |  | manufacturer standard locking facility | [5 empty] | select | manufacturer's standard locking facility | padlockable | hasp and padlock | other
109 |  | Transport, storage and handling
110 | 11.1,11.2,11.3,11.4,11.5 | Transport, storage and handling : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
111 | 8.2.1 | Quantity of portable battery module lifting trolley required : | not required |  | not required | [5 empty] | select | not required | 1 | 2 | other
Note on C4: Specify the unique tag number of the BESS.
Note on C5: Specify the functional description of the BESS.
Note on C6: Specify the purchase order reference and date. If there is no data to specify, input "not applicable".
Note on C8: Specify the country where the project is located in accordance with ISO 3166-1. This information is necessary for the supplier to provide the appropriate product marking and certification for the region.
Note on C9: Specify the geographic location, within the country, which will determine the applicability of local regulatory requirements.
Note on C10: Select the required service life of the BESS in accordance with the project design basis, ensuring that the supplier can design the system accordingly. If "other" is selected, specify details in the "Additional notes" column. Default value : 10
Note on C11: Specify the relevant local codes, regulatory standards, greenhouse policies, or company-specific requirements. If there is a document that encompasses all codes or standards, specify the document number in the "Additional notes" column.
Note on C12: Specify the applicable grid codes that the BESS should adhere to. If there is a document that encompasses all codes or standards, specify the document number in the "Additional notes" column.
Note on C13: Select the low-voltage (LV) AC switchgear standard. If "other" is selected, specify details in the "Additional notes" column.
Note on C14: Select the low-voltage (LV) DC switchgear standard. If "other" is selected, specify details in the "Additional notes" column.
Note on C15: Select the high-voltage (HV) AC switchgear standard. If "other" is selected, specify details in the "Additional notes" column.
Note on C16: Select whether the isolation or coupling transformer upstream of the BESS power conversion subsystem (PCS) is to be supplied as part of the BESS package. Default value : not required
Note on C17: Select the isolation of coupling transformer standard. If "other" is selected, specify details in the "Additional notes" column.
Note on C18: Select the distribution transformer standard. If "other" is selected, specify details in the "Additional notes" column.
Note on C19: Select the required marine/offshore certification authority that the BESS should adhere to. Applicable for marine/offshore installations. If "other" is selected, specify details in the "Additional notes" column. Default value : not required
Note on C20: Select the BESS equipment external paint colour. If "other" is selected, specify the required painting standard (e.g. RAL, MUNSSEL, ANSI) in the "Additional notes" column. The marking of the logo may not be required on the external housing. Default value : manufacturer's standard
Note on C21: Select the CAS level to be applied in IOGP S-753Q, Annex A. CAS D requires the fewest quality interventions and information requirements. Default value : D
Note on C22: Select the CAS level to be applied in IOGP S-753Q, Annex A for site acceptance testing. Default value : D
Note on C24: Select the location of the facility where the BESS will be permanently installed. If "other" is selected, specify details in the "Additional notes" column.
Note on C25: Select the permanent installation location for the BESS. If "other" is selected, specify details of the location such as under shelter, inside an outdoor building or within a room in the "Additional notes" column. Default value : outdoor
Note on C27: Select the expected minimum ambient temperature for the area surrounding the BESS . If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≥ −10
Note on C28: Select the expected maximum ambient temperature for the area surrounding the BESS . If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 40
Note on C29: Select the expected 24 h average ambient temperature for the area surrounding the BESS . If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 35
Note on C30: Select the required design ambient temperature for the area surrounding the BESS. If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 40
Note on C31: Select the expected solar radiation intensity. If "other" is selected, specify another intensity or a reference to an applicable document (e.g. procedure) in the "Additional notes" column.
Note on C32: Select the installation altitude above sea level. If "other" is selected, specify another altitude or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 1 000
Note on C33: Select the expected non-condensing relative humidity. If "other" is selected, specify another percentage or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 95
Note on C34: Select whether condensation or precipitation is present. If "yes" is selected, specify the form of precipitation in the "Additional notes" column. Precipitation characteristics for insulation are detailed in IEC 60060-1 and IEC 60071-1. Default value : no
Note on C35: Specify any expected special environmental conditions (e.g. dust, corrosion, flood, or wind). If corrosive environment conditions are specified, specify the corrosion category in accordance with EN ISO 12944-2 in the "Additional notes" column.
Note on C36: Select the outdoor battery cabinet IP rating. If "other" is selected, specify details in the "Additional notes" column. Default value : IP55
Note on C37: Select the applicable contaminant exposure to the BESS. If "other" is selected, specify another type of contamination or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : none
Note on C38: Select the seismic activity zone as defined in IEC 60721-2-6 for the location where the equipment is to be used. Where seismic certification is not required, select "not applicable".
Note on C40: Select the expected minimum ambient temperature for transportation and storage. If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≥ −10
Note on C41: Select the expected maximum ambient temperature for transportation and storage. If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 40
Note on C42: Select the expected maximum non-condensing relative humidity for transportation and storage. If "other" is selected, specify another percentage or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 95
Note on C43: Select the requirements for equipment preservation during transportation. If "other" is selected, specify another type of preservation (e.g. waterproofing, or a reference to an applicable document/procedure) in the "Additional notes" column. Default value : manufacturer's standard
Note on C44: Select the appropriate storage location for the BESS. If "other" is selected, specify another storage site or a reference to an applicable document (e.g. procedure) in the "Additional notes" column.
Note on C45: Specify any additional or unusual conditions expected (e.g. long storage of batteries) during transportation and storage.
Note on C46: Select whether thermostatically controlled anticondensation heater for transport and storage is required. If required, specify details in "Additional notes" column. Default value : not required
Note on C48: Specify the nominal voltage at the power system interface point.
Note on C49: Select the expected steady state voltage variation at the power system interface point. If "other" is selected, specify details in the "Additional notes" column. Default value : ±10
Note on C50: Specify the expected temporary voltage variation and its duration at the power system interface point.
Note on C51: Select the nominal frequency at the power system interface point. Default value : 50
Note on C52: Select the expected steady state frequency variation at the power system interface point. If "other" is selected, specify details in the "Additional notes" column. Default value : ±1
Note on C53: Specify the expected temporary frequency variation and its duration at the power system interface point.
Note on C54: Specify the value of minimum and maximum short circuit current at the power system interface point.
Note on C55: Select the type of neutral earthing. If "other" is selected, specify details in the "Additional notes" column. If "impedance earthed neutral" is selected, specify the value of impedance, current and duration in the "Additional notes" column.
Note on C56: Select the compatibility level for individual harmonic distortion of voltage in accordance with IEC 61000-2-4:2002, Table 2, Table 3 and Table 4. Default value : Class 2
Note on C57: Select the compatibility level for total harmonic distortion of voltage in accordance with IEC 61000-2-4:2002, Table 5. Default value : Class 2
Note on C59: Select the source of auxiliary power supply. If "internally derived" is selected no additional data is to be provided by the purchaser. Default value : externally derived
Note on C60: Specify the nominal voltage of the auxiliary power at the interface point.
Note on C61: Select the expected steady state voltage variation of the auxiliary power at the interface point. If "other" is selected, specify details in the "Additional notes" column. Default value : ±10
Note on C62: Select the nominal frequency of the auxiliary power at the interface point. Default value : 50
Note on C63: Select the expected steady state frequency variation of the auxiliary power at the interface point. If "other" is selected, specify details in the "Additional notes" column. Default value : ±1
Note on C64: Specify the available short-circuit current auxiliary power at the interface point.
Note on C65: Specify the type of neutral earthing. If "other" is selected, specify details in the "Additional notes" column. For "impedance earthed neutral", specify the value of impedance, current and duration in the "Additional notes" column.
Note on C67: Specify whether another language is to be used in addition to English for caution/danger/warning/safety marking information on equipment labels.
Note on C68: Select the acoustic noise at 1 m during operation in normal mode. If "other" is selected, specify details in the "Additional notes" column. Default value : manufacturer's standard
Note on C69: Select whether the evidence/documentation detailing the supplier’s hazard identification process in accordance with IEC 62933-5-2 is required to be submitted. Default value : not required
Note on C70: Select whether evidence/documentation detailing the safety design and functional information for each risk reduction measure utilized in the supplier failure modes and effects analysis (FMEA) or fault tree analysis (FTA) is required to be submitted. Default value : not required
Note on C72: Select the required BESS category in accordance with IEC 62933-5-2. If "other" is selected, specify details in the "Additional notes" column.
Note on C73: Select the intended purpose of the BESS application. If "other" is selected, specify details in the "Additional notes" column.
Note on C74: Specify the operation states of control for the selected BESS application.
Note on C75: Specify the rated active input power for which the BESS is to be designed to accept and store.
Note on C76: Specify the rated reactive input power for which the BESS is to be designed to absorb from the upstream network.
Note on C77: Specify the required rated active output power for which the BESS is to be designed to supply during its discharge phase.
Note on C78: Specify the required rated reactive output power for which the BESS is to be designed to supply during its discharge phase.
Note on C79: Specify the reference number of the BESS functional description document to be included as part of the BESS requisition.
Note on C81: Specify the reference of the duty cycle profile and description document to be included as part of the BESS requisition. Refer to Annex A and PNNL-22010 for further guidance on the duty cycle use case definition and the parameters associated to it.
Note on C83: Specify the required lithium battery chemistry. If "other" is selected, specify details of lithium chemistry required in the "Additional notes" column. Default value : lithium iron phosphate - LFP (LiFePO4)
Note on C84: Select the required battery housing. If "other" is selected, specify details in the "Additional notes" column. Default value : manufacturer's standard
Note on C85: Select the fire resistance rating for the battery housing. If "other" is selected, specify details in the "Additional notes" column. Default value : manufacturer's standard
Note on C87: Select the power conversion subsystem (PCS) housing. If "other" is selected, specify details in the "Additional notes" column. Default value : manufacturer's standard
Note on C89: Select whether an integrated fire suppression system for the battery housing is required. If "other" is selected, specify details in the "Additional notes" column. Default value : required
Note on C90: Select whether a fire and gas audible alarm is required. If "required" is selected, specify details (e.g. one audible alarm per container/cabinet or a common alarm for the entire BESS) in the "Additional notes" column. Default value : not required
Note on C91: Select whether an externally mounted high-visibility strobe light is required. Default value : not required
Note on C93: Select the BESS message category for remote monitoring and control. It is recommended to provide specific communications interface requirements within the datasheet Supplement tab or other procurement documentation (e.g. network architecture). Default value : category II
Note on C94: Select the network connectivity interface media based on time synchronization, remote access and configuration of the ECMS/PMS. If "other" is selected, specify details in the "Additional notes" column. Default value : Ethernet (fiber)
Note on C95: Select the required interface protocol to the ECMS/PMS as per project requirements. If "other" is selected, specify details in the "Additional notes" column. Default value : Ethernet IP
Note on C96: Select the interface network redundancy for the ECMS/PMS. If "other" is selected, specify details of the less preferred redundancy protocols such as the rapid spanning tree protocol (RSTP) as specified in IEEE 802.3 in the "Additional notes" column. Default value : not required
Note on C97: Select whether BESS remote access is required. If "required" is selected, specify details in the 'Additional notes' column. Default value : required
Note on C98: Select the interface media for the external fire and gas system (FGS). If "other" is selected, specify details in the "Additional notes" column. Default value : hardwired discrete
Note on C99: Select the interface protocol to the external fire and gas system (FGS). If "other" is selected, specify details in the "Additional notes" column. Default value : not applicable
Note on C100: Select the interface media for the external emergency shutdown (ESD) system. If "other" is selected, specify details in the "Additional notes" column. Default value : not required
Note on C101: Select the interface protocol to the external emergency shutdown (ESD) system. If "other" is selected, specify details in the "Additional notes" column. Default value : not applicable
Note on C102: Select whether hardware is required for remote access. If "required" is selected, specify details of hardware for interfacing with existing installations or third-party systems (e.g. adapters, connectors, cables) in the "Additional notes" column. Default value : required
Note on C104: Select whether interconnecting cables between the BESS equipment or subsystems are required to be supplied as part of the BESS package. Default value : required
Note on C105: If interconnecting cables between the BESS equipment or subsystems are required, specify the cable type required (e.g. 1.1kV/Cu/PVC/LSZH) and the applicable international standards.
Note on C107: Select whether the HV switchgear and associated devices upstream of the BESS (PCS) are to be supplied as part of the BESS package. Default value : not required
Note on C108: Default value : manufacturer standard locking facility
Note on C110: Select the transport, storage and handling requirements. If “other” is selected, specify details such as impact indicator, data logger, date-time stamping and export packing in the "Additional notes" column. Default value : manufacturer's standard
Note on C111: Select the required quantity of portable lifting trolley. If "other" is selected, specify details in the "Additional notes" column. Default value : not required

## Supplement
Row |  | IOGP S-753D (1.0) Procurement Data Sheet for Battery Energy Storage Systems (BESS) (IEC) | Issue
2 | Purchase order specific requirements
3 | Delete this sheet if not required.
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60

## Guidance
IOGP S-753D (1.0) Procurement Data Sheet for Battery Energy Storage Systems (BESS) (IEC)
Guidance on the use of this procurement data sheet (PDS)
This PDS is to be used in conjunction with IOGP S-753, Supplementary Specification to IEC TS 62933-3-1 for Battery Energy Storage Systems (BESS).
This PDS is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This PDS, completed with requested values, should be delivered back to the purchaser by using the PDS template or other mutually agreed method.
The Ref. clause column provides references back to the following: — parent standard and/or supplementary specification when the PDS is used in conjunction with a supplementary specification; — specification when the PDS is used in conjunction with a standalone specification.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the PDS item and/or an explanation of how to complete the input.
The Additional notes column may be used by the purchaser or supplier to provide additional information pertinent to the specification and/or supply of the equipment.
The Issue column should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the PDS that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data in a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set in accordance with essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the PDS. This worksheet is not intended to modify requirements defined in the specification.
The Purchaser requirement and Purchaser requirement UOM columns specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
The Supplier offered value and Supplier offered UOM columns are used by the supplier to declare the offered value. Where the offered product characteristic differs from the purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the purchaser requirement.
The Requirement CFIHOS ID and Equipment CFIHOS ID in columns K and L enable information exchange in a data-centric manner. Note that these columns are in a hidden area of the worksheet and can be unhidden for use.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data