## Addendum 1
Date of issue:
March 2026
Affected publication:
IOGP S-729D, Procurement Data Sheet for Control Valves, First Edition, May 2022
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in May 2022.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Worksheet | Row | Column | Update
| Common items | 14 | Description | Description amended Embedded guidance note amended
| Common items | 15 | Description | Description amended Embedded guidance note amended
| Common items | 21 | All | New data sheet item "Fittings make"
| Common items | 22 | All | New data sheet item "Sealing compound for threaded fittings"
| Common items | 28 | Description | Embedded guidance note amended
| Common items | 30 | Description | Description amended Embedded guidance note amended
| Common items | 36 | All | New data sheet item "Limit switch / position transmitter housing material
| Common items | 40 * | All | Data sheet item "Solenoid valve body material" * deleted
| Tag-specific | 17 |  | Description amended Embedded guidance note amended
| Tag-specific | 18 | All | New data sheet item "Hazardous protection method for limit switches/positioners/position transmitters"
| Tag-specific | 37 * | All | Data sheet item "Minimum flow rate" * deleted (from section "Process inputs - general")
| Tag-specific | 38 * | All | Data sheet item "Normal flow rate" * deleted (from section "Process inputs - general")
| Tag-specific | 39 * | All | Data sheet item "Maximum flow rate" * deleted (from section "Process inputs - general")
| Tag-specific | 55 | All | New data sheet item "Minimum flow rate" (in section "Process inputs - gas")
| Tag-specific | 56 | All | New data sheet item "Normal flow rate" (in section "Process inputs - gas")
| Tag-specific | 57 | All | New data sheet item "Maximum flow rate" (in section "Process inputs - gas")
| Tag-specific | 58 | All | New data sheet item "Inlet density at minimum flow" (in section "Process inputs - liquid")
| Tag-specific | 59 | All | New data sheet item "Inlet density at normal flow" (in section "Process inputs - liquid")
| Tag-specific | 60 | All | New data sheet item "Inlet density at maximum flow" (in section "Process inputs - liquid")
| Tag-specific | 61 | All | New data sheet item "Inlet viscosity at minimum flow" (in section "Process inputs - liquid")
| Tag-specific | 62 | All | New data sheet item "Inlet viscosity at normal flow" (in section "Process inputs - liquid")
List of updates (continued)
| Tag-specific | 63 | All | New data sheet item "Inlet viscosity at maximum flow" (in section "Process inputs - liquid")
| Tag-specific | 70 | All | New data sheet item "Minimum flow rate" (in section "Process inputs - gas")
| Tag-specific | 71 | All | New data sheet item "Normal flow rate" (in section "Process inputs - gas")
| Tag-specific | 72 | All | New data sheet item "Maximum flow rate" (in section "Process inputs - gas")
| Tag-specific | 108 | Description | Description amended Embedded guidance note amended
| Tag-specific | 132 | All | New data sheet item "Air fail trip valve"
| Tag-specific | 154 | All | New data sheet item "Air fail trip valve model number"
| All | Various | Row | Numbering updated as per new and deleted rows
* Data from Edition 1.0.

## Front & Preliminaries
|  |  |  | SPECIFICATION | March 2026
|  |  |  | IOGP S-729D | Version 1.01
ADDENDUM 1 TO FIRST EDITION (MAY 2022)
Procurement Data Sheet for Control Valves
Revision history
VERSION | DATE | PURPOSE
1.01 | March 2026 | Addendum 1
1 | May 2022 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-729D (1.01) Procurement Data Sheet for Control Valves
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-729D (1.01) Procurement Data Sheet for Control Valves
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of control valves in accordance with IOGP S-729 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-729), information requirements specification (IOGP S-729L) and quality requirements specification (IOGP S-729Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Common Items Proc. Data Sheet
Row | IOGP S-729D (1.01) Procurement Data Sheet for Control Valves Common Items | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
5 |  | Project country : | input data |  | input data
6 |  | Project region : | input data |  | input data
7 | 4.1 | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
8 | 10.1.1, Clause 15, 4.1 | Climate classification : | select |  | select | [5 empty] | select | tropical | arid | temperate | cold | polar | not applicable
9 | 10.1.1, Clause 15, 4.1 | Environmental classification : | input data |  | input data
10 |  | Units of measurement : | select |  | select | [5 empty] | select | SI | US customary
11 | 14.1.4.1, 14.1.5.1, 14.2.2, 14.2.3, 6.3.1, 6.6.2, 7.3, 8.1.1, 8.5, Table 14, Table 2 | Normative reference base standard : | select |  | select | [5 empty] | select | IEC 60534 series | ANSI/ISA 75 Series and ANSI/FCI
12 | 10.1.1, Clause 15, 4.1 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
13 | 10.1.1, Clause 15, 4.1 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
14 | 11.2.1,11.2.4 | Minimum network supply pressure : | input data | select | input data | select |  |  |  |  | select | kPag | barg | psig
15 | 11.3.2,12.1.1 | Maximum network supply pressure : | input data | select | input data | select |  |  |  |  | select | kPag | barg | psig
16 |  | Actuator control equipment (accessories)
17 |  | Cable entries for actuator control equipment (accessories) : | input data |  | input data
18 | 12.3.2.1, 12.5.1 | Position indication achieved through : | select |  | select | [5 empty] | select | smart positioner | limit switch | position transmitter
19 | 12.8 | Tubing size : | input data | select | input data | select |  |  |  |  | select | mm | in
20 | 12.8 | Tubing and fittings material : | select |  | select | [5 empty] | select | 316 stainless steel | 316L stainless steel | alloy 254 (6 Mo) | other
21 |  | Fittings make : | input data |  | input data
22 |  | Sealing compound for threaded fittings : | input data |  | input data
23 | 12.2.1 | Pressure gauge for air filter regulator : | select |  | select | [5 empty] | select | required | not required
24 |  | Air filter regulator body material : | select |  | select | [5 empty] | select | aluminium | 316 stainless steel
25 |  | Air filter regulator wetted parts material : | select |  | select | [5 empty] | select | 316 stainless steel | manufacturer's standard
26 |  | Positioner housing material : | select |  | select | [5 empty] | select | aluminium | 316 stainless steel | manufacturer's standard
27 |  | Positioner type : | select |  | select | [5 empty] | select | analog I/P | smart positioner
28 |  | Positioner mounting : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | IEC 60534-6-1/IEC 60534-6-2 | NAMUR NE 04 | manufacturer's standard
29 | 14.1.8.2 | Positioner input signal and protocol : | select |  | select | [5 empty] | select | 4 to 20 mA with HART® | FoundationTM Fieldbus | profibus
30 |  | Positioner gauges/indicators : | select |  | select | [5 empty] | select | required | not required
31 | 12.5.1 | Limit switch type : | input data |  | input data
32 |  | Limit switch mounting : | select |  | select | [5 empty] | select | NAMUR | manufacturer's standard
33 |  | Position transmitter type : | input data |  | input data
34 | 14.1.8.2 | Position transmitter output signal and protocol : | select |  | select | [5 empty] | select | 4 to 20 mA with HART® | FoundationTM Fieldbus | profibus
35 | 14.1.8.2 | Position transmitter supply voltage : | input data | select | input data | select |  |  |  |  | select | V DC | V AC
36 |  | Limit switch / position transmitter housing material : | select |  | select | [5 empty] | select | 316 stainless steel | flame-retardant material | manufacturer's standard
37 |  | Solenoid valve reset type : | auto reset |  | auto reset | [5 empty] | select | manual reset | auto reset
38 | 12.4.2 | Solenoid coil insulation : | select |  | select | [5 empty] | select | class F | class H
39 | 14.1.8.2 | Solenoid valve coil voltage : | input data | select | input data | select |  |  |  |  | select | V DC | V AC
40 |  | Booster, quick exhaust, air-lock relay body and wetted parts material : | select |  | select | [5 empty] | select | aluminium | 316 stainless steel | not applicable
41 | 12.7.1 | Air receiver : | select |  | select | [5 empty] | select | required | not required
42 | 12.7.3 | Overpressure protection for air receiver : | select |  | select | [5 empty] | select | required | not required
43 |  | Air receiver design code : | select |  | select | [5 empty] | select | ASME BPVC Section VIII | EN 13445-3 | other
44 | 10.2.2, Table 12 | Air receiver material : | select |  | select | [5 empty] | select | carbon steel with manufacturer's specified coating | carbon steel with purchaser's specified coating | 316 stainless steel
45 | 12.7.1 | Number of actuator strokes required for air receiver sizing : | three |  | three | [5 empty] | select | three | six
46 |  | Surface protection
47 | 15.1, 15.2, 15.3 | Atmospheric corrosivity category : | select |  | select | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
48 | 15.1, 15.2, 15.3 | Surface protection durability category : | medium (M) 7 to 15 years |  | medium (M) 7 to 15 years | [5 empty] | select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
49 | 14.1.2 | Actuator coating and painting colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
Note on C4: Select the CAS level to be applied in IOGP S-729Q, Annex A. Default value : D
Note on C5: Specify the country in which the equipment will be located.
Note on C6: Specify the geographic location of the project within the country. This location determines the applicability of local regulatory requirements.
Note on C7: Select the location of the facility, "offshore", "marine coastal", "subsea", "buried" or "onshore" where the equipment will be permanently installed.
Note on C8: Select the climate classification as per IEC 60721-2-1.
Note on C9: Specify the determined environmental classification as per IEC 60721-3-0.
Note on C10: Select "SI" or "US" customary units based on the project philosophy.
Note on C11: Select the required standard based on the project requirement (e.g. for North American location, select "ISA 75 series and ANSI/FCI"; for Europe, select "IEC").
Note on C12: Specify the minimum ambient temperature as per design data.
Note on C13: Specify the maximum ambient temperature as per design data.
Note on C14: Specify the minimum network supply pressure for sizing the actuator.
Note on C15: Specify the maximum network supply pressure to determine the need for overpressure protection (e.g. relief valves) and enable selection of actuator control equipment suitable for this maximum network supply pressure.
Note on C17: Specify the required cable entry for the actuator control equipment.
Note on C18: Select how the position indication back to the control system is achieved.
Note on C19: Specify the tubing size from of IOGP S-716, Table 1.
Note on C20: If "other" is selected, specify the tubing material from IOGP S-716, Table 2 in "Additional notes".
Note on C21: Specify the make of fittings.
Note on C22: Specify the sealing compound for threaded fittings.
Note on C23: Select whether a pressure gauge is required for the air supply line in addition to the pressure gauges available in the positioner.
Note on C24: Select the required body material.
Note on C25: Select the wetted parts material for the air filter regulator. If “manufacturer’s standard” is selected, supplier to specify the material in “Additional notes”.
Note on C26: Select housing material based on the site locations. If “manufacturer’s standard” is selected, supplier to specify the material in “Additional notes”.
Note on C27: Select whether a simple analog I/P is adequate or a smart positioner is required based on the project philosophy.
Note on C28: Select the required mounting based on the project philosophy. If “manufacturer’s standard” is selected, supplier to specify the mounting type in “Additional notes”. If the positioner is remote mounted, purchaser to specify the same in "Additional notes". Default value : manufacturer's standard
Note on C29: Select the required input signal. Ensure the same revision of protocol is used across the project to avoid compatibility issues.
Note on C30: Select whether gauges/indicators are required.
Note on C31: Specify the required limit switch type.
Note on C32: Select the required mounting from the listed options. If “manufacturer’s standard” is selected, supplier to specify the mounting type in “Additional notes”.
Note on C33: Specify the position transmitter type (e.g. analog, hall effect).
Note on C34: Select the required output signal.
Note on C35: Specify the required supply voltage.
Note on C36: Select the material for limit switch/ position transmitter housing.
Note on C37: Select auto-reset for general applications and specify manual-reset for safety, shutdown or applications as required by the process. Default value : auto reset
Note on C38: Select "Class F" or "Class H" based on the combination of heat generated by the coil and ambient temperature. Class F has a coil insulation rating of 155° C (311° F) and Class H has a coil insulation rating of 180° C (356° F).
Note on C39: Specify the required coil voltage.
Note on C40: Select the required body and wetted parts material for the actuator control equipment such as booster, quick exhaust valve and air lock relay.
Note on C41: Select the air receiver as "required" if a double-acting non-spring return actuator is specified.
Note on C42: Select overpressure protection device as "required" if the air receiver is located in a fire area or if the local regulations warrants a device for air receiver.
Note on C43: Select the design code for fabrication of the equipment.
Note on C44: Select the vessel material based on the site location and project philosophy (see Table 12).
Note on C45: Select the required actuator strokes required for sizing the air receiver based on application. The default value is "three" based on industry practice. Default value : three
Note on C47: Select the atmospheric corrosivity category in accordance with ISO 12944-2.
Note on C48: Select the surface durability category in accordance with ISO 12944-1, 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme. Default value : medium (M) 7 to 15 years
Note on C49: When the manufacturer's standard paint colour is unacceptable, specify the paint colour in "Additional notes". Default value : manufacturer's standard

## Tag-specific Proc. Data Sheet
Row | IOGP S-729D (1.01) Procurement Data Sheet for Control Valves Tag-specific | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 | 16.1 | Valve tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 | 12.4.3, 16.1 | Positioner tag number : | input data |  | input data
7 | 16.1 | Position transmitter tag number : | input data |  | input data
8 | 16.1 | Limit switch - open tag number : | input data |  | input data
9 | 16.1 | Limit switch - close tag number : | input data |  | input data
10 | 12.4.3, 16.1, 9.3 | Solenoid valve tag number : | input data |  | input data
11 | 16.1 | Air receiver tag number : | input data |  | input data
12 | 12.7.3, 16.1 | Pressure safety valve or rupture disc tag number for air receiver : | input data |  | input data
13 |  | General
14 | 10.1.1, 15.1, 15.2, 15.3, 4.1 | Special environmental conditions : | input data |  | input data
15 | A.1, Table 3 through Table 11, Table A.1, Table A.2 | Quality specification level for non-destructive examination (NDE) : | QSL-1 |  | QSL-1 | [5 empty] | select | QSL-1 | QSL-2 | QSL-3 | QSL-4
16 | 10.5.1, 10.5.2 | Control valve categorization : | select |  | select | [5 empty] | select | general service | severe service | special service
17 |  | Hazardous protection method for solenoid valves : | input data |  | input data
18 |  | Hazardous protection method for limit switches / positioners / position transmitters : | input data |  | input data
19 |  | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505 | not applicable
20 |  | Explosion hazard classification : | select |  | select | [5 empty] | select | zone 2 | zone 1 | zone 0 | division 2 | division 1 | not applicable
21 |  | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D | not applicable
22 |  | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6 | not applicable
23 |  | Pipe
24 |  | Line size : | input data | select | input data | select |  |  |  |  | select | DN | NPS
25 |  | Line schedule : | input data |  | input data
26 | 10.1.1, 15.4 | Pipe material : | input data |  | input data
27 | 15.1, 15.4 | Pipe insulation thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
28 |  | Process inputs - general
29 | 10.1.1, 10.5.3, 5.3.2, 8.1.1 | Process fluid : | input data |  | input data
30 | 8.1.1 | Fluid state : | input data |  | input data
31 | 8.1 | Fluid phase : | select |  | select | [5 empty] | select | single | multi | super-critical
32 | 10.1.1, 5.3.2, 7.4.1, 8.1 | Service : | select |  | select | [5 empty] | select | corrosive | erosive | toxic | depressurization | outgassing | fouling | others
33 | 10.1.1, 10.4, 8.1.1 | Sour service : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
34 | 10.1.1, 10.4, 10.5.1, 10.5.2, 10.5.3 | H₂S content : | input data | select | input data | select |  |  |  |  | select | % | mol % | parts per million by volume
35 | 10.1.1, 10.4, 10.5.1, 10.5.2, 10.5.3 | CO₂ content : | input data | select | input data | select |  |  |  |  | select | % | mol % | parts per million by volume
36 | 10.1.1, 10.4, 14.1.4.1, 4.2, 6.5.2 | Design pressure : | input data | select | input data | select |  |  |  |  | select | kPag | barg | psig
37 | 10.1.1, 10.1.10, 10.4, 4.2, 6.5.2 | Design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
38 | 8.1.1 | Inlet pressure at minimum flow : | input data | select | input data | select |  |  |  |  | select | kPag | barg | psig
39 | 8.1.1 | Inlet pressure at normal flow : | input data | select | input data | select |  |  |  |  | select | kPag | barg | psig
40 | 8.1.1 | Inlet pressure at maximum flow : | input data | select | input data | select |  |  |  |  | select | kPag | barg | psig
41 | 8.1.1, 8.2.1, 8.2.2 | Pressure drop at minimum flow : | input data | select | input data | select |  |  |  |  | select | kPa | bar | psi
42 | 8.1.1 | Pressure drop at normal flow : | input data | select | input data | select |  |  |  |  | select | kPa | bar | psi
43 | 8.1.1, 8.2.1, 8.2.2 | Pressure drop at maximum flow : | input data | select | input data | select |  |  |  |  | select | kPa | bar | psi
44 |  | Maximum allowable pressure drop : | input data | select | input data | select |  |  |  |  | select | kPa | bar | psi
45 | 8.1.1 | Inlet temperature at minimum flow : | input data | select | input data | select |  |  |  |  | select | °C | °F
46 |  | Inlet temperature at normal flow : | input data | select | input data | select |  |  |  |  | select | °C | °F
47 | 8.1.1 | Inlet temperature at maximum flow : | input data | select | input data | select |  |  |  |  | select | °C | °F
48 | 8.1.1 | Outlet temperature at minimum flow : | input data | select | input data | select |  |  |  |  | select | °C | °F
49 | 8.1.1 | Outlet temperature at normal flow : | input data | select | input data | select |  |  |  |  | select | °C | °F
50 | 8.1.1 | Outlet temperature at maximum flow : | input data | select | input data | select |  |  |  |  | select | °C | °F
51 | 11.2.1, 11.2.4, 8.1.1 | Maximum shutoff differential pressure (forward flow direction) : | input data | select | input data | select |  |  |  |  | select | kPa | bar | psi
52 | 11.2.3, 11.2.4, 8.1.1 | Maximum shutoff differential pressure (reverse flow direction) : | input data | select | input data | select |  |  |  |  | select | kPa | bar | psi
53 | 11.3.1, 12.6, 14.1.8.3 | Valve action on air and power failure : | select |  | select | [5 empty] | select | fail-open | fail-close | fail-lock
54 |  | Process inputs - liquid
55 | 8.1.1,8.2 | Minimum flow rate : | input data | select | input data | select |  |  |  |  | select | m3/h | ft3/h
56 | 8.1.1 | Normal flow rate : | input data | select | input data | select |  |  |  |  | select | m3/h | ft3/h
57 | 8.1.1,8.2 | Maximum flow rate : | input data | select | input data | select |  |  |  |  | select | m3/h | ft3/h
58 | 8.1.1,8.2 | Inlet density at minimum flow : | input data | select | input data | select |  |  |  |  | select | kg/m3 | lb/ft3
59 | 8.1.1 | Inlet density at normal flow : | input data | select | input data | select |  |  |  |  | select | kg/m3 | lb/ft3
60 | 8.1.1,8.2 | Inlet density at maximum flow : | input data | select | input data | select |  |  |  |  | select | kg/m3 | lb/ft3
61 | 8.1.1,8.2 | Inlet viscosity at minimum flow : | input data | select | input data | select |  |  |  |  | select | cP | cS
62 | 8.1.1 | Inlet viscosity at normal flow : | input data | select | input data | select |  |  |  |  | select | cP | cS
63 | 8.1.1,8.2 | Inlet viscosity at maximum flow : | input data | select | input data | select |  |  |  |  | select | cP | cS
64 | 8.1.1 | Inlet vapour pressure at minimum flow : | input data | select | input data | select |  |  |  |  | select | kPaa | bara | psia
65 | 8.1.1 | Inlet vapour pressure at normal flow : | input data | select | input data | select |  |  |  |  | select | kPaa | bara | psia
66 | 8.1.1 | Inlet vapour pressure at maximum flow : | input data | select | input data | select |  |  |  |  | select | kPaa | bara | psia
67 | 8.1.1 | Critical pressure : | input data | select | input data | select |  |  |  |  | select | kPaa | bara | psia
68 | 8.1.1 | Critical temperature : | input data | select | input data | select |  |  |  |  | select | K | °R
69 |  | Process inputs - gas
70 | 8.1.1,8.2 | Minimum flow rate : | input data | select | input data | select |  |  |  |  | select | kg/h | m3/h | lb/h | ft3/h
71 | 8.1.1 | Normal flow rate : | input data | select | input data | select |  |  |  |  | select | kg/h | m3/h | lb/h | ft3/h
72 | 8.1.1,8.2 | Maximum flow rate : | input data | select | input data | select |  |  |  |  | select | kg/h | m3/h | lb/h | ft3/h
73 | 8.1.1 | Molecular weight at minimum flow : | input data | select | input data | select |  |  |  |  | select | g/mole | lb/mole
74 | 8.1.1 | Molecular weight at normal flow : | input data | select | input data | select |  |  |  |  | select | g/mole | lb/mole
75 | 8.1.1 | Molecular weight at maximum flow : | input data | select | input data | select |  |  |  |  | select | g/mole | lb/mole
76 | 8.1.1 | Compressibility factor at minimum flow : | input data |  | input data
77 | 8.1.1 | Compressibility factor at normal flow : | input data |  | input data
78 | 8.1.1 | Compressibility factor at maximum flow : | input data |  | input data
79 | 8.1.1 | Specific heat ratio at minimum flow : | input data |  | input data
80 | 8.1.1 | Specific heat ratio at normal flow : | input data |  | input data
81 | 8.1.1 | Specific heat ratio at maximum flow : | input data |  | input data
82 |  | Body and bonnet
83 | 5.2.1 | Body style : | select |  | select | [5 empty] | select | globe - straight | globe - angle | axial | full ball | segmented ball | three way | rotary plug - eccentric | butterfly - eccentric offset
84 | 6.1, 6.3.2, Table 1 | Inlet/outlet size : | input data | select | input data | select |  |  |  |  | select | DN | NPS
85 | 4.2, 6.3.2 | Pressure class : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | special
86 |  | End connection type : | select |  | select | [5 empty] | select | flanged | double-flanged | wafer | drilled lug | tapped lug | butt welded | hubbed
87 |  | Flange facing : | input data |  | input data
88 |  | Flange facing finish : | input data |  | input data
89 | 6.1.3 | Flange standard for sizes between DN 650 (NPS 26) and DN 1500 (NPS 60) : | select |  | select | [5 empty] | select | ASME B16.47 Series A | ASME B16.47 Series B | not applicable
90 | Table 3 through Table 11 | Body and bonnet material : | input data |  | input data
91 | Table 3 through Table 11 | Body/bonnet bolting and nuts material : | input data |  | input data
92 |  | Bonnet style : | select |  | select | [5 empty] | select | standard bonnet | extension bonnet
93 | 10.1.6, 6.7.1 | Body/bonnet gasket material : | input data |  | input data
94 | 6.5.2 | Packing material : | input data |  | input data
95 |  | Packing type : | select |  | select | [5 empty] | select | live loaded | bolted
96 |  | Trim
97 |  | Trim (port) size : | input data | select | input data | select |  |  |  |  | select | mm | in
98 |  | Plug balance : | select |  | select | [5 empty] | select | balanced | unbalanced
99 | 8.3.1 | Valve characteristics : | select |  | select | [5 empty] | select | linear | equal % | quick opening | other
100 | 10.5.1, 10.5.2, 10.5.3, Table 3 through Table 11 | Ball/plug/disk material and hardfacing : | input data |  | input data
101 | 10.5.1, 10.5.2, 10.5.3, Table 3 through Table 11 | Seat material and hardfacing : | input data |  | input data
102 | Table 3 through Table 11 | Stem material : | input data |  | input data
103 | 10.5.1, Table 3 through Table 11 | Cage material : | input data |  | input data
104 | 7.4.2.2 | Anti-cavitation trim : | select |  | select | [5 empty] | select | yes | no
105 |  | Noise abatement trim : | select |  | select | [5 empty] | select | yes | no
106 |  | Actuator
107 |  | Actuator type : | single-acting with spring return |  | single-acting with spring return | [5 empty] | select | single-acting with spring return | double-acting
108 | 11.3.2 | Piston actuator cylinder design pressure achieved : | select |  | select | [5 empty] | select | by design | by pressure relief valve | by air filter regulator
109 | 10.2.2, Table 12 | Housing/cylinder material : | select |  | select | [5 empty] | select | carbon steel with coating | aluminium | stainless steel
110 | 10.2.2, Table 12 | Handwheel : | not required |  | not required | [5 empty] | select | not required | required
111 |  | Travel : | input data | select | input data | select |  |  |  |  | select | mm | in
112 | 11.4.3 | Limit (travel) stop : | not required |  | not required | [5 empty] | select | adjustable | non-adjustable | not required
113 | 11.4.3, 14.1.8.2 | Limit (travel) stop setting : | input data | select | input data | select |  |  |  |  | select | % | º | N/A
114 |  | Performance/special requirements
115 | 13.2.1, 13.2.2, 14.2.5 | Stroking time for opening : | input data | s | input data | s
116 | 13.2.1, 13.2.2, 14.2.5 | Stroking time for closing : | input data | s | input data | s
117 | 11.2.3, 14.1.5.1, 14.2.6.1, 7.3, Table 14 | Leakage class : | input data |  | input data
118 |  | Maximum external sound pressure level : | input data | dBA | input data | dBA
119 |  | Duty cycle : | input data |  | input data
120 | 13.2.4 | Overshoot for anti-surge valves : | input data | % | input data | %
121 |  | Maximum control signal change to move off the seat for anti-surge valves : | input data | % | input data | %
122 | 6.4 | Elastomer rapid gas (explosive) decompression resistant grade : | no |  | no | [5 empty] | select | yes | no
123 | 6.6.3 | Fugitive emission packing type : | input data |  | input data
124 | 6.6.3 | Fugitive emission tightness class : | select |  | select | [5 empty] | select | AH | BH | CH | AM | BM | CM | 100 ppmv | 500 ppmv
125 | 6.6.2 | Fugitive emission endurance class : | select |  | select | [5 empty] | select | CC1 | CC2 | CC3 | A1 | A2 | B1 | B2
126 |  | Fugitive emission temperature class : | input data | select | input data | select |  |  |  |  | select | °C | °F
127 | 14.1.6, 6.6.1 | Certified fugitive emission packing : | select |  | select | [5 empty] | select | yes | no
128 |  | Actuator control equipment - Miscellaneous
129 |  | Booster : | select |  | select | [5 empty] | select | yes | no
130 |  | Quick exhaust valve : | select |  | select | [5 empty] | select | yes | no
131 |  | Air lock relay : | select |  | select | [5 empty] | select | yes | no
132 | 11.3.1 | Air fail trip valve : | select |  | select | [5 empty] | select | required | not required
133 | 9.3 | Solenoid valve type : | select |  | select | [5 empty] | select | direct acting | external pilot operated
134 |  | Limit switch open setting : | input data | select | input data | select |  |  |  |  | select | ° | %
135 |  | Limit switch close setting : | input data | select | input data | select |  |  |  |  | select | ° | %
136 |  | Manufacturer
137 |  | Control valve manufacturer : | input data |  | input data
138 |  | Actuator manufacturer : | input data |  | input data
139 |  | Positioner manufacturer : | input data |  | input data
140 |  | Limit switch manufacturer : | input data |  | input data
141 |  | Solenoid valve manufacturer : | input data |  | input data
142 |  | Position transmitter manufacturer : | input data |  | input data
143 |  | Model number
144 |  | Control valve model number : | input data |  | input data
145 |  | Actuator model number : | input data |  | input data
146 |  | Positioner model number : | input data |  | input data
147 |  | Limit switch model number : | input data |  | input data
148 |  | Position transmitter model number : | input data |  | input data
149 |  | Air filter regulator model number : | input data |  | input data
150 |  | Solenoid model number : | input data |  | input data
151 |  | Booster model number : | input data |  | input data
152 |  | Quick exhaust model number : | input data |  | input data
153 |  | Air lock relay model number : | input data |  | input data
154 |  | Air fail trip valve model number : | input data |  | input data
Note on C4: Specify the control valve tag from the PID or the process data sheet.
Note on C5: Specify the functional description of the tag.
Note on C6: Specify the positioner tag from the PID.
Note on C7: Specify the position transmitter tag from the PID.
Note on C8: Specify the limit switch - open tag from the PID.
Note on C9: Specify the limit switch - close tag from the PID.
Note on C10: Specify the solenoid tag from the PID.
Note on C11: Specify the air receiver tag from the PID.
Note on C12: Specify the pressure safety valve or rupture disc tag number for the air receiver.
Note on C14: Indicate special conditions arising from the installation location (e.g. wet salt accumulation, sea water spray conditions, dust concentration, particle size distribution).
Note on C15: Default value : QSL-1
Note on C16: Based on the preliminary sizing, categorize the valve as per 3.1, 3.2 and 3.3 and select the valve service accordingly. This information is used by the manufacturer to initially quote. In addition, this gives a firm basis for the bid evaluation.
Note on C17: Specify the required protection method (e.g. EX protection for solenoid valves based on the project philosophy).
Note on C18: Specify the required protection method (e.g. EX protection for limit switches / positioners / position transmitters based on the project philosophy).
Note on C19: Select the code to be followed for the hazardous area classification.
Note on C20: Select the hazardous zone based on the functional requirement or the environment in which the equipment will be installed.
Note on C21: Select the explosion group classification of the equipment in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C22: Select the temperature classification of the equipment in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C24: Specify the line size from the PID.
Note on C25: Specify the line schedule from the piping class.
Note on C26: Specify the pipe material from the piping class.
Note on C27: Specify the pipe insulation thickness from the piping class.
Note on C29: Specify the process fluid as per the process data sheet and in "Additional notes", indicate whether the fluid is flammable or non-flammable. Do not specify "produced water" as "water". This will avoid erosion risk to the valve components.
Note on C30: Specify the fluid state as per the process data sheet.
Note on C31: Select the fluid phase as per the process data sheet.
Note on C32: Select the service based on the process data sheet. Indicate the user definition for lethal and toxic service so that the manufacturer clearly understands the importance of the service.
Note on C33: "ANSI/NACE MR0175/ISO 15156" may be selected to projects in upstream exploration and production and "ANSI/NACE MR0103/ISO 17945" may be selected for refinery projects. Default value : not applicable
Note on C34: Specify the H₂S content in %, mol %, parts per million by volume.
Note on C35: Specify the CO₂ content in %, mol %, parts per million by volume.
Note on C36: Specify the design pressure as per the process data sheet.
Note on C37: Specify the design temperature as per the process data sheet.
Note on C38: Specify the inlet pressure at minimum flow rate as per the process data sheet.
Note on C39: Specify the inlet pressure at normal flow rate as per the process data sheet.
Note on C40: Specify the inlet pressure at maximum flow rate as per the process data sheet.
Note on C41: Specify the pressure drop at minimum flow rate as per the process data sheet.
Note on C42: Specify the pressure drop at normal flow rate as per the process data sheet.
Note on C43: Specify the pressure drop at maximum flow rate as per the process data sheet.
Note on C44: Specify the maximum allowable pressure drop if the pressure drop for minimum, normal, maximum conditions are not provided.
Note on C45: Specify the inlet temperature at minimum flow rate as per the process data sheet.
Note on C46: Specify the inlet temperature at normal flow rate as per the process data sheet.
Note on C47: Specify the inlet temperature at maximum flow rate as per the process data sheet.
Note on C48: Specify the outlet temperature at minimum flow rate as per the process data sheet. On high pressure drop gas applications, the predicted downstream temperature should be defined.
Note on C49: Specify the outlet temperature at normal flow rate as per the process data sheet. On high pressure drop gas applications, the predicted downstream temperature should be defined.
Note on C50: Specify the outlet temperature at maximum flow rate as per the process data sheet. On high pressure drop gas applications, the predicted downstream temperature should be defined.
Note on C51: Specify the maximum shutoff differential pressure (forward flow direction) as per the process data sheet.
Note on C52: Specify the maximum shutoff differential pressure (reverse flow direction) as per the process data sheet.
Note on C53: Select the failure action for air and power failure as per the process data sheet.
Note on C55: Specify the minimum flow rate as per the process data sheet. If more than one liquid is present, separate values with a "[ ] / [ ]" (e.g. "[oil] / [water]").
Note on C56: Specify the normal flow rate as per the process data sheet. If more than one liquid is present, separate values with a "[ ] / [ ]" (e.g. "[oil] / [water]").
Note on C57: Specify the maximum flow rate as per the process data sheet. If more than one liquid is present, separate values with a "[ ] / [ ]" (e.g. "[oil] / [water]").
Note on C58: Specify the inlet density at minimum flow as per the process data sheet. If more than one liquid is present, separate values with a "[ ] / [ ]" (e.g. "[oil] / [water]").
Note on C59: Specify the inlet density at normal flow as per the process data sheet. If more than one liquid is present, separate values with a "[ ] / [ ]" (e.g. "[oil] / [water]").
Note on C60: Specify the inlet density at maximum flow as per the process data sheet. If more than one liquid is present, separate values with a "[ ] / [ ]" (e.g. "[oil] / [water]").
Note on C61: Specify the inlet viscosity at minimum flow as per the process data sheet. If more than one liquid is present, separate values with a "[ ] / [ ]" (e.g. "[oil] / [water]").
Note on C62: Specify the inlet viscosity at normal flow as per the process data sheet.If more than one liquid is present, separate values with a "[ ] / [ ]" (e.g. "[oil] / [water]").
Note on C63: Specify the inlet viscosity at maximum flow as per the process data sheet. If more than one liquid is present, separate values with a "[ ] / [ ]" (e.g. "[oil] / [water]").
Note on C64: Specify the inlet vapour pressure at minimum flow rate as per the process data sheet.
Note on C65: Specify the inlet vapour pressure at normal flow rate as per process data sheet.
Note on C66: Specify the inlet vapour pressure at maximum flow rate as per the process data sheet.
Note on C67: Specify the critical pressure as per the process data sheet.
Note on C68: Specify the critical temperature as per the process data sheet.
Note on C70: Specify the minimum flow rate as per the process data sheet.
Note on C71: Specify the normal flow rate as per the process data sheet.
Note on C72: Specify the maximum flow rate as per the process data sheet.
Note on C73: Specify the molecular weight at minimum flow rate as per the process data sheet.
Note on C74: Specify the molecular weight at normal flow rate as per the process data sheet.
Note on C75: Specify the molecular weight at maximum flow rate as per the process data sheet.
Note on C76: Specify the compressibility factor at minimum flow rate as per the process data sheet.
Note on C77: Specify the compressibility factor at normal flow rate as per the process data sheet.
Note on C78: Specify the compressibility factor at maximum flow rate as per the process data sheet.
Note on C79: Specify the specific heat ratio at minimum flow rate as per the process data sheet.
Note on C80: Specify the specific heat ratio at normal flow rate as per the process data sheet.
Note on C81: Specify the specific heat ratio at maximum flow rate as per the process data sheet.
Note on C83: Select the body style based on the application as a starting point. Subsequently based on the manufacturer's sizing and recommendation, fine tune the body style as required. Single, double or triple offset can be specified in "Additional notes".
Note on C84: Confirm the valve inlet/outlet size based on the sizing calculation.
Note on C85: Select the pressure class based on the piping class.
Note on C86: Select the end connection type based on piping specification. For rotary valves DN 200 (NPS 8) DN 300 (NPS 12) or above, non-centering bolt holes may be provided as "non-threaded". This should be specified in "Additional notes".
Note on C87: Specify the required flange facing (e.g. RF, RTJ) as per the piping specification.
Note on C88: Specify the required flange facing as per the piping specification.
Note on C89: Select the applicable flange series based on the piping requirements.
Note on C90: Specify the body/bonnet material based on the piping material.
Note on C91: Specify the body/bonnet bolting and nuts material based on the piping material.
Note on C92: Purchaser to select the initial selection of the bonnet style based on the selected packing and design temperature. Subsequently, manufacturer to offer a suitable bonnet style.
Note on C93: Confirm the gasket material.
Note on C94: Confirm the packing material based on the design temperature. Purchaser to verify the quoted material.
Note on C95: Select the required packing based on the application or leakage class requirements.
Note on C97: Confirm the trim size based on the sizing calculation.
Note on C98: Manufacturer to select the offered plug type i.e. balanced or unbalanced plug based on selected model.
Note on C99: Select the characteristics based on the system pressure drop and pressure drop across the valve at various operating conditions or process model for the intended application.
Note on C100: Specify the ball/plug/disk material based on the material selection from Table 3 through Table 11. The manufacturer should recommend hardfacing based on severe service conditions.
Note on C101: Specify the seat material based on the material selection from Table 3 through Table 11. The manufacturer should recommend hardfacing based on severe service conditions.
Note on C102: Specify the stem material based on the material selection from Table 3 through Table 11.
Note on C103: Specify the cage material based on the material selection from Table 3 through Table 11.
Note on C107: Select the required actuator type based on experience for the application. Default value : single-acting with spring return
Note on C108: Based on the project philosophy and risk tolerance, select how the piston actuator cylinder design pressure needs to be achieved "by design", "by pressure relief valve" or "by air filter regulator".
Note on C109: Confirm the housing/cylinder material grade based on Table 12.
Note on C110: Select "required" if the handwheel is required. Select "not required" for safety instrumented function. Default value : not required
Note on C111: Confirm the travel based on the selected actuator.
Note on C112: Select the type of limit (travel) stop i.e. adjustable or non-adjustable. When limit (travel) stop is not required, select "not required". Default value : not required
Note on C113: Specify the travel stop position in terms of percentage or degree if the set positions are known. If not, specify the limiting Cv in "Additional notes" and the manufacturer will calculate the stop position in terms of percentage or degree.
Note on C115: Specify the required stroking time in the opening direction as per the process data sheet.
Note on C116: Specify the required stroking time in the closing direction as per the process data sheet.
Note on C117: Specify the leakage class as per process data sheet based on IEC or ISA adoption.
Note on C118: Specify the maximum external sound pressure level as per the project noise philosophy and based on continuous, intermittent or infrequent service of the application.
Note on C119: Specify this attribute if the duty cycle is typically more than 10 cycles per hour.
Note on C120: Specify the overshoot in percentage based on user experience for the application or based on the compressor manufacturer's input.
Note on C121: Typically within 2 % of control signal the valve will start moving from the seat. This value can be specified based on user experience or on the compressor manufacturer's input.
Note on C122: If required, grade to conform to NORSOK M-710 or ISO 23936. RGD grade elastomer to be considered for high pressure applications, as the probability of explosive decompression increases with P, P variations, T and X-section of the O-ring. Default value : no
Note on C123: Confirm the fugitive emission packing type based the emission requirements.
Note on C124: Select the required fugitive emission tightness class as per ISO 15848-1 or FCI 91-1.
Note on C125: Select the required endurance class for the application as per ISO 15848-1 or FCI 91-1.
Note on C126: Confirm the required fugitive emission temperature class as per ISO 15848-1.
Note on C127: Purchaser to select "yes" if a certified fugitive emission packing is required based on the application. If this attribute is not specified by the purchaser, manufacturer to select "yes" or "no" based on the fugitive emission packing supplied.
Note on C129: Select "yes" if a booster is required to meet the specified stroking (travel) time.
Note on C130: Select "yes" if a quick exhaust valve is required to meet the specified stroking (travel) time.
Note on C131: Select "yes" if an air lock relay is required for fail last applications.
Note on C132: Select "required" if air fail trip valve is required for fail last applications.
Note on C133: Select the solenoid valve type based on the project philosophy.
Note on C134: Specify the required limit switch open setting based on the application.
Note on C135: Specify the required limit switch close setting based on the application.
Note on C137: Provide the control valve manufacturer's name during bid evaluation stage.
Note on C138: Provide the actuator manufacturer's name during bid evaluation stage.
Note on C139: Provide the positioner manufacturer's name during bid evaluation stage.
Note on C140: Provide the limit switch manufacturer's name during bid evaluation stage.
Note on C141: Provide the solenoid valve manufacturer's name during bid evaluation stage.
Note on C142: Provide the position transmitter manufacturer's name during bid evaluation stage.
Note on C144: Provide the model number prior to purchase order.
Note on C145: Provide the model number prior to purchase order.
Note on C146: Provide the model number prior to purchase order.
Note on C147: Provide the model number prior to purchase order.
Note on C148: Provide the model number prior to purchase order.
Note on C149: Provide the model number prior to purchase order.
Note on C150: Provide the model number prior to purchase order.
Note on C151: Provide the model number prior to purchase order.
Note on C152: Provide the model number prior to purchase order.
Note on C153: Provide the model number prior to purchase order.
Note on C154: Provide the model number prior to purchase order.

## Supplement
Row |  | IOGP S-729D (1.01) Procurement Data Sheet for Control Valves | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
9
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-729D (1.01) Procurement Data Sheet for
Control Valves
Guidance on the use of this procurement data sheet
To be used in conjunction with :
IOGP S-729 Specification for Control Valves.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data