## Addendum 1
Date of issue:
March 2026
Affected publication:
IOGP S-729L, Information Requirements for Control Valves, First Edition, May 2022
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in May 2022.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Worksheet | IR ID | Column | Update
| Definitions | IR-4 | F - CFIHOS Code | CFIHOS code CFIHOS-70000451 added
| Definitions | IR-5 | F - CFIHOS Code | CFIHOS code CFIHOS-70000455 added
| Definitions | IR-9 | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000260
| Definitions | IR-33 | C - Description | Description amended
| Definitions | IR-38 | F - CFIHOS Code | CFIHOS code CFIHOS-70000203 added
| Definitions | IR-54 | F - CFIHOS Code | CFIHOS code CFIHOS-70000227 added
| Requirements Definitions | IR-75 | All | New information requirement "Welding traceability records"
| Definitions | IR-71 | F - CFIHOS Code | CFIHOS code CFIHOS-70000245 added
| Definitions | IR-63 | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000431
| Definitions | IR-46 | F - CFIHOS Code | CFIHOS code CFIHOS-70000437 added
| Definitions | IR-52 | F - CFIHOS Code | CFIHOS code CFIHOS-70000446 added
| Definitions | IR-48 | F - CFIHOS Code | CFIHOS code CFIHOS-70000446 added
| Definitions | IR-47 | F - CFIHOS Code | CFIHOS code CFIHOS-70000245 added
| Definitions | IR-69 | F - CFIHOS Code | CFIHOS code CFIHOS-70000245 added
| Definitions | IR-41 | C - Description | Description amended
| Requirements Definitions | IR-76 | All | New information requirement "Manufacturer record book (MRB)"

## Front & Preliminaries
|  |  |  | SPECIFICATION | March 2026
|  |  |  | IOGP S-729L | Version 1.01
ADDENDUM 1 TO FIRST EDITION (MAY 2022)
Information Requirements for Control Valves
Revision history
VERSION | DATE | PURPOSE
1.01 | March 2026 | Addendum 1
1 | May 2022 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-729L (1.01) Information Requirements for Control Valves
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-729L (1.01) Information Requirements for Control Valves
Introduction
The purpose of this information requirements specification (IRS) is to define information requirements for the procurement of control valves in accordance with IOGP S-729 for application in the petroleum and natural gas industries. The IRS defines the information requirements, including format, timing and purpose, for information to be provided by the supplier. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the specification (IOGP S-729), procurement data sheet (IOGP S-729D) and quality requirements specification (IOGP S-729Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification

## Instructions
IOGP S-729L (1.01) Information Requirements for
Control Valves
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS Structure Contents
| 1 | 'Front & Preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes / No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information Submission Abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS .
Column K — 'Translation Required' (Yes / No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable Formats
Column F — 'CFIHOS Discipline Document Type Code' relates to the CFIHOS discipline document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3 below. Metadata listed below are as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The document master to which this revision is related |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification |  |  | The Export Control Rule that is applicable for the document revision (e.g., ECCN, EAR). |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
| Security classification |  |  | Indicates internal Owner-Operator access restriction applicable for the document |  |  | TBA
Table 3 — Supplier Deliverable Metadata

## Requirements
IOGP S-729L (1.01) Information Requirements for Control Valves
Requirements
Column | Heading - Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Information Deliverable Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S729-IR-1 | Supplier master information schedule |  | Information Deliverables List | No | For Acceptance |  | - | - |  | -
S729-IR-2 | Delivery schedule |  | Delivery/Production Schedule | Yes | For Information |  | - | - |  | -
S729-IR-3 | Progress report |  | Progress Report | No | For Information |  | - | - |  | -
S729-IR-4 | Quality plan | Required for CAS A, CAS B | Quality Plan | - | - |  | - | - |  | -
S729-IR-5 | Sub-supplier list |  | Sub-Supplier List | Yes | For Information |  | - | - |  | -
S729-IR-6 | Inspection and test plan for complete package |  | Inspection and Test Plan (ITP) | Yes | For Acceptance |  | - | - |  | -
S729-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | - | - |  | -
S729-IR-8 | Non-conformance records |  | Non-conformance records | No | For Information |  | - | - |  | -
S729-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | - | - |  | -
Technical Information Deliverables
S729-IR-26 | General arrangement diagram |  | General Arrangement Diagram | Yes | For Acceptance |  | - | - |  | -
S729-IR-62 | Pneumatic schematics including hook-up information |  | Schematics Including Hook-Up Information | No | For Acceptance |  | - | - |  | -
S729-IR-23 | Control valve sizing calculations |  | Design calculation | Yes | For Acceptance |  | - | - |  | -
S729-IR-33 | Actuator sizing calculations |  | Design calculation | Yes | For Acceptance |  | - | - |  | -
S729-IR-55 | Pressure vessel (air receiver) design calculation |  | Design Calculation | No | For Acceptance |  | - | - |  | -
S729-IR-21 | Manufacturer datasheet |  | Manufacturer Datasheet | Yes | For Acceptance |  | - | - |  | -
S729-IR-38 | Utility consumption details (electrical and pneumatic) |  | Consumption Data And Load List | No | For Information |  | - | - |  | - | Air and power consumption details required for plant design such as air compressor and UPS design.
S729-IR-36 | Equipment cross section diagram |  | Equipment Cross Section Diagram | No | For Information |  | - | - |  | -
S729-IR-64 | Manufacturer's product catalog or product data sheet |  | Manufacturer Datasheet | Yes | For Information |  | - | - |  | -
S729-IR-44 | Hydrostatic test procedure |  | Pressure Test Procedure | No | For Acceptance |  | - | - |  | -
S729-IR-43 | Non-destructive test procedure |  | Non Destructive Test Procedure | No | For Information |  | - | - |  | -
S729-IR-72 | Heat treatment procedure |  | Heat Treatment Procedure | No | For Acceptance |  | - | - |  | -
S729-IR-54 | Positive material identification (PMI) procedure |  | Positive Material Identification (PMI) Procedure | No | For Acceptance |  | - | - |  | -
S729-IR-42 | Factory acceptance test (FAT) procedure |  | Factory Acceptance Test (FAT) Procedure | No | For Acceptance |  | - | - |  | -
S729-IR-60 | Cryogenic testing (FAT) procedure |  | Factory Acceptance Test (FAT) Procedure | No | For Acceptance |  | - | - |  | -
S729-IR-65 | Welding procedure specification |  | Welding Procedure Specification | No | For Acceptance |  | - | - |  | -
S729-IR-49 | Welding repair procedure |  | Welding Repair Procedure | No | For Acceptance |  | - | - |  | -
S729-IR-75 | Welding traceability records |  | Welding traceability records | No | For Acceptance |  | - | - |  | -
S729-IR-27 | Painting and coating procedure |  | Painting And Coating Procedure | No | For Acceptance |  | - | - |  | -
S729-IR-57 | Lifting hook or fixture load safety factor calculations |  | Design calculation | No | For Information |  | - | - |  | -
S729-IR-71 | Manufacturing qualification procedure test reports |  | Manufacturing Qualification Procedure Test Reports | No | For Information |  | - | - |  | -
S729-IR-32 | Materials inspection certificate (3.1) for pressure containing and retaining parts, ball, plug, disk, cage, seat ring, bellows and air receiver |  | Materials Inspection Certificate (3.1) | No | For Information |  | - | - |  | -
S729-IR-63 | Declaration of compliance (2.1) for seals, gaskets and packing assembly |  | Material Declaration Of Conformity (2.1) | No | For Acceptance |  | - | - |  | -
S729-IR-70 | Material inspection report (2.2) for ball, plug, disk, cage, seat ring in QSL-1 and QSL-2 valve |  | Material inspection report (2.2) | No | For Information |  |  | - |  | -
S729-IR-68 | Certificate of conformance for the finished valve assembly (Sour service) |  | Certificate of conformance | No | For Information |  | - | - |  | -
S729-IR-53 | Hydrostatic test report |  | Pressure Test Report | No | For Information |  | - | - |  | -
S729-IR-46 | Non-destructive examination (NDE) personnel qualification |  | Non Destructive Examination (NDE) Personnel Qualification | No | For Information |  | - | - |  | -
S729-IR-52 | Non-destructive examination (NDE) report |  | Non-Destructive Examination (NDE) Report | No | For Acceptance |  | - | - |  | -
S729-IR-48 | Positive material identification (PMI) records |  | Positive Material Identification (PMI) Records | No | For Information |  | - | - |  | -
S729-IR-51 | Factory acceptance test (FAT) records |  | Factory Acceptance Test (FAT) Records | No | For Information |  | - | - |  | -
S729-IR-50 | Welding procedure qualification record |  | Welding Procedure Qualification Record | No | For Information |  | - | - |  | -
S729-IR-67 | Welder performance qualification records |  | Welder qualification certificate | No | For Information |  | - | - |  | -
S729-IR-47 | Painting and coating system qualification | Required for CAS A, CAS B | Painting And Coating System Qualification | - | - |  | - | - |  | -
S729-IR-69 | Painting and coating inspection records |  | Painting and Coating Inspection Records | No | For Information |  | - | - |  | -
S729-IR-37 | Spare part list |  | Spare Part List | No | For Information |  | - | - |  | - | Owner/lifecycle information required for maintenance.
S729-IR-30 | Fugitive emission type test certificate (applicable if fugitive emission packing is specified) |  | General certificate | No | For Information |  | - | - |  | -
S729-IR-24 | Hazardous area certificate (type) for actuator control equipment |  | Hazardous Area Certificate (Type) | No | For Information |  | - | - |  | -
S729-IR-28 | Ingress protection certificate for actuator control equipment |  | General certificate | No | For Information |  | - | - |  | -
S729-IR-34 | Failure data or safety integrity level (SIL) Certificate (applicable for components used in safety instrumented function) |  | Safety Integrity Level (SIL) Certificate | No | For Information |  | - | - |  | -
S729-IR-39 | Installation manual |  | Installation Manual | No | For Information |  | - | - |  | - | Installation manual index, if required, should be provided in first revision of the document. When index agreed, Installation manual content shall be provided in subsequent revision of the document.
S729-IR-41 | Operating manual |  | Operating Manual | No | For Information |  | - | - |  | - | Owner/lifecycle information required for operations.
S729-IR-29 | Maintenance manual |  | Maintenance Manual | No | For Information |  | - | - |  | - | Maintenance manual index, if required, should be provided in first revision of the document. When index agreed, Maintenance manual content shall be provided in subsequent revision of the document.
S729-IR-20 | Declaration of conformity |  | Declaration Of Conformity | No | For Information |  | - | - |  | -
S729-IR-76 | Manufacturer record book (MRB) |  | Manufacturer record book (MRB) | No | For Acceptance |  | - | - |  | - | Manufacturer Record Book (MRB) index to be provided in first revision of the document.
Purchase Order Specific Information Requirements

## Definitions
IOGP S-729L (1.01) Information Requirements for Control Valves
Definitions
Column | Heading - Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Discipline Document Type Code — CFIHOS discipline document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Deliverables
S729-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the manufacturer and accepted by the purchaser to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines: — information deliverable type, title/description; — unique identification (code/number) in the manufacturer's format; — planned submission arrangements including; purpose, formats, timing, frequency. Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S729-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by the manufacturers. Schedule details typically** include: — contractual milestones; — activity early/late start/completion dates, durations, dependencies (Calendar Dates); — critical path and float; — outsourced services and equipment (cross-referenced to purchase order and supplier); — information deliverable submission dates identifying any execution activity dependencies. Progress against planned dates are measured and the schedule updated and reported to the purchaser in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the manufacturer's standard practice or follow contractual formats if agreed. |  | PDF | CFIHOS-70000298
S729-IR-3 | Progress report | A report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities. Note: The progress report may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S729-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the manufacturers, and when applicable sub-suppliers, to deliver the services or procured item(s) in conformance with the agreed requirements. |  | PDF | CFIHOS-70000451
S729-IR-5 | Sub-supplier list | Definition of processes, products or services that will be externally provided and the controls to be applied by the manufacturer to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment, quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . Note: ISO 9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. |  | Native | CFIHOS-70000455
S729-IR-6 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated manufacturer, purchaser and independent conformity assessment activities. | 14.1.1.3, 14.1.10, 14.1.2, 14.1.3, 14.1.4.1, 14.1.5.1, 14.1.6, 14.1.7, 14.1.8.2, 14.1.8.4, 14.1.8.5, 14.1.9, 14.2.1, 14.2.2, 14.2.3, 14.2.5, 14.2.6.1, 14.2.6.2, 14.2.6.3.1, Table 13, Table 14, Table 15 | PDF | CFIHOS-70000180
S729-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: — packaging requirements e.g. contents, identification, size, weight and number of packages/container (s); — special packing/unpacking/handling requirements; — storage location and requirements; — preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post-installation, but prior to commissioning. | Clause 17 | PDF | CFIHOS-70000154
S729-IR-8 | Non-conformance records | Details of non-conformances raised by or to the manufacturer against technical requirements before or during the delivery of the products or services. Non-conformance is managed by the manufacturer in accordance with ISO 9001, 8.7 and associated records typically include the description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection that has taken place to demonstrate subsequent conformance. Note: Instances, where the proposed disposition is to accept a non-conforming condition, are subject to agreement by the purchaser in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S729-IR-9 | Concession requests | A concession request is a formal request from the manufacturer's seeking the purchaser's agreement to accept deviations from the contracted scope or technical requirements. Such requests may be raised as a result of e.g. material or service availability, obsolescence, innovation and non-conformance. Concession requests are typically raised as required during execution with a summary report detailing concessions raised, purchaser approval status, agreed action status provided. Concession requests should be submitted as part of progress reports and during contract closeout. |  | PDF | CFIHOS-70000260
Technical Information Deliverables
S729-IR-26 | General arrangement diagram | General arrangement drawing shall include the following information: — overall dimensions; — critical interface dimensions; — connection size; — connection rating; — make and model number of valve, actuator and actuator control equipment; — bill of materials for accessories with its part references; — material for valve components; — components mounted on the actuator with its tubing; — travel indicator with markings; — travel stop details; — handwheel diameter (if applicable), breakaway torque/thrust and handwheel open/close direction marking; — earthing details; — junction box details, inlet/outlet connections; — flow direction markings; — interface connection details viz. cable entries and tube connections; — weight of complete assemblies; — termination details; — bonnet bolting arrangement; — pipe insulation thickness. — lifting arrangement. The drawing must include references to the design standards. For equipment/components, the drawing may include cross-sectional views. The drawing may contain the following additional information: — centre of gravity; — withdrawal/installation and maintenance space. | 4.2, 5.1, 5.2, 5.3.2, 6.1.2, 6.1.3, 6.2, 6.3, 6.5.1, 6.5.3, 6.6.3, 6.7, 6.8.1, 6.8.3, 7.2.4, 7.4.2, 9.1, 9.3, 10.1.1, 10.1.2, 10.1.5, 10.1.7, 10.1.11, 10.1.12, 10.2.1, 10.4, 10.5, 11.1.1, 11.1.2, 11.1.3, 11.4.1, 11.4.3, 11.5, 12.1.2, 12.1.3, 12.4.4, 12.5.2, 12.5.3, 12.8, 16.3, Table 2 through Table 12 | PDF | CFIHOS-70000153
S729-IR-62 | Pneumatic schematics including hook-up information | This document shall provide pneumatic hook-up information for actuator control equipment to demonstrate the specified functionality. To be prepared for valve assemblies with instrumentation, buffer vessel and pneumatic control panels. All components and interconnection between units to be identified. Actuator control equipment user interfaces type and size shall be identified. The information requested in this document can be part of a general arrangement diagram. | 11.1.4, 11.3, 12.2.1, 12.4.3, 12.6, 12.7.2, 12.7.3, 12.9, 12.10 | PDF | CFIHOS-70000170
S729-IR-23 | Control valve sizing calculations | The sizing calculation shall indicate the inputs used for sizing and the results of the valve sizing calculations for the operating parameters specified indicating the following: — flow coefficient); — sound pressure level dBA (noise); — valve opening; — coefficients such as FL and XT; — cavitation index; — choked flow pressure drop; and — rated flow coefficient. | 5.2.2, 6.1.1, 8.1, 8.2, 8.3.2, 8.4, 8.5, Table 1 | PDF | CFIHOS-70000086
S729-IR-33 | Actuator sizing calculations | The actuator sizing calculations shall indicate the inputs to arrive at a specific actuator model e.g. minimum network supply pressure, differential pressure shutoff, unbalanced, frictional, seating forces and safety factor with equations, definition for the variables and outputs e.g. torque/thrust, safety factor. | 8.1.1, 11.2 | PDF | CFIHOS-70000086
S729-IR-55 | Pressure vessel (air receiver) design calculation | Sizing calculation shall include the basic conditions and assumptions used for the selection of appropriate system solutions, parts or material, as well as the way these data have been processed and evaluated: a. Mandatory content of information: — calculation methods used; — formula; — international standard reference number; — input data; — results; — analysis of the results. b. Optional content of information: — case studies; — verification of different technical solutions. | 12.7.1 | PDF | CFIHOS-70000086
S729-IR-21 | Manufacturer datasheet | Data sheet shall provide information about technical data and characteristics about material, products or systems and their environment for implementation. This document shall provide structured data format containing part/model number, design information, operational data and limitations of the valve, actuator and actuator control equipment. | 4.1, 5.3.2, 10.1.1, 10.1.2, 10.1.7, 10.1.9, 10.2.1, 10.4, 10.5.3, 10.5.4, 10.5.5, 13.1, Clause 15, Table 2 through Table 12 | Native | CFIHOS-70000416
S729-IR-38 | Utility consumption details (electrical and pneumatic) | A document stating the utility requirements for the following: a. Solenoid valves: — tag number; — steady-state and maximum power consumption; — power supply (V AC or V DC). b. Positioner: — tag number; — steady-state and maximum air consumption. Note: This deliverable may not be required for replacing the existing control valves by the new control valves. |  | PDF | CFIHOS-70000203
S729-IR-36 | Equipment cross section diagram | A cross-sectional drawing shall include the manufacturer's parts list and material definitions with relevant standards to facilitate dismantling, repair and assembly of parts and components. | 7.1, 7.2.1, 7.2.2, 7.2.3, 7.4.3, 10.1.1, 10.1.6, 10.1.7, 10.1.9, 10.2, 11.1.4, Table 3 through Table 12 | PDF | CFIHOS-70000116
S729-IR-64 | Manufacturer's product catalog or product data sheet | A document that defines the product features, functional description operating and ambient conditions, decoding details of the quoted model, performance capabilities, dimensional details, weights, design and testing standards and interface details that fulfill the purchaser's technical requirements. | Clause 4, 5.2.1 , 5.3.1, 6.3.1, 6.3.2, 6.3.3, 6.5, 6.6.3, 7.2.4, 7.4.1, 7.4.3, 8.3, 11.3.2, 11.3.4, 11.4, 12.1.1, 12.2.2, 12.2.3, 12.2.4, 12.3.1, 12.3.2, 12.3.3.3, 12.3.4, 12.4.1, 12.4.2, 12.5.1, 13.1, Table 12 | PDF | CFIHOS-70000416
S729-IR-44 | Hydrostatic test procedure | A procedure to document specific steps involved to inspect an asset/object. Typically details boundaries of the test, isolations, method of pressurization, required hold intervals, water quality, draining and drying, etc. This procedure can include hydrostatic, pneumatic, vacuum and leak tests and their acceptance criteria. | 14.1.4 | PDF | CFIHOS-70000286
S729-IR-43 | Non-destructive test procedure | This document is a part of the Quality Assurance Plan, and herein the Quality Assurance work process and verification. This document provides a procedure for NDT operators to ensure repeatability and formalism and hence prove the quality of the NDT work. This document should describe how to perform NDT (i.e. MT, PT, RT, UT, VT or ET) for a given object, including acceptance criteria and reporting | 14.1.10, A.1 through A.8, Table A.1, Table A.2 | PDF | CFIHOS-70000227
S729-IR-72 | Heat treatment procedure | A procedure detailing heating, soak, cooling parameters, temperature ranges, method of attachment of thermocouples, temperature control, equipment calibration, production testing, etc. | Table 3 through Table 11 | PDF | CFIHOS-70000147
S729-IR-54 | Positive material identification (PMI) procedure | Procedure describing the method and acceptance criteria for material identification by elemental analysis. Methods typically conform to ASTM E415 for carbon and low alloy steels and ASTM E1086 for austenitic stainless steels and guidelines in API RP578. | 14.1.9 | PDF | CFIHOS-70000227
S729-IR-42 | Factory acceptance test (FAT) procedure | The FAT procedure shall detail testing activities, acceptance criteria in accordance with applicable standards, specifications, requirements and document the condition of the equipment as tested from the factory. Test set-up and test equipment shall be defined. Manufacturer's standard (routine) test procedures should be used as far as possible. | 7.3, 11.5.3, 12.5.4, 12.7.1, 13.2.3, 13.2.4, 13.2.5, 14.1.1.3, 14.1.1.4, 14.1.2, 14.1.3, 14.1.5, 14.1.6, 14.1.7, 14.1.8, 14.1.11, 14.2.1, 14.2.2, 14.2.3, 14.2.5, Table 13 | PDF | CFIHOS-70000427
S729-IR-60 | Cryogenic testing (FAT) procedure | The cryogenic FAT procedure shall detail testing activities, acceptance criteria in accordance with applicable standards, specifications, requirements and document the condition of the equipment as tested from the factory. Test set-up and test equipment shall be defined. | 7.3, 11.5.3, 12.7.1, 14.1.1.3, 14.1.1.4, 14.1.2, 14.1.3, 14.1.5.2, 14.1.5.3, 14.1.5.4, 14.1.6, 14.1.8.1, 14.1.8.2, 14.2.5, 14.2.6, 14.2.6.3, Table 14, Table 15 | PDF | CFIHOS-70000427
S729-IR-65 | Welding procedure specification | A specification that describes the welding procedure and process of a specific set of essential variables. | 10.3, 10.4, 10.5.1, 10.5.2, 10.5.3, 10.5.5 | PDF | CFIHOS-70000408
S729-IR-49 | Welding repair procedure | A document that describes a set of logically sequenced instructions to execute a weld repair. | 10.3.1 | PDF | CFIHOS-70000363
S729-IR-75 | Welding traceability records | Welding records are presented as data sets, plans, drawings and/or maps. Welding records typically provide traceability for the following. — Weld number and welders identification — Welding procedure specification number — NDE results with NDE report number — Weld repairs and weld repair procedure number — PWHT report number — Weld maps for traceability of each weld to applicable WPS, Welder, consumable batch and NDE reports | 10.3.1, 10.3.2, A.8 | PDF | CFIHOS-70000360
S729-IR-27 | Painting and coating procedure | The objective of this procedure is to: — translate user-specific requirements to the manufacturer's procedure; — detail step-by-step instructions that aid the coating operators to ensure repeatable performances that prove the quality of the coating work; — verify the manufacturer's compliance with this procedure; — cover coating and painting for actuator and control valve separately. A procedure may cover wet paint, powder coating, or metallic coatings. The document shall include references to applied standards and standards revision. | 15.1, 15.2, 15.4 | PDF | CFIHOS-70000384
S729-IR-57 | Lifting hook or fixture load safety factor calculations | The document provides calculations to prove the soundness of the lifting hook or fixture and its welding to prove the safety factor requested. Indicate the equations, constants and units used. | 6.8.2 | PDF | CFIHOS-70000086
S729-IR-71 | Manufacturing qualification procedure test reports | Qualification test records establishing conformance to associated acceptance criteria and test methods. (Source: NORSOK M-650) | Table 5, Table 6, Table 8, Table 9 | PDF | CFIHOS-70000245
S729-IR-32 | Materials inspection certificate (3.1) for pressure containing and retaining parts, ball, plug, disk, cage, seat ring, bellows and air receiver | A document with test results based on specific inspection and testing, issued by the Manufacturer and validated by the Manufacturer's authorized inspection representative independent of the manufacturing department in accordance with ISO 10474 / EN 10204 and ISO/IEC 17000. For trim parts, this requirement applies to QSL-3 and QSL-4. | 6.8.2, 10.1.3, 10.1.4, 10.1.5, 10.1.6, 10.1.7, 10.1.8, 10.1.9, 10.2.1, 10.4, 10.5, Table 3 through Table 11 | PDF | CFIHOS-70000412
S729-IR-63 | Declaration of compliance (2.1) for seals, gaskets and packing assembly | A document in which the manufacturer declares that the products supplied are in compliance with the requirements of the PO, without inclusion of any test results. NOTE: see ISO/IEC 17000, clause 5.5 and ISO 10474 / EN 10204. | 6.4, 10.1.3, 10.1.4, 10.1.7, 10.1.9, 10.2.1, 10.5 | PDF | CFIHOS-70000431
S729-IR-70 | Material inspection report (2.2) for ball, plug, disk, cage, seat ring in QSL-1 and QSL-2 valve | Document in which the manufacturer declares that the products supplied are in compliance with the requirements of the order and in which he supplies test results based on non-specific inspection, i.e. inspection carried out by the manufacturer in accordance with his own procedures and where the products inspected are not necessarily the products actually supplied. | Table 3 through Table 11 | - | CFIHOS-70000412
S729-IR-68 | Certificate of conformance for the finished valve assembly (Sour service) | The manufacturer will provide a certificate of conformance to ANSI/NACE MR0175/ISO 15156 or ISO17945/MR0103. | 10.4 | PDF | CFIHOS-70000013
S729-IR-53 | Hydrostatic test report | A report containing information's about the tests, e.g. test pressure, test medium, test duration, results of hydrostatic, pneumatic and leak test examinations and test standard to which the product has been tested. | 14.1.4.1, 14.2.6.2, Table 15 | PDF | CFIHOS-70000287
S729-IR-46 | Non-destructive examination (NDE) personnel qualification | Records demonstrating competence of NDE personnel in accordance with recognized certification program ASNT or ISO. | 14.1.10, A.5, A.6, A.9 | PDF | CFIHOS-70000437
S729-IR-52 | Non-destructive examination (NDE) report | Records to document the compliance with the specified procedures and performed NDT methods (in typical NDT methods e.g. MT, PT, RT, UT, ET and VT). | 14.1.10, A.1, A.2, A.8, Table A.1, Table A.2 | PDF | CFIHOS-70000446
S729-IR-48 | Positive material identification (PMI) records | Result of Positive Material Identification testing to a defined procedure confirming materials subject to PMI are of the specified material grade. Note: PMI results do not constitute material certification. | 14.1.9 | PDF | CFIHOS-70000446
S729-IR-51 | Factory acceptance test (FAT) records | The FAT report shall demonstrate that the equipment has been tested in accordance with the FAT procedure. The FAT report is typically used for acceptance of the equipment delivery. This document shall include all testing activities and their acceptance criteria according to the FAT procedure, to applicable standards, specifications and requirements, to document the condition of the equipment as tested from the factory. Test set-up and test equipment shall be defined. | 12.5.4, 13.2.5, 14.1.1.3, 14.1.2, 14.1.3, 14.1.5.1, 14.1.6, 14.1.7, 14.1.8, 14.1.11, 14.2.1, 14.2.2, 14.2.3, 14.2.5, 14.2.6.1, 14.2.6.3, Table 13, Table 14, Table 15 | PDF | CFIHOS-70000429
S729-IR-50 | Welding procedure qualification record | Records to document the welding and associated testing of welding processes to a defined set of essential variables. Typically includes all testing procedure references and both destructive and non-destructive testing results. | 10.3, 10.4 | PDF | CFIHOS-70000362
S729-IR-67 | Welder performance qualification records | Records demonstrating that a welder is qualified to perform work to defined WPSs in accordance with the specified welding code or welding specification. | 10.3.1 | PDF | CFIHOS-70000413
S729-IR-47 | Painting and coating system qualification | Test results establishing coating system conformance with the painting and coating procedure. | 15.1, 15.3, 15.4 | PDF | CFIHOS-70000245
S729-IR-69 | Painting and coating inspection records | This document is used for verification of compliance with surface protection and coating requirements. Document containing records of performed surface protection and coating work. | 15.1, 15.2, 15.4 | PDF | CFIHOS-70000245
S729-IR-37 | Spare part list | A table containing list items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for later use. Mandatory content of information: — item reference number; — quantity; — part number or global identifier (together with manufacturer/supplier); — part name. Optional content of information: — type designation; — specifying technical data; — descriptive technical data; — mass, dimensions; — reference to document; — remark. |  | Native | CFIHOS-70000374
S729-IR-30 | Fugitive emission type test certificate (applicable if fugitive emission packing is specified) | A type test certificate issued by an independent authority for the specified fugitive emission, temperature and endurance class in accordance with ISO 15848-1 or ANSI/FCI 91-1 standard. The certificate should include the model number, pressure class, stem diameter, packing material, temperature class, endurance class, leakage class, measured leakage rate at temperature and drawing number. | 6.6.1, 6.6.2 | PDF | CFIHOS-70000239
S729-IR-24 | Hazardous area certificate (type) for actuator control equipment | A type test certificate issued by an independent authority e.g. ATEX, BASEEFA, PTB, UL, CSA, NEMA, EX for each type of electrical or electronic equipment for the specified hazardous area classification in accordance with IEC 60079 or NFPA 70. |  | PDF | CFIHOS-70000160
S729-IR-28 | Ingress protection certificate for actuator control equipment | A type test certificate issued by approved bodies for each type of equipment to demonstrate the ingress protection rating in accordance with IEC 60529 or NEMA 250. | 12.1.4 | PDF | CFIHOS-70000239
S729-IR-34 | Failure data or safety integrity level (SIL) Certificate (applicable for components used in safety instrumented function) | The manufacturer shall include failure data for components involved in safety instrumented function or a SIL certificate for the assembly to establish conformance to IEC 61508. | 9.2 | PDF | CFIHOS-70000433
S729-IR-39 | Installation manual | Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. NOTE: Installation manual can be delivered as part of the manufacturer's standard Installation, operation and maintenance manual or as a standalone document. | 6.8.1, 6.8.3 | PDF | CFIHOS-70000181
S729-IR-41 | Operating manual | Description of methods of operating a piece of equipment or process unit, including but not limited to instructions, procedures, drawings, tables, etc. for the operation -stop, start, and emergency shutdown. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. The supplier shall issue a statement of confirmation for section 11.5.4 as part of the Operating manual. NOTE: Operating manual can be delivered as part of the manufacturer's standard Installation, operation and maintenance manual or as a standalone document. | 11.5.4 | PDF | CFIHOS-70000228
S729-IR-29 | Maintenance manual | Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package supplier. Manufacturer to provide torque values for bolted connections in pressure containing parts, e.g. body/bonnet, gland packing. NOTE: Maintenance manual can be delivered as part of the manufacturer's standard Installation, operation and maintenance manual or as a standalone document. | 6.8.1, 6.8.3 | PDF | CFIHOS-70000206
S729-IR-20 | Declaration of conformity | A declaration that contains information's to enable the recipient of the declaration of conformity to identify the issuer of the declaration, the object of the declaration, the standards and other specified requirements with which conformity is declared, and the person signing for and on behalf of the issuer of the declaration of conformity (first party). ISO/IEC 17000 and ISO/IEC 17050-1 can be used as the basis for providing declaration of conformity. | 1.1, 10.4 | PDF | CFIHOS-70000431
S729-IR-76 | Manufacturer record book (MRB) | Detailed information/description of the documents to be included in the MRB is to be agreed between the Purchaser and the Vendor. The MRB shall include but not be limited to the following. a. Documents recording compliance with statutory and/or local regulations b. Inspection and testing results / reports for all the testing (e.g. mill tests on material, production test coupon results, NDE, NDE personnel qualification, impact test, heat treatment, leak testing, etc.) c. Certificates d. Welding procedure specification, Welding repair procedure, Welding traceability records, Welding procedure qualification record, Welder performance qualification records The MRB index is to be provided in first revision of the document. Subsequent versions of the MRB to contain the documentation as per the agreed MRB Index. |  | PDF | CFIHOS-70000178
Purchase Order Specific Information Requirements

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: