## Addendum 1
Date of issue:
February 2026
Affected publication:
IOGP S-749D, Procurement Data Sheet for Plate-and-frame Heat Exchangers (API), First Edition, December 2023
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in December 2023.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Row | Column | Update
| 191 | All | New data sheet item "Port holes on movable cover for maintenance"
| 192 to 236 | Row | Rows 191 * to 235 * renumbered to 192 to 236
| 230 | Description | Description amended Default value added to embedded guidance note
|  | Purchaser requirement / Supplier offered value | Default value "2%" added
|  | Purchaser requirement / Supplier offered value - options | Options "100 % of plates and welds, 10 % of heat transfer plates and 100 % of welds, none, other" * replaced with "2%, 10%, 100%, other"
* Data from Edition 1.0.

## Front & Preliminaries
[5 empty] | SPECIFICATION | February 2026
[5 empty] | IOGP S-749D | Version 1.01
ADDENDUM 1 TO FIRST EDITION (DECEMBER 2023)
Procurement Data Sheet for
Plate-and-frame Heat Exchangers (API)
Revision history
| VERSION | DATE | PURPOSE
| 1.01 | February 2026 | Addendum 1
| 1 | December 2023 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-749D (1.01) Procurement Data Sheet for
Plate-and-frame Heat Exchangers (API)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-749D (1.01) Procurement Data Sheet for
Plate-and-frame Heat Exchangers (API)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of plate-and-frame heat exchangers in accordance with IOGP S-749 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-749), information requirements specification (IOGP S-749L) and quality requirements specification (IOGP S-749Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)

## Procurement Data Sheet
Row | IOGP S-749D (1.01) Procurement Data Sheet for Plate-and-frame Heat Exchangers (API) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 | 6.1.1 | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 | 4.6, 6.1.1 | Project country : | input data |  | input data
9 | 4.6, 6.1.1 | Project region : | input data |  | input data
10 | 6.1.1, 7.7.17 | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | onshore
11 |  | Case
12 | Table B.1 Continuation | Utility service : | select |  | select | [5 empty] | select | yes | no
13 | 7.8.6, Table A.1, Table B.1 Continuation | Fluid name - hot side : | input data |  | input data
14 | 7.8.6, Table A.1, Table B.1 Continuation | Fluid name - cold side : | input data |  | input data
15 | 5.8 | Total flow - hot side : | input data | select | input data | select |  |  |  |  | select | kg/s | Ib/h
16 | 5.8 | Total flow - cold side : | input data | select | input data | select |  |  |  |  | select | kg/s | Ib/h
17 | 6.1.1, 7.1.5, 7.2.1, 7.2.2, 7.8.6,Table 2 | Maximum design temperature - hot side : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 6.1.1, 7.1.5, 7.2.1,7.2.2, 7.8.6,Table 2 | Maximum design temperature - cold side : | input data | select | input data | select |  |  |  |  | select | °C | °F
19 | 6.1.1, 7.1.5, 7.2.1, 7.2.2, 8.1.7, 8.1.8 | Minimum design metal temperature - hot side : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 | 6.1.1, 7.1.5, 7.2.1, 7.2.2, 8.1.7, 8.1.8 | Minimum design metal temperature - cold side : | input data | select | input data | select |  |  |  |  | select | °C | °F
21 | 6.1.1, 7.1.5, 7.3, 7.6.1, 7.8.6 | Design pressure - hot side : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
22 | 6.1.1, 7.1.5, 7.3, 7.6.1, 7.8.6 | Design pressure - cold side : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
23 | 5.10, 7.4, Table A.1, Table B.1 Continuation | Pressure drop allowable - hot side : | input data | select | input data | select |  |  |  |  | select | kPa | psi
24 | 5.10, 7.4, Table A.1 | Pressure drop calculated - hot side : | input data | select | input data | select |  |  |  |  | select | kPa | psi
25 | 5.10, 7.4, Table A.1, Table B.1 Continuation | Pressure drop allowable - cold side : | input data | select | input data | select |  |  |  |  | select | kPa | psi
26 | 5.10, 7.4, Table A.1 | Pressure drop calculated - cold side : | input data | select | input data | select |  |  |  |  | select | kPa | psi
27 | 5.1 | Port calculated pressure drop inlet - hot side : | input data | select | input data | select |  |  |  |  | select | kPa | psi
28 | 5.1 | Port calculated pressure drop outlet - hot side : | input data | select | input data | select |  |  |  |  | select | kPa | psi
29 | 5.1 | Port calculated pressure drop inlet - cold side : | input data | select | input data | select |  |  |  |  | select | kPa | psi
30 | 5.1 | Port calculated pressure drop outlet - cold side : | input data | select | input data | select |  |  |  |  | select | kPa | psi
31 | 5.11 | Port velocity - hot side inlet : | input data | select | input data | select |  |  |  |  | select | m/s | ft/s
32 | 5.11 | Port velocity - hot side outlet : | input data | select | input data | select |  |  |  |  | select | m/s | ft/s
33 | 5.11 | Port velocity - cold side inlet : | input data | select | input data | select |  |  |  |  | select | m/s | ft/s
34 | 5.11 | Port velocity - cold side outlet : | input data | select | input data | select |  |  |  |  | select | m/s | ft/s
35 | 5.8 | Minimum wall temperature - hot side : | input data | select | input data | select |  |  |  |  | select | °C | °F
36 | 5.8 | Maximum wall temperature - hot side : | input data | select | input data | select |  |  |  |  | select | °C | °F
37 | 5.8 | Minimum wall temperature - cold side : | input data | select | input data | select |  |  |  |  | select | °C | °F
38 | 5.8 | Maximum wall temperature - cold side : | input data | select | input data | select |  |  |  |  | select | °C | °F
39 | 7.4, Equation 1, A.3.2.1,Table A.1 footnote e, Table A.1 | Fouling margin - hot side : | input data | % | input data | %
40 | 7.4, Equation 1, A.3.2.1,Table A.1 footnote e, Table A.1 | Fouling margin - cold side : | input data | % | input data | %
41 | 7.4, Table A.1, Table B.1 Continuation | Pressure drop multiplier - hot side : | input data |  | input data
42 | 7.4, Table A.1, Table B.1 Continuation | Pressure drop multiplier - cold side : | input data |  | input data
43 |  | Operating data
44 | 5.8 | Liquid flow - hot side inlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
45 | 5.8 | Liquid flow - hot side outlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
46 | 5.8 | Liquid flow - cold side inlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
47 | 5.8 | Liquid flow - cold side outlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
48 | 5.8 | Vapor flow - hot side inlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
49 | 5.8 | Vapor flow - hot side outlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
50 | 5.8 | Vapor flow - cold side inlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
51 | 5.8 | Vapor flow - cold side outlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
52 | 5.8 | Non-condensable flow - hot side inlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
53 | 5.8 | Non-condensable flow - hot side outlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
54 | 5.8 | Non-condensable flow - cold side inlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
55 | 5.8 | Non-condensable flow - cold side outlet : | input data | select | input data | select |  |  |  |  | select | kg/s | lb/h
56 | 5.5, 7.8.6 | Operating temperature - hot side inlet : | input data | select | input data | select |  |  |  |  | select | °C | °F
57 | 5.5, 7.8.6 | Operating temperature - hot side outlet : | input data | select | input data | select |  |  |  |  | select | °C | °F
58 | 5.5, 7.8.6 | Operating temperature - cold side inlet : | input data | select | input data | select |  |  |  |  | select | °C | °F
59 | 5.5, 7.8.6 | Operating temperature - cold side outlet : | input data | select | input data | select |  |  |  |  | select | °C | °F
60 | 5.5 | Operating pressure - hot side inlet : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
61 | 5.5 | Operating pressure - hot side outlet : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
62 | 5.5 | Operating pressure - cold side inlet : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
63 | 5.5 | Operating pressure - cold side outlet : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
64 |  | Liquid properties
65 | 5.8 | Density of liquid - hot side inlet : | input data | select | input data | select |  |  |  |  | select | kg/m³ | lb/ft³
66 | 5.8 | Density of liquid - hot side outlet : | input data | select | input data | select |  |  |  |  | select | kg/m³ | lb/ft³
67 | 5.8 | Density of liquid - cold side inlet : | input data | select | input data | select |  |  |  |  | select | kg/m³ | lb/ft³
68 | 5.8 | Density of liquid - cold side outlet : | input data | select | input data | select |  |  |  |  | select | kg/m³ | lb/ft³
69 | 5.8 | Specific heat capacity of liquid - hot side inlet : | input data | select | input data | select |  |  |  |  | select | kJ/kg·K | BTU/lb·°R
70 | 5.8 | Specific heat capacity of liquid - hot side outlet : | input data | select | input data | select |  |  |  |  | select | kJ/kg·K | BTU/lb·°R
71 | 5.8 | Specific heat capacity of liquid - cold side inlet : | input data | select | input data | select |  |  |  |  | select | kJ/kg·K | BTU/lb·°R
72 | 5.8 | Specific heat capacity of liquid - cold side outlet : | input data | select | input data | select |  |  |  |  | select | kJ/kg·K | BTU/lb·°R
73 | 5.8 | Dynamic viscosity of liquid - hot side inlet : | input data | select | input data | select |  |  |  |  | select | mPa·s | cP
74 | 5.8 | Dynamic viscosity of liquid - hot side outlet : | input data | select | input data | select |  |  |  |  | select | mPa·s | cP
75 | 5.8 | Dynamic viscosity of liquid - cold side inlet : | input data | select | input data | select |  |  |  |  | select | mPa·s | cP
76 | 5.8 | Dynamic viscosity of liquid - cold side outlet : | input data | select | input data | select |  |  |  |  | select | mPa·s | cP
77 | 5.8 | Thermal conductivity of liquid - hot side inlet : | input data | select | input data | select |  |  |  |  | select | W/m·K | BTU/h·ft·°R
78 | 5.8 | Thermal conductivity of liquid - hot side outlet : | input data | select | input data | select |  |  |  |  | select | W/m·K | BTU/h·ft·°R
79 | 5.8 | Thermal conductivity of liquid - cold side inlet : | input data | select | input data | select |  |  |  |  | select | W/m·K | BTU/h·ft·°R
80 | 5.8 | Thermal conductivity of liquid - cold side outlet : | input data | select | input data | select |  |  |  |  | select | W/m·K | BTU/h·ft·°R
81 | 5.8 | Surface tension of liquid - hot side inlet : | input data | select | input data | select |  |  |  |  | select | N/m | dyn/cm
82 | 5.8 | Surface tension of liquid - hot side outlet : | input data | select | input data | select |  |  |  |  | select | N/m | dyn/cm
83 | 5.8 | Surface tension of liquid - cold side inlet : | input data | select | input data | select |  |  |  |  | select | N/m | dyn/cm
84 | 5.8 | Surface tension of liquid - cold side outlet : | input data | select | input data | select |  |  |  |  | select | N/m | dyn/cm
85 |  | Vapor properties
86 | 5.8 | Density of vapor - hot side inlet : | input data | select | input data | select |  |  |  |  | select | kg/m³ | lb/ft³
87 | 5.8 | Density of vapor - hot side outlet : | input data | select | input data | select |  |  |  |  | select | kg/m³ | lb/ft³
88 | 5.8 | Density of vapor - cold side inlet : | input data | select | input data | select |  |  |  |  | select | kg/m³ | lb/ft³
89 | 5.8 | Density of vapor - cold side outlet : | input data | select | input data | select |  |  |  |  | select | kg/m³ | lb/ft³
90 | 5.8 | Specific heat capacity of vapor - hot side inlet : | input data | select | input data | select |  |  |  |  | select | kJ/kg·K | BTU/lb·°R
91 | 5.8 | Specific heat capacity of vapor - hot side outlet : | input data | select | input data | select |  |  |  |  | select | kJ/kg·K | BTU/lb·°R
92 | 5.8 | Specific heat capacity of vapor - cold side inlet : | input data | select | input data | select |  |  |  |  | select | kJ/kg·K | BTU/lb·°R
93 | 5.8 | Specific heat capacity of vapor - cold side outlet : | input data | select | input data | select |  |  |  |  | select | kJ/kg·K | BTU/lb·°R
94 | 5.8 | Dynamic viscosity of vapor - hot side inlet : | input data | select | input data | select |  |  |  |  | select | mPa·s | cP
95 | 5.8 | Dynamic viscosity of vapor - hot side outlet : | input data | select | input data | select |  |  |  |  | select | mPa·s | cP
96 | 5.8 | Dynamic viscosity of vapor - cold side inlet : | input data | select | input data | select |  |  |  |  | select | mPa·s | cP
97 | 5.8 | Dynamic viscosity of vapor - cold side outlet : | input data | select | input data | select |  |  |  |  | select | mPa·s | cP
98 | 5.8 | Thermal conductivity of vapor - hot side inlet : | input data | select | input data | select |  |  |  |  | select | W/m·K | BTU/h·ft·°R
99 | 5.8 | Thermal conductivity of vapor - hot side outlet : | input data | select | input data | select |  |  |  |  | select | W/m·K | BTU/h·ft·°R
100 | 5.8 | Thermal conductivity of vapor - cold side inlet : | input data | select | input data | select |  |  |  |  | select | W/m·K | BTU/h·ft·°R
101 | 5.8 | Thermal conductivity of vapor - cold side outlet : | input data | select | input data | select |  |  |  |  | select | W/m·K | BTU/h·ft·°R
102 |  | Common fluid properties
103 | 5.8 | Relative molecular mass - hot side inlet : | input data | select | input data | select |  |  |  |  | select | kg/kmol | lb/lb.mol
104 | 5.8 | Relative molecular mass - hot side outlet : | input data | select | input data | select |  |  |  |  | select | kg/kmol | lb/lb.mol
105 | 5.8 | Relative molecular mass - cold side inlet : | input data | select | input data | select |  |  |  |  | select | kg/kmol | lb/lb.mol
106 | 5.8 | Relative molecular mass - cold side outlet : | input data | select | input data | select |  |  |  |  | select | kg/kmol | lb/lb.mol
107 | 5.8 | Relative molecular mass, non-condensables - hot side : | input data | select | input data | select |  |  |  |  | select | kg/kmol | lb/lb.mol
108 | 5.8 | Relative molecular mass, non-condensables - cold side : | input data | select | input data | select |  |  |  |  | select | kg/kmol | lb/lb.mol
109 | 5.8 | Dew point / bubble point - hot side : | input data | select | input data | select |  |  |  |  | select | °C | °F
110 | 5.8 | Dew point / bubble point - cold side : | input data | select | input data | select |  |  |  |  | select | °C | °F
111 | 5.1, 7.4, Table B.1 Continuation | Solids maximum size - hot side : | 1 mm (0.04 in.) | select | 1 mm (0.04 in.) | select |  |  |  |  | select | mm | in.
112 | 5.1, 7.4, Table B.1 Continuation | Solids maximum size - cold side : | 1 mm (0.04 in.) | select | 1 mm (0.04 in.) | select |  |  |  |  | select | mm | in.
113 | 5.8, Table B.1 Continuation | Solids concentration (% volume) - hot side : | input data | % | input data | %
114 | 5.8, Table B.1 Continuation | Solids concentration (% volume) - cold side : | input data | % | input data | %
115 | 5.8 | Latent heat - hot side : | input data | select | input data | select |  |  |  |  | select | kJ/kg | BTU/lb
116 | 5.8 | Latent heat - cold side : | input data | select | input data | select |  |  |  |  | select | kJ/kg | BTU/lb
117 | 5.8 | Critical pressure - hot side : | input data | select | input data | select |  |  |  |  | select | kPa (abs) | psia
118 | 5.8 | Critical temperature - hot side : | input data | select | input data | select |  |  |  |  | select | °C | °F
119 | 5.8 | Critical pressure - cold side : | input data | select | input data | select |  |  |  |  | select | kPa (abs) | psia
120 | 5.8 | Critical temperature - cold side : | input data | select | input data | select |  |  |  |  | select | °C | °F
121 |  | Heat transfer data
122 | 5.8 | Total heat exchanged : | input data | select | input data | select |  |  |  |  | select | kW | BTU/h
123 | 5.1 | Overall heat transfer coefficient (U), clean : | input data | select | input data | select |  |  |  |  | select | W/m²·K | BTU/(h·ft²·°R)
124 | 5.8 | Log mean temperature difference (LMTD) : | input data | select | input data | select |  |  |  |  | select | °C | °F
125 | 5.8 | Effective mean temperature difference (EMTD) : | input data | select | input data | select |  |  |  |  | select | °C | °F
126 | 5.8 | Heat transfer area : | input data | select | input data | select |  |  |  |  | select | m² | ft²
127 | 5.8 | Stream heat transfer coefficient - hot side : | input data | select | input data | select |  |  |  |  | select | W/m²·K | BTU/(h·ft²·°R)
128 | 5.8 | Stream heat transfer coefficient - cold side : | input data | select | input data | select |  |  |  |  | select | W/m²·K | BTU/(h·ft²·°R)
129 | 5.8, A.3.2.1 | Overall heat transfer coefficient (U), service : | input data | select | input data | select |  |  |  |  | select | W/m²·K | BTU/(h·ft²·°R)
130 |  | Configuration for exchanger and plate details
131 | 5.9 | Number of exchangers (plate packs) in parallel : | input data |  | input data
132 | 5.9 | Number of exchangers (plate packs) in series : | input data |  | input data
133 | 5.8 | Heat transfer area total : | input data | select | input data | select |  |  |  |  | select | mm² | ft²
134 | 5.9 | Heat transfer area per plate : | input data | select | input data | select |  |  |  |  | select | mm² | ft²
135 | 5.9, 6.1.1 | Number of plates per exchanger : | input data |  | input data
136 | 6.1.1, 7.1.1 | Maximum number of plates per exchanger : | input data |  | input data
137 | 5.9 | Number of passes per pack - hot side : | input data |  | input data
138 | 5.9 | Number of passes per pack - cold side : | input data |  | input data
139 | 5.9 | Number of channels in each hot fluid pass : | input data |  | input data
140 | 5.9 | Number of channels in each cold fluid pass : | input data |  | input data
141 | 5.9 | Flow across the plate (diagonal or parallel) : | select |  | select | [5 empty] | select | diagonal | parallel
142 | 5.9, 6.1.1 | Relative directions of fluids : | select |  | select | [5 empty] | select | cocurrent | countercurrent
143 | 5.9 | Nominal plate gap : | input data | select | input data | select |  |  |  |  | select | mm | in.
144 | 5.9 | Nominal plate thickness : | input data | select | input data | select |  |  |  |  | select | mm | in.
145 | 5.9 | Plate chevron angle(s) : | input data | select | input data | select |  |  |  |  | select | degrees | radians
146 |  | Design data
147 | 4.1, 4.10, 4.11, 5.2, 6.1.1, 6.3.1 ,7.1.4, 7.7.1, 7.7.8, 9.1.1, 10.1.8, 10.1.10, 10.1.19, 10.1.22, 10.2.5 | Pressure design code : | input data |  | input data
148 | 8.2.2, Table B.1 Continuation | Material certificate type : | Type 3.1 - Material inspection certificate |  | Type 3.1 - Material inspection certificate | [5 empty] | select | Type 3.1 - Material inspection certificate | Type 2.2 - Material test report
149 | 10.3.2, Table B.1 Continuation | Code stamp : | select |  | select | [5 empty] | select | yes | no
150 | 4.7, 4.8, 6.1.1, 7.7.7, 8.2.2, 8.2.3, 9.1.5, 10.1.10 | Sour service or wet hydrogen sulfide service : | not applicable |  | not applicable | [5 empty] | select | ANSI/NACE MR0175/ISO15156 (all parts) | ANSI/NACE MR0103/ISO17945 | not applicable
151 | 10.1.10,4.7,8.2.2,9.1.5,8.2.3 | Sour service or wet hydrogen sulfide applicability side : | select |  | select | [5 empty] | select | hot side | cold side | both sides | not applicable
152 | 4.8, 10.1.7 | Sour service requirements to be applied where carbon steel is lined : | select |  | select | [5 empty] | select | yes | no
153 | 4.9, 6.1.1, 7.7.6, 7.7.7 | Cyclic service : | select |  | select | [5 empty] | select | yes | no
154 | 5.9 | Vendor data required for thermal verification : | select |  | select | [5 empty] | select | yes | no
155 | 4.2, 6.1.1, 9.1.1 | Structural welding code : | AWS D1.1 |  | AWS D1.1 | [5 empty] | select | AWS D1.1 | ASME BPVC Section IX | ISO 15607 | other
156 | 7.7.2 | Flange design code : | ASME B16.5 |  | ASME B16.5 | [5 empty] | select | ASME B16.5 | ASME B16.47 | other
157 | 4.7 | Applicable specifications : | input data |  | input data
158 | 4.6 | Plant regulations : | not applicable |  | not applicable
159 |  | Local register of exchanger : | input data |  | input data
160 | 6.1.1, 10.2.1 | Test pressure - hot side : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
161 | 6.1.1, 10.2.1 | Test pressure - cold side : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
162 | Table A.1 | Velocity between plates - hot side : | input data | select | input data | select |  |  |  |  | select | m/s | ft/s
163 | Table A.1 | Velocity between plates - cold side : | input data | select | input data | select |  |  |  |  | select | m/s | ft/s
164 | 7.4, Table A.1, Table B.1 Continuation | Wall shear stress - hot side clean : | input data | select | input data | select |  |  |  |  | select | Pa | psi
165 | 7.4, Table A.1, Table B.1 Continuation | Wall shear stress - cold side clean : | input data | select | input data | select |  |  |  |  | select | Pa | psi
166 | 6.1.1 | Volume per exchanger - hot side : | input data | select | input data | select |  |  |  |  | select | m³ | ft³
167 | 6.1.1 | Volume per exchanger - cold side : | input data | select | input data | select |  |  |  |  | select | m³ | ft³
168 | 5.1, 6.1.1 | Length : | input data | select | input data | select |  |  |  |  | select | mm | in.
169 | 5.1, 6.1.1 | Width : | input data | select | input data | select |  |  |  |  | select | mm | in.
170 | 5.1, 6.1.1 | Height : | input data | select | input data | select |  |  |  |  | select | mm | in.
171 | 5.1, 6.1.1 | Mass empty : | input data | select | input data | select |  |  |  |  | select | kg | lb
172 | 6.1.1 | Mass full of water : | input data | select | input data | select |  |  |  |  | select | kg | lb
173 | 4.11, 4.9 | Detailed fatigue analysis required : | select |  | select | [5 empty] | select | yes | no
174 |  | Connections
175 | 5.1, 6.1.1, 7.7.16 | Nozzle size - hot side inlet : | input data | select | input data | select |  |  |  |  | select | DN | NPS
176 | 5.1, 7.7.2, 7.7.3, 7.7.17 | Nozzle flange rating and facing - hot side inlet : | input data |  | input data
177 | 7.7.4, 7.7.5 | Nozzle flange type - hot side inlet : | weld neck |  | weld neck | [5 empty] | select | weld neck | long weld neck | slip-on | studded
178 | 5.1, 7.7.1, 7.7.2, 7.7.7, 10.1.4 | Nozzle connection design - hot side inlet : | select |  | select | [5 empty] | select | set-in | set-on | studded
179 | 5.1, 6.1.1, 7.7.16 | Nozzle size - hot side outlet : | input data | select | input data | select |  |  |  |  | select | DN | NPS
180 | 5.1, 7.7.2, 7.7.3, 7.7.17 | Nozzle flange rating and facing - hot side outlet : | input data |  | input data
181 | 7.7.4, 7.7.5 | Nozzle flange type - hot side outlet : | weld neck |  | weld neck | [5 empty] | select | weld neck | long weld neck | slip-on | studded
182 | 5.1, 7.7.1, 7.7.2, 7.7.7, 10.1.4 | Nozzle connection design - hot side outlet : | select |  | select | [5 empty] | select | set-in | set-on | studded
183 | 5.1, 6.1.1, 7.7.16 | Nozzle size - cold side inlet : | input data | select | input data | select |  |  |  |  | select | DN | NPS
184 | 5.1, 7.7.2, 7.7.3, 7.7.17 | Nozzle flange rating and facing - cold side inlet : | input data |  | input data
185 | 7.7.4, 7.7.5 | Nozzle flange type - cold side inlet : | weld neck |  | weld neck | [5 empty] | select | weld neck | long weld neck | slip-on | studded
186 | 5.1, 7.7.1, 7.7.2, 7.7.7, 10.1.4 | Nozzle connection design - cold side inlet : | select |  | select | [5 empty] | select | set-in | set-on | studded
187 | 5.1, 6.1.1, 7.7.16 | Nozzle size - cold side outlet : | input data | select | input data | select |  |  |  |  | select | DN | NPS
188 | 5.1, 7.7.2, 7.7.3, 7.7.17 | Nozzle flange rating and facing - cold side outlet : | input data |  | input data
189 | 7.7.4, 7.7.5 | Nozzle flange type - cold side outlet : | weld neck |  | weld neck | [5 empty] | select | weld neck | long weld neck | slip-on | studded
190 | 5.1, 7.7.1, 7.7.2, 7.7.7, 10.1.4 | Nozzle connection design - cold side outlet : | select |  | select | [5 empty] | select | set-in | set-on | studded
191 |  | Port holes on movable cover for maintenance : | select |  | select | [5 empty] | select | required | not required
192 |  | Component materials and construction
193 | 4.7 | Exchanger type : | select |  | select | [5 empty] | select | gasketed | semi-welded
194 | 4.7, 5.9, 8.2.2 | Heat transfer plates : | input data |  | input data
195 | 6.1.1, 7.8.2, Table B.1 Continuation | Gasket fixing : | select |  | select | [5 empty] | select | glued | not glued
196 | 6.1.1, 7.8.6, 7.2.2, Table 2,Table B.1 Continuation | Gasket - hot side : | input data |  | input data
197 | 6.1.1, 7.8.6, 7.2.2, Table 2,Table B.1 Continuation | Gasket - cold side : | input data |  | input data
198 | 8.2.2 | Cover fixed : | input data |  | input data
199 | 8.2.2 | Cover movable : | input data |  | input data
200 | 8.2.2 | Tie bolts : | input data |  | input data
201 | 8.2.2 | Tie nuts : | input data |  | input data
202 | 7.7.6, 8.2.2 | Nozzle pipes - hot side : | input data |  | input data
203 | 7.7.6, 8.2.2 | Nozzle pipes - cold side : | input data |  | input data
204 | 8.2.2 | Nozzle flanges - hot side : | input data |  | input data
205 | 8.2.2 | Nozzle flanges - cold side : | input data |  | input data
206 | 7.5.2, 6.1.1 | Corrosion allowance on connections - hot side : | 3 mm (1/8 in.) | select | 3 mm (1/8 in.) | select |  |  |  |  | select | mm | in.
207 | 7.5.2, 6.1.1 | Corrosion allowance on connections - cold side : | 3 mm (1/8 in.) | select | 3 mm (1/8 in.) | select |  |  |  |  | select | mm | in.
208 | 8.2.2 | Stud bolts : | input data |  | input data
209 | 8.2.2 | Stud nuts : | input data |  | input data
210 | 6.1.5, 7.6.6, 7.6.7, A.3.7.2 | Shroud : | select |  | select | [5 empty] | select | spray | fire | not required
211 | 7.6.8 | Drip tray : | select |  | select | [5 empty] | select | yes | no | by others
212 | 6.1.1, 9.4.1, 9.4.2 | Painting specification : | ISO 12944 (all parts) |  | ISO 12944 (all parts) | [5 empty] | select | IOGP S-715 (offshore and coastal environment) | ISO 12944 (all parts) | manufacturer's standard | other
213 | 9.4.1, 10.2.9 | Application of paint or other coatings prior to final pressure test : | not permitted |  | not permitted | [5 empty] | select | permitted | not permitted
214 | 7.7.14 | Insulation : | select |  | select | [5 empty] | select | yes | no | by others
215 | 8.1.6, 8.2.3, Table 3 | Maximum allowable CE for carbon steel in sour service : | Table 3 |  | Table 3
216 | 8.2.3 | Residual or micro-alloying elements : | no restrictions |  | no restrictions
217 | 11.7 | Surface preparation and protection for shipping : | no |  | no | [5 empty] | select | yes | no
218 |  | Loading
219 | 6.1.1, 7.7.17, 7.7.18, Table B.1 Continuation | Connection loads and moments : | select |  | select | [5 empty] | select | onshore (Table 1) | offshore (2.5 x Table 1) | actual loads
220 | 7.6.5 | Wind loading : | input data |  | input data
221 | 7.6.5 | Explosion blast pressure : | input data |  | input data
222 | 7.6.5 | Earthquake loading : | input data |  | input data
223 | 7.6.5 | Transport loading : | input data |  | input data
224 |  | Testing and inspection
225 | 10.2.8 | Specific drying procedure : | no |  | no | [5 empty] | select | yes | no
226 | 10.2.8 | Dried by : | blowing dry air |  | blowing dry air | [5 empty] | select | blowing dry air | blowing nitrogen | vacuum pump | manufacturer's standard | none | other
227 | 11.9, 11.11, 11.12 | Purge method : | select |  | select | [5 empty] | select | inert gas | desiccant bags | volatile corrosion inhibitor | none | other
228 | 9.1.1, 10.1.14 | NDE in addition to pressure design code : | select |  | select | [5 empty] | select | yes | no
229 | 10.1.6 | Ultrasonic lamination check of carbon steel plate in sour or wet hydrogen sulfide service : | select |  | select | [5 empty] | select | EN 10160 class S2E2 | ASTM A578/578M acceptance level A supplementary requirement S1 | not required | other
230 | 10.1.12, Table B.1 Continuation | PMI extent of alloy heat transfer plates : | 2% |  | 2% | [5 empty] | select | 2% | 10% | 100% | other
231 | 10.1.1, Table B.1 Continuation | NDE of heat transfer plates : | light box test |  | light box test | [5 empty] | select | light box testing | liquid-penetrant testing | none | other
232 | 10.1.1 | NDE extent for heat transfer plates : | 100% |  | 100% | [5 empty] | select | 10% | 100% | none | other
233 | 9.1.1, 10.1.3 | NDE of semi-welded plate joints : | vacuum leak test |  | vacuum leak test | [5 empty] | select | vacuum leak testing | helium leak testing | eddy current testing | gas leak testing | none | other
234 | 10.1.10, Table B.1 Continuation | Hardness testing of heat-affected zone of pressure retaining welds in carbon steel components : | select |  | select | [5 empty] | select | required | not required
235 | 7.7.19, 10.1.11, Table B.1 Continuation | Weld overlay chemical composition production test depth : | 1.5 mm (1/16 in.) |  | 1.5 mm (1/16 in.) | [5 empty] | select | 1.5 mm (1/16 in.) | other
236 | 10.1.15, Table B.1 Continuation | Acceptance criteria for ultrasonic examination of material : | select |  | select | [5 empty] | select | ASTM A578 including supplementary requirement S1 | EN 10160 class S2E3 | other
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the equipment.
Note on C7: Select the CAS level to be applied in IOGP S-749Q, Annex A. CAS D requires the fewest quality interventions and information requirements. Default value : D
Note on C8: Specify the country in which the project is located, in accordance with ISO 3166-1.
Note on C9: Specify the geographic location, within the country, which will determine the applicability of local regulatory requirements.
Note on C10: Select the location of the facility where the equipment will be permanently installed.
Note on C12: Select whether the exchanger is in utility service as per 3.26. If "yes" is selected, by also selecting CAS level D, fewer quality interventions and information deliverables will be applicable.
Note on C13: Specify the hot side fluid name and the detailed fluid composition for all applicable operating conditions. If required, details can be provided in the "Additional notes" column. Typical fluid names can be found in Table A.1.
Note on C14: Specify the cold side fluid name and the detailed fluid composition for all applicable operating conditions. If required, details can be provided in the "Additional notes" column. Typical fluid names can be found in Table A.1.
Note on C15: Specify the total fluid flow entering on the hot side.
Note on C16: Specify the total fluid flow entering on the cold side.
Note on C17: Specify the maximum design temperature for the hot side.
Note on C18: Specify the maximum design temperature for the cold side.
Note on C19: Specify the minimum design metal temperature for the hot side. Also, consider the effect of critical exposure temperature (CET) which is typically the lower of either ambient temperature or minimum process fluid temperature.
Note on C20: Specify the minimum design metal temperature for the cold side. Also, consider the effect of critical exposure temperature (CET) which is typically the lowest of either ambient temperature or minimum process fluid temperature.
Note on C21: Specify the design pressure of the hot side.
Note on C22: Specify the design pressure of the cold side.
Note on C23: Specify the allowable pressure drop for the hot side in fouled/dirty condition. A low value can lead to a larger sized plate-and-frame heat exchanger with a greater sensitivity to fouling.
Note on C24: Confirm the calculated total pressure drop of the hot side in fouled/dirty condition.
Note on C25: Specify the allowable pressure drop for the cold side in fouled/dirty condition. A low value can lead to a larger sized plate-and-frame heat exchanger with a greater sensitivity to fouling.
Note on C26: Confirm the calculated total pressure drop of the cold side in fouled/dirty condition.
Note on C27: Confirm the calculated port pressure drop for the hot side inlet in dirty/fouled condition.
Note on C28: Confirm the calculated port pressure drop for the hot side outlet in dirty/fouled condition.
Note on C29: Confirm the calculated port pressure drop for the cold side inlet in dirty/fouled condition.
Note on C30: Confirm the calculated port pressure drop for the cold side outlet in dirty/fouled condition.
Note on C31: Confirm the calculated port velocity for the hot side inlet in fouled/dirty condition.
Note on C32: Confirm the calculated port velocity for the hot side outlet in fouled/dirty condition.
Note on C33: Confirm the calculated port velocity for the cold side inlet in fouled/dirty condition.
Note on C34: Confirm the calculated port velocity for the cold side outlet in fouled/dirty condition.
Note on C35: Confirm the minimum wall temperature for the hot side.
Note on C36: Confirm the maximum wall temperature for the hot side.
Note on C37: Confirm the minimum wall temperature for the cold side.
Note on C38: Confirm the maximum wall temperature for the cold side.
Note on C39: Specify the fouling (overdesign) margin for the applicable fluid name from Table A.1. Vendor to confirm the calculated hot side fouling margin based on the selected plate-and-frame heat exchanger model. See Equation 1 for the fouling margin calculation.
Note on C40: Specify the fouling (overdesign) margin for the applicable fluid name from Table A.1. Vendor to confirm the calculated cold side fouling margin based on the selected plate-and-frame heat exchanger model. See Equation 1 for the fouling margin calculation.
Note on C41: Specify the pressure drop multiplier for fouled/dirty condition. Use the pressure drop multiplier over the calculated pressure drop in clean condition to report pressure drop in fouled condition for each specified design and rating case. See Table A.1.
Note on C42: Specify the pressure drop multiplier for fouled/dirty condition. Use the pressure drop multiplier over the calculated pressure drop in clean condition to report pressure drop in fouled condition for each specified design and rating case. See Table A.1.
Note on C44: Specify the liquid flow at the hot side inlet.
Note on C45: Specify the liquid flow at the hot side outlet.
Note on C46: Specify the liquid flow at the cold side inlet.
Note on C47: Specify the liquid flow at the cold side outlet.
Note on C48: Specify the vapor flow at the hot side inlet.
Note on C49: Specify the vapor flow at the hot side outlet.
Note on C50: Specify the vapor flow at the cold side inlet.
Note on C51: Specify the vapor flow at the cold side outlet.
Note on C52: Specify the non-condensable flow at the hot side inlet.
Note on C53: Specify the non-condensable flow at the hot side outlet.
Note on C54: Specify the non-condensable flow at the cold side inlet.
Note on C55: Specify the non-condensable flow at the cold side outlet.
Note on C56: Specify the operating temperature at the hot side inlet.
Note on C57: Specify the operating temperature at the hot side outlet.
Note on C58: Specify the operating temperature at the cold side inlet.
Note on C59: Specify the operating temperature at the cold side outlet.
Note on C60: Specify the operating pressure at the hot side inlet.
Note on C61: Specify the operating pressure at the hot side outlet.
Note on C62: Specify the operating pressure at the cold side inlet.
Note on C63: Specify the operating pressure at the cold side outlet.
Note on C65: Specify the density of liquid at the hot side inlet.
Note on C66: Specify the density of liquid at the hot side outlet.
Note on C67: Specify the density of liquid at the cold side inlet.
Note on C68: Specify the density of liquid at the cold side outlet.
Note on C69: Specify the specific heat capacity of liquid at the hot side inlet.
Note on C70: Specify the specific heat capacity of liquid at the hot side outlet
Note on C71: Specify the specific heat capacity of liquid at the cold side inlet.
Note on C72: Specify the specific heat capacity of liquid at the cold side outlet.
Note on C73: Specify the dynamic viscosity of liquid at the hot side inlet.
Note on C74: Specify the dynamic viscosity of liquid at the hot side outlet.
Note on C75: Specify the dynamic viscosity of liquid at the cold side inlet.
Note on C76: Specify the dynamic viscosity of liquid at the cold side outlet.
Note on C77: Specify the thermal conductivity of liquid at the hot side inlet.
Note on C78: Specify the thermal conductivity of liquid at the hot side outlet.
Note on C79: Specify the thermal conductivity of liquid at the cold side inlet.
Note on C80: Specify the thermal conductivity of liquid at the cold side outlet.
Note on C81: Specify the surface tension of liquid at the hot side inlet.
Note on C82: Specify the surface tension of liquid at the hot side outlet.
Note on C83: Specify the surface tension of liquid at the cold side inlet.
Note on C84: Specify the surface tension of liquid at the cold side outlet.
Note on C86: Specify the density of vapor at the hot side inlet.
Note on C87: Specify the density of vapor at the hot side outlet.
Note on C88: Specify the density of vapor at the cold side inlet.
Note on C89: Specify the density of vapor at the cold side outlet.
Note on C90: Specify the specific heat capacity of vapor at the hot side inlet.
Note on C91: Specify the specific heat capacity of vapor at the hot side outlet.
Note on C92: Specify the specific heat capacity of vapor at the cold side inlet.
Note on C93: Specify the specific heat capacity of vapor at the cold side outlet.
Note on C94: Specify the dynamic viscosity of vapor at the hot side inlet.
Note on C95: Specify the dynamic viscosity of vapor at the hot side outlet.
Note on C96: Specify the dynamic viscosity of vapor at the cold side inlet.
Note on C97: Specify the dynamic viscosity of vapor at the cold side outlet.
Note on C98: Specify the thermal conductivity of vapor at the hot side inlet.
Note on C99: Specify the thermal conductivity of vapor at the hot side outlet.
Note on C100: Specify the thermal conductivity of vapor at the cold side inlet.
Note on C101: Specify the thermal conductivity of vapor at the cold side outlet.
Note on C103: Specify the relative molecular mass at the hot side inlet.
Note on C104: Specify the relative molecular mass at the hot side outlet.
Note on C105: Specify the relative molecular mass at the cold side inlet.
Note on C106: Specify the relative molecular mass at the cold side outlet.
Note on C107: Specify the relative molecular mass of non-condensables for the hot side.
Note on C108: Specify the relative molecular mass of non-condensables for the cold side.
Note on C109: Specify the dew point / bubble point for the hot side.
Note on C110: Specify the dew point / bubble point for the cold side.
Note on C111: Specify the maximum solid particle size for the hot side, if known. Default value : 1 mm (0.04 in.)
Note on C112: Specify the maximum solid particle size for the cold side, if known. Default value : 1 mm (0.04 in.)
Note on C113: Specify the concentration of solids (% volume) for the hot side.
Note on C114: Specify the concentration of solids (% volume) for the cold side.
Note on C115: Specify the latent heat for the hot side when the fluid is two phase or phase change is expected.
Note on C116: Specify the latent heat for the cold side when the fluid is two phase or phase change is expected.
Note on C117: Specify the critical pressure for the hot side when the fluid is two phase or phase change is expected.
Note on C118: Specify the critical temperature for the hot side when the fluid is two phase or phase change is expected.
Note on C119: Specify the critical pressure for the cold side when the fluid is two phase or phase change is expected.
Note on C120: Specify the critical temperature for the hot side when the fluid is two phase or phase change is expected.
Note on C122: Specify the required total heat exchanged. Vendor to confirm the total heat exchanged for the proposed plate-and-frame heat exchanger.
Note on C123: Confirm the calculated overall heat transfer coefficient (U) in clean condition for the proposed plate-and-frame heat exchanger model.
Note on C124: Confirm the log mean temperature difference (LMTD) of the proposed plate-and-frame heat exchanger.
Note on C125: Confirm the effective mean temperature difference (EMTD) of the proposed plate-and-frame heat exchanger.
Note on C126: Confirm the heat transfer area per exchanger.
Note on C127: Confirm the stream heat transfer coefficient for the hot side.
Note on C128: Confirm the stream heat transfer coefficient for the cold side.
Note on C129: Confirm the calculated overall heat transfer coefficient (U) for the in-service condition for the proposed plate-and-frame heat exchanger model.
Note on C131: Confirm the number of exchangers (plate packs) in parallel.
Note on C132: Confirm the number of exchangers (plate packs) in series.
Note on C133: Confirm the total heat transfer area of the proposed plate-and-frame heat exchanger.
Note on C134: Confirm the heat transfer area per plate.
Note on C135: Confirm the number of heat transfer plates per exchanger (excluding end plates).
Note on C136: Confirm the maximum number of heat transfer plates per exchanger (excluding end plates), considering the future expansion requirements specified in 7.1.1.
Note on C137: Confirm the number of hot fluid passes per pack/exchanger when it is specified that data for thermal verification is required.
Note on C138: Confirm the number of cold fluid passes per pack/exchanger when it is specified that data for thermal verification is required.
Note on C139: Confirm the number of channels in each hot fluid pass when it is specified that data for thermal verification is required.
Note on C140: Confirm the number of channels in each cold fluid pass when it is specified that data for thermal verification is required.
Note on C141: Confirm the direction of flow across the plate when it is specified that data for thermal verification is required.
Note on C142: Confirm the relative directions of fluids.
Note on C143: Confirm the nominal plate gap.
Note on C144: Confirm the nominal plate thickness.
Note on C145: Confirm the plate chevron angle(s).
Note on C147: Specify the pressure design code.
Note on C148: Select the material certificate type for pressure-retaining components in accordance with ISO 10474 or EN 10204. Default value : Type 3.1 - Material inspection certificate
Note on C149: Select whether code stamping is required.
Note on C150: If the plate-and-frame heat exchanger is operating in sour service or wet hydrogen sulfide service, select the applicable standard. Default value : not applicable
Note on C151: Select the sides that will be exposed to sour or wet hydrogen sulfide service.
Note on C152: Select if sour service requirements are to be applied where carbon steel is lined. If additional NDE (X-ray and ultrasonic examination) on liner welds is specified, "no" can be selected.
Note on C153: Select whether the plate heat exchanger will be in cyclic service. If yes, provide details of all operating conditions over the full operating envelope and for the life of the facility including start-up, shutdown, upset, cleaning and back flush.
Note on C154: Select whether the data required for thermal verification is to be supplied by the vendor.
Note on C155: Select the welding code for structural parts. If "other" is selected, specify in the "Additional notes" column. Default value : AWS D1.1
Note on C156: Select the flange design code from ASME B16.5, ASME B16.47 or other equivalent standard. If "other" is selected, specify in the "Additional notes" column. Default value : ASME B16.5
Note on C157: Specify the applicable purchaser's specifications to be followed.
Note on C158: Specify company or plant-specific regulations or certifications applicable to the installation location. These are in addition to the local authority (legal) regulations determined by the project country and region. Default value : not applicable
Note on C159: Specify the local register for the plate-and-frame heat exchanger.
Note on C160: Confirm the test pressure for the hot side.
Note on C161: Confirm the test pressure for the cold side.
Note on C162: Confirm the velocity between the plates for the hot side.
Note on C163: Confirm the velocity between the plates for the cold side.
Note on C164: Specify the wall shear stress for the hot side in clean condition. Vendor to confirm the calculated hot side wall shear stress for the selected plate-and-frame heat exchanger. If not specified, refer to Table A.1 minimum wall shear stress values.
Note on C165: Specify the wall shear stress for the cold side in clean condition. Vendor to confirm the calculated cold side wall shear stress for the selected plate-and-frame heat exchanger. If not specified, refer to Table A.1 minimum wall shear stress values
Note on C166: Confirm the volume per exchanger for the hot side.
Note on C167: Confirm the volume per exchanger for the cold side.
Note on C168: Confirm the length of the plate-and-frame heat exchanger assembly.
Note on C169: Confirm the width of the plate-and-frame heat exchanger assembly.
Note on C170: Confirm the height of the plate-and-frame heat exchanger assembly.
Note on C171: Confirm the mass of the plate-and-frame heat exchanger when empty.
Note on C172: Confirm the mass of the plate-and-frame heat exchanger when filled with water.
Note on C173: Confirm whether a detailed fatigue analysis is required based on the screening criteria of the selected pressure design code (see 4.11). If a detailed fatigue analysis is required as per A.1.2.3, use of plate-and-frame heat exchangers is not recommended.
Note on C175: Specify the nozzle size for the hot side inlet. Vendor to confirm the nozzle size for the hot side inlet.
Note on C176: Specify the nozzle flange rating and facing for the hot side inlet. Vendor to confirm the nozzle flange rating and facing for the hot side inlet
Note on C177: Select the nozzle flange type for the hot side inlet. Vendor to confirm the nozzle flange type for the hot side inlet. Default value : weld neck
Note on C178: Select the nozzle connection design for the hot side inlet. Flanged connections are recommended due to a lower reported risk of leaks. In utility services for PN 20 (ASME Rating 150), the use of studded connections is considered lower risk.
Note on C179: Specify the nozzle size for the hot side outlet. Vendor to confirm the nozzle size for the hot side outlet.
Note on C180: Specify the nozzle flange rating and facing for the hot side outlet. Vendor to confirm the nozzle flange rating and facing for the hot side outlet.
Note on C181: Select the nozzle flange type for the hot side outlet. Vendor to confirm the nozzle flange type for the hot side outlet. Default value : weld neck
Note on C182: Select the nozzle connection design for the hot side outlet. Flanged connections are recommended due to a lower reported risk of leaks. In utility services for PN 20 (ASME Rating 150), the use of studded connections is considered lower risk.
Note on C183: Specify the nozzle size for the cold side inlet. Vendor to confirm the nozzle size for the cold side inlet.
Note on C184: Specify the nozzle flange rating and facing for the cold side inlet. Vendor to confirm the nozzle flange rating and facing for the cold side inlet
Note on C185: Specify the nozzle flange type for the cold side inlet. Vendor to confirm the nozzle flange type for the cold side inlet. Default value : weld neck
Note on C186: Select the nozzle connection design for the cold side inlet. Flanged connections are recommended due to a lower reported risk of leaks. In utility services for PN 20 (ASME Rating 150), the use of studded connections is considered lower risk.
Note on C187: Specify the nozzle size for the cold side outlet. Vendor to confirm the nozzle size for the cold side outlet.
Note on C188: Specify the nozzle flange rating and facing for the cold side outlet. Vendor to confirm the nozzle flange rating and facing for the cold side outlet.
Note on C189: Select the nozzle flange type for the cold side outlet. Vendor to confirm the nozzle flange type for the cold side outlet. Default value : weld neck
Note on C190: Select the nozzle connection design for the cold side outlet. Flanged connections are recommended due to a lower reported risk of leaks. In utility services for PN 20 (ASME Rating 150), the use of studded connections is considered lower risk.
Note on C191: Select whether port holes on movable covers for maintenance (e.g., cleaning, inspection) are required. If "required" is selected, specify details (e.g., quantity, type) in the "Additional notes" column. Default value : not required
Note on C193: Select the type of plate-and-frame heat exchanger. Fully gasketed plate-and-frame heat exchangers are not recommended for fluids such as wet hydrogen sulfide, hydrogen, hydrogen fluoride and kerosene (low boiling fluid).
Note on C194: Specify the heat transfer plate material.
Note on C195: Select the gasket attachment method.
Note on C196: Specify the gasket material for the hot side.
Note on C197: Specify the gasket material for the cold side.
Note on C198: Specify the material for the fixed cover.
Note on C199: Specify the material for the movable cover.
Note on C200: Specify the material for the tie bolts.
Note on C201: Specify the material for the tie bolt nuts.
Note on C202: Specify the material for the nozzle pipes for the hot side. Lined connections are not recommended in cyclic service.
Note on C203: Specify the material for the nozzle pipes for the cold side. Lined connections are not recommended in cyclic service.
Note on C204: Specify the material for the nozzle flanges for the hot side. Lined connections are not recommended in cyclic service.
Note on C205: Specify the material for the nozzle flanges for the cold side. Lined connections are not recommended in cyclic service.
Note on C206: Specify the corrosion allowance on carbon steel wetted surfaces on hot side connections. Default value : 3 mm (1/8 in.)
Note on C207: Specify the corrosion allowance on carbon steel wetted surface cold side connections. Default value : 3 mm (1/8 in.)
Note on C208: Specify the material for the stud bolts.
Note on C209: Specify the material for the stud bolt nuts.
Note on C210: Select the type of protection shroud required. If a fire protection shroud is required, specify the fire protection level (e.g. as per A.3.7) or the company specification detailing the shroud requirements in the "Additional notes" column.
Note on C211: Select whether a drip tray is to be supplied.
Note on C212: Select the coating specification for carbon steel and low-alloy steel pressure-containing and structural parts. If "other" is selected, specify the applicable specification in the "Additional notes" column. Default value : ISO 12944 (all parts)
Note on C213: Select whether it is permitted to apply paint or other coatings over welds and any installed liners prior to the final pressure test. If permitted, the extent of painting and associated dry film thickness can be specified in the "additional notes" column. Default value : not permitted
Note on C214: Select whether insulation is required.
Note on C215: Specify the maximum allowable CE for carbon steel pressure-containing parts in sour service. Default value : Table 3
Note on C216: Specify any restrictions on residual elements or micro-alloying elements which may apply for carbon steel in sour or wet hydrogen sulfide service. Default value : no restrictions
Note on C217: Select whether surface preparation and protection measures are required for shipping and storage which differ or are in addition to those specified in Section 11. If "yes" is selected, specify the applicable specification in the "Additional notes" column. Default value: no
Note on C219: Select connection loads and moments. Specify the load values or a multiplication factor with reference to Table 1 in the "Additional notes" column."
Note on C220: Specify any wind loading to be considered in the design.
Note on C221: Specify any explosion blast pressure to be considered in the design.
Note on C222: Specify any earthquake/seismic loading to be considered in the design.
Note on C223: Specify any transport loading to be considered in the design.
Note on C225: Select whether a purchaser-specific drying procedure is to be followed. If "yes" is selected, specify the document number in the "Additional notes" column. Default value : no
Note on C226: Select the drying method. If "other" is selected, specify in the "Additional notes" column. Default value : blowing dry air
Note on C227: Specify the purging method. If "other" is selected, specify in the "Additional notes" column.
Note on C228: Select if any nondestructive examination (NDE) is required in addition to that specified by the selected pressure design code. If "yes", specify in the "Additional notes" column. e.g. helium leak test of the assembly as applicable can be specified.
Note on C229: Select whether carbon steel plate in sour or wet hydrogen sulfide service shall be subjected to an ultrasonic lamination check, or if not required. If "other" is selected, specify in the "Additional notes" column.
Note on C230: Select the extent of PMI required to be performed on alloy heat transfer plates. If "other" is selected, specify in the "Additional notes" column. Default value : 2%
Note on C231: Select the type of nondestructive examination (NDE) to be performed on the heat transfer plates after forming. If "other" is selected, specify in the "Additional notes" column. Default value : light box test
Note on C232: Select the extent of nondestructive examination (NDE) to be performed on the heat transfer plates after forming. If "other" is selected, specify in the "Additional notes" column. Default value : 100 %
Note on C233: For semi-welded heat transfer plate pairs, select the type of nondestructive examination (NDE) to be performed on the welds. If "other" is selected, specify the type of testing in the "Additional notes" column. Default value : vacuum leak test
Note on C234: Select whether hardness testing of the heat-affected zone of pressure retaining welds in carbon steel components is required, when not required by the selected pressure design code.
Note on C235: Select the depth from the machined/finished weld overlay surface at which chemical analysis is to be carried out. If "other" is selected, specify in the "Additional notes" column. Default value : 1.5 mm (1/16 in.)
Note on C236: Select the code to which the ultrasonic lamination check is to be performed. If "other" is selected, specify the applicable code or specification in the "Additional notes" column.

## Physical properties
Row | IOGP S-749D (1.01) Procurement Data Sheet for Plate-and-frame Heat Exchangers (API) | [9 empty] | Issue
2 | Description | Purchaser requirement UOM | Physical properties (including water if present)
3 | Case
4 | Temperature | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | °C | °F
5 | Pressure | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kPa (abs) | psia
6 | Heat released | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kW | BTU/h
7 | Liquid phase
8 | Mass fraction vapor |  | input data | input data | input data | input data | input data | input data | input data | input data |  | input data
9 | Mass fraction H2O in liquid |  | input data | input data | input data | input data | input data | input data | input data | input data |  | input data
10 | Density | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kg/m3 | lb/ft3
11 | Specific heat capacity | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kJ/kg·K | BTU/lb·°R
12 | Dynamic viscosity | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | mPa·s | cP
13 | Thermal conductivity | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | W/m·K | BTU/h·ft·°R
14 | Surface tension | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | N/m | dyn/cm
15 | Vapor pressure | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kPa (abs) | psia
16 | Vapor phase
17 | Density | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kg/m3 | lb/ft3
18 | Specific heat | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kJ/kg·K | BTU/lb·°R
19 | Dynamic viscosity | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | mPa·s | cP
20 | Thermal conductivity | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | W/m·K | BTU/h·ft·°R
21 | Vapor pressure | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kPa (abs) | psia
22 | Relative molecular mass | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kg/kmol | lb/lb·mol
23 | Common fluid properties
24 | Latent heat | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kJ/kg | BTU/lb
25 | Critical pressure | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | kPa (abs) | psia
26 | Critical temperature | select | input data | input data | input data | input data | input data | input data | input data | input data |  | select | °C | °F
Note on B4: Specify the reference temperature.
Note on B5: Specify the pressure for the reference case.
Note on B6: Specify the heat released for the reference case.

## Cyclic service information
Row | IOGP S-749D (1.01) Procurement Data Sheet for Plate-and-frame Heat Exchangers (API) | [6 empty] | Issue
2 | Cyclic service information Description of cyclic service operation
3 | Condition | Time (h/min) | Duration (h/min) | Composition |  | Flow rate | Unit
4 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
5 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
6 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
7 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
8 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
9 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
10 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
11 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
12 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
13 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
14 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
15 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
16 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
17 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
18 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
19 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
20 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
21 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
22 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
23 | input data | input data | input data | input data |  | input data | select |  | select | kg/h | lb/h
24 | Condition | Time (h/min) | Duration (h/min) | Temperature | Unit | Pressure | Unit
25 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
26 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
27 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
28 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
29 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
30 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
31 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
32 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
33 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
34 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
35 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
36 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
37 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
38 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
39 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
40 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
41 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
42 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
43 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
44 | input data | input data | input data | input data | select | input data | select |  | select | °C | °F | select | kPa(g) | psig
Note on B3: Specify all operating conditions affecting design of the plate heat exchanger over the full operating envelope, and for the life of the facility, including startup, shutdown, steady-state, transient, turn-down upset conditions, cleaning and back flushing.
Note on C3: Specify the time reference.
Note on D3: Specify the duration with respect to the time reference.
Note on F3: Specify the composition with respect to the time reference.
Note on H3: Specify the flowrate with respect to the time reference.
Note on B24: Specify all operating conditions affecting design of the plate heat exchanger over the full operating envelope, and for the life of the facility, including startup, shutdown, steady-state, transient, turn-down upset conditions, cleaning and back flushing.
Note on C24: Specify the time reference.
Note on D24: Specify the duration with respect to the time reference.
Note on F24: Specify the temperature with respect to the time reference.
Note on H24: Specify the pressure with respect to the time reference.

## Supplement
Row |  | IOGP S-749D (1.01) Procurement Data Sheet for Plate-and-frame Heat Exchangers (API) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-749D (1.01) Procurement Data Sheet for
Plate-and-frame Heat Exchangers (API)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-749 Supplementary Specification to API Standard 667 for Plate-and-frame Heat Exchangers.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
Copy for SC Approval