## Addendum 1
Date of issue:
April 2026
Affected publication:
IOGP S-745D, Procurement Data Sheet for High-voltage Synchronous Machines (IEC), First Edition, April 2024
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.01 published in April 2024.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Worksheet | Row | Column | Update
| Single-speed Motor | 96 | Purchaser requirement / Supplier offered value - options | New option "manufacturer's standard"
| Single-speed Motor | 100 | Description | Description amended Embedded guidance note amended
| Convertor Duty Motor | 45 | All | New data sheet item "Impulse voltage insulation class"
| Convertor Duty Motor | 91 | Description | Description amended Embedded guidance note amended
| Generators | 59 | All | New data sheet item "Minimum allowed direct-axis transient reactance (X'd)(Saturated)"
| Generators | 60 | All | New data sheet item "Maximum allowed direct-axis transient reactance (X'd)(Saturated)"
| Generators | 61 | Description | Description amended Embedded guidance note amended
| Generators | 62 | All | New data sheet item "Direct-axis transient reactance (X'd)(Unsaturated)"
| Generators | 68 | Description | Description amended Embedded guidance note amended
|  |  | Purchaser requirement / Supplier offered value - options | New option "other"
| Generators | 91 | Purchaser requirement / Supplier offered value - options | New option "manufacturer's standard"
| Generators | 95 | Description | Description amended Embedded guidance note amended
| Generators | 106 | All | New data sheet item "Control panel ingress protection"
| Generators | 134 | Description | Section heading amended
| Generators | 135 | All | New data sheet item "Rotor field earth fault circuit detection"
| Generators | 136 | All | New data sheet item "Monitoring of insulation resistance"
| Generators | 144 | All | New data sheet item "Cooling water inlet supply maximum design pressure"
| Testing | 6 * | All | Data sheet item "Performance test - No-load characteristic (saturation curve) at rated frequency" * deleted
| Testing | 6 | Description | Description amended
| Testing | 10 | Description | Description amended
List of updates (continued)
| Worksheet | Row | Column | Update
| Testing | 12 * | All | Data sheet item "Performance test - Determination of efficiency at 100 %, 75 % and 50 % load at rated power factor (converter duty synchronous motor)" * deleted
| Testing | 21 | All | New data sheet item "Special test - Stator External Discharge test"
| Testing | 32 | All | New data sheet item "Special test - Generator waveform analysis test"
| Testing | 33 | All | New data sheet item "Special test - Rotor impedance test at rated frequency for the machine (stator frequency)"
| Testing | 34 | All | New data sheet item "Special test - Test for determination of unsaturated Negative Sequence Reactance (X2)"
| Testing | 35 | All | New data sheet item "Special test - Test for determination of unsaturated Zero Sequence Reactance (X0)"
| Testing | 36 | All | New data sheet item "Special test - Test for determination of Direct-Axis Open Circuit Time Constant (T'do)"
| Testing | 37 | All | New data sheet item "Special test - End Winding Impact Test"
| Testing | 38 | All | New data sheet item "Special test - Overspeed test"
| Various | Various | Ref. Clause | List of references updated
| Various | Various | Row | Numbering amended as per new and deleted rows
* Data from Edition 1.0.

## Front & Preliminaries
|  |  |  | SPECIFICATION | April 2026
|  |  |  | IOGP S-745D | Version 1.01
ADDENDUM 1 TO FIRST EDITION (APRIL 2024)
Procurement Data Sheet for High-voltage Synchronous Machines (IEC)
Revision history
VERSION | DATE | PURPOSE
1.01 | April 2026 | Addendum 1
1 | April 2024 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-745D (1.01) Procurement Data Sheet for High-voltage Synchronous Machines (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-745D (1.01) Procurement Data Sheet for High-voltage Synchronous Machines (IEC)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of high-voltage synchronous machines in accordance with IOGP S-745 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-745), information requirements specification (IOGP S-745L) and quality requirements specification (IOGP S-745Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Single-speed Motor
Row | IOGP S-745D (1.01) Procurement Data Sheet for High-voltage Synchronous Machines (IEC) Single-speed Motor | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Project country : | input data |  | input data
9 |  | Project region : | input data |  | input data
10 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine - coastal | subsea | buried | onshore
11 |  | Order status : | select |  | select | [5 empty] | select | for enquiry | for purchase
12 |  | Manufacturer : | input data |  | input data
13 |  | Model number : | input data |  | input data
14 |  | Number of poles : | select |  | select | [5 empty] | select | 2 pole | 4 pole | 6 pole | 8 pole | other
15 | 11.4.2.3.1 | Frame size/designation : | input data |  | input data
16 |  | Site conditions
17 | 6.1 | Location environment : | select |  | select | [5 empty] | select | indoor | onshore - coastal | onshore - desert | onshore - inland | offshore - fixed | offshore - floating | marine - ship | other
18 | 6.1 | Altitude : | 1 000 or below | m | 1 000 or below | m |  |  |  |  | select | 1 000 or below | other
19 | 9.1,6.1 | Maximum ambient air temperature : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50 | other
20 | 6.1 | Minimum ambient air temperature : | 0 | °C | 0 | °C |  |  |  |  | select | 0 | other
21 | 6.1 | Storage conditions : | select |  | select | [5 empty] | select | conditioned environment | non-conditioned environment
22 | 6.1 | Maximum rolling of vessel in dynamic conditions : | input data |  | input data
23 | 6.1 | Maximum pitching of vessel in dynamic conditions : | input data |  | input data
24 | 6.1 | Chemicals and corrosives : | input data |  | input data
25 | 6.1 | Unusual service conditions : | no |  | no | [5 empty] | select | yes | no
26 |  | Motors rated for use in hazardous area
27 | 11.4.16.1.1,11.4.16.1.2 | Hazardous area equipment certification : | select |  | select | [5 empty] | select | ATEX | IECEx | other | not applicable
28 | 11.4.16.1.1,11.4.16.1.2 | Temperature class : | T3 |  | T3 | [5 empty] | select | T3 | T4 | T5 | T6 | T1 | T2 | not applicable
29 | 11.4.16.1.1,11.4.16.1.2 | Gas/dust group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | not applicable
30 | 11.4.16.1.1,11.4.16.1.2,11.4.16.3 | Equipment protection level : | select |  | select | [5 empty] | select | EPL Gb | EPL Gc | EPL Db | EPL Dc | not applicable
31 | 11.4.16.1.1,11.4.16.1.2,11.4.16.3 | Type of protection : | select |  | select | [5 empty] | select | Ex db | Ex db eb | Ex pxb | Ex pxb eb | Ex pzc | not applicable
32 |  | Driven equipment interface
33 | 4.1 | Duty type : | S1 |  | S1 | [5 empty] | select | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8
34 | 5.5.3 | Duty point shaft power : | input data | kW | input data | kW
35 | 10.4.2 | Direction of rotation : | select |  | select | [5 empty] | select | clockwise | counter-clockwise
36 |  | Driven equipment type : | select |  | select | [5 empty] | select | centrifugal pump | centrifugal fan | centrifugal compressor | reciprocating pump | reciprocating compressor | positive displacement pump | other
37 |  | Load drive : | select |  | select | [5 empty] | select | direct coupled | gearbox | other
38 | 11.3.3.2 | Maximum pulsating current : | 40 | % of FLC | 40 | % of FLC |  |  |  |  | select | 40 | other
39 | 11.3.3.2 | Moment of inertia of load (Jext) : | input data | kg·m² | input data | kg·m²
40 |  | Coupling hub type : | select |  | select | [5 empty] | select | integral flange | cylindrical | taper | other
41 |  | Coupling hub fit : | select |  | select | [5 empty] | select | keyed | keyless | hydraulic | other
42 |  | Electrical operating conditions
43 | 7.4 | Motor rated voltage : | input data | kV | input data | kV
44 | 7.4 | Maximum voltage variation : | select | % | select | % |  |  |  |  | select | 10 | 5 | other
45 | 7.4 | Minimum voltage variation : | select | % | select | % |  |  |  |  | select | -10 | -5 | other
46 | 7.4 | Motor rated frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
47 | 7.4 | Maximum frequency variation : | select | % | select | % |  |  |  |  | select | 2 | 4 | other
48 | 7.4 | Minimum frequency variation : | select | % | select | % |  |  |  |  | select | -2 | -6 | other
49 |  | 3-phase fault current at motor terminals for 0,5 s : | input data | kA | input data | kA
50 |  | Thermal performance
51 | 8.1 | Insulation thermal class : | F |  | F | [5 empty] | select | F | H
52 | 8.1 | Temperature rise class : | B |  | B | [5 empty] | select | B | F
53 | 8.6.1 | Determination of winding temperature rise : | resistance method |  | resistance method | [5 empty] | select | resistance method | embedded temperature detector method | manufacturer's standard
54 |  | Starting performance
55 |  | Starting method : | select |  | select | [5 empty] | select | direct-on-line | captive transformer | reactor | auto-transformer starter | variable speed drive | soft-starter | other
56 |  | Starting load : | select |  | select | [5 empty] | select | unloaded | loaded
57 | 11.3.1.1 | Locked rotor current required : | input data |  | input data
58 | 11.3.1.1 | Locked rotor current tolerance required : | 20 | % | 20 | % |  |  |  |  | select | 20 | 10 | 0
59 | 11.3.1.1 | Locked rotor current at rated voltage : | input data | pu of FLC | input data | pu of FLC
60 | 11.3.1.1 | Locked rotor current at 80 % rated voltage : | input data | pu of FLC | input data | pu of FLC
61 |  | Pull-up torque : | input data | pu of full load torque | input data | pu of full load torque
62 |  | Locked rotor torque at rated voltage : | input data | N·m | input data | N·m
63 |  | Locked rotor torque at 80 % rated voltage : | input data | N·m | input data | N·m
64 |  | Locked rotor power factor at rated voltage : | input data | pu | input data | pu
65 |  | Moment of inertia of the rotor (Jm) : | input data | kg·m² | input data | kg·m²
66 |  | Operating performance
67 | 5.5.3 | Rated output : | input data | kW | input data | kW
68 |  | Rated current : | input data | A | input data | A
69 |  | Rated synchronous speed : | input data | min⁻¹ | input data | min⁻¹
70 |  | Rated torque : | input data | N·m | input data | N·m
71 |  | Pull out torque : | input data | pu | input data | pu
72 | 5.9,Table 24 | Efficiency at rated output : | input data | % | input data | %
73 | 5.9,Table 24 | Efficiency at 75 % of rated output : | input data | % | input data | %
74 | 5.9,Table 24 | Efficiency at 50 % of rated output : | input data | % | input data | %
75 |  | Power factor at rated output : | input data | pu | input data | pu
76 |  | Power factor at 75 % of rated output : | input data | pu | input data | pu
77 |  | Power factor at 50 % of rated output : | input data | pu | input data | pu
78 |  | Surface protection
79 | 11.4.2.3.4,11.4.2.4.1,11.4.2.4.2,Table 27 | Surface protection corrosivity category : | C3 |  | C3 | [5 empty] | select | C3 | C4 | C5 | CX
80 | 11.4.2.3.4,11.4.2.4.3,Table 27 | Surface protection durability category : | medium (M) 7 to 15 years |  | medium (M) 7 to 15 years | [5 empty] | select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
81 |  | Paint colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
82 |  | Motor construction
83 | 6.8,Table 25 | Motor enclosure ingress protection : | IP44 |  | IP44 | [5 empty] | select | IP56 | IP55 | IP44 | IPW24 | IP23 | other
84 | 11.4.3.1.1,Table 28 | Cooling method : | select |  | select | [5 empty] | select | IC4A1A1 | IC5A1A1 | IC6A1A1 | IC7A1W7 | IC8A1W7 | other
85 | 11.4.3.2.3 | Heat exchanger tube construction : | select |  | select | [5 empty] | select | single tubing | double tubing | not applicable
86 |  | Motor weight : | input data | kg | input data | kg
87 |  | Direct axis subtransient reactance (X''d)(Saturated/Unsaturated) : | input data | pu | input data | pu
88 |  | Negative sequence reactance (X2) : | input data | pu | input data | pu
89 |  | Armature short-circuit time constant (Ta) : | input data | s | input data | s
90 |  | Bearings (general)
91 |  | Bearing type : | select |  | select | [5 empty] | select | sleeve bearings | tilted pad bearings
92 | 9.1 | Lubrication specification : | input data |  | input data
93 |  | Lubrication system : | select |  | select | [5 empty] | select | manufacturer's standard | self-lubrication | flooded lubrication provided by others | flooded independent lubrication | flooded common lubrication system with driven equipment
94 | 11.4.9.2.13 | Low-speed barring : | not required |  | not required | [5 empty] | select | required | not required
95 |  | Vibration
96 | 11.4.5.3 | Applicable rotor balancing grade : | G2,5 |  | G2,5 | [5 empty] | select | G2,5 | G1,0 | G0,665 | manufacturer's standard
97 | 9.1,11.4.5.4,11.4.5.6 | Bearing housing vibration limits : | select |  | select | [5 empty] | select | grade A - IEC 60034-14:2018 Table 1 | grade B - IEC 60034-14:2018 Table 1 | other | not applicable
98 | 9.1,11.3.4.1,11.4.5.4,11.4.5.6 | Maximum shaft vibration limit : | select |  | select | [5 empty] | select | grade A - IEC 60034-14:2018 Table 2 | grade B - IEC 60034-14:2018 Table 2 | other | not applicable
99 | 9.1,11.3.4.1,11.4.5.4,11.4.5.6 | Maximum shaft runout limit : | select |  | select | [5 empty] | select | grade A - IEC 60034-14:2018 Table 2 | grade B - IEC 60034-14:2018 Table 2 | other | not applicable
100 | 11.3.4.1 | Maximum allowable vibration limit of shaft vibration (Sp-p) at rated output : | input data | µm | input data | µm
101 | 11.3.4.1,11.4.10 | Lateral vibration analysis : | not required |  | not required | [5 empty] | select | required for standalone motor | required for standalone motor and data/model for driven equipment supplier | not required
102 | 11.4.11 | Torsional vibration analysis : | not required |  | not required | [5 empty] | select | required data/model input for driven equipment supplier | not required
103 | 11.4.9.2.7 | Proximity probes for vibration measurement : | select |  | select | [5 empty] | select | two non-contacting proximity probes per sleeve bearing | two non-contacting proximity probes per sleeve bearing and one phase reference transducer | not required
104 |  | Noise
105 | 11.3.5.2,11.3.5.3 | Sound pressure level at no load : | input data | dB(A) | input data | dB(A)
106 |  | Excitation data
107 |  | Excitation system scope : | by manufacturer |  | by manufacturer | [5 empty] | select | by manufacturer | by purchaser
108 |  | Exciter power : | select |  | select | [5 empty] | select | external power supply | permanent magnet generator (PMG)
109 |  | Control and protection
110 |  | Control panel location : | indoor |  | indoor | [5 empty] | select | indoor | outdoor
111 |  | Cable entry location : | select |  | select | [5 empty] | select | bottom | top | bottom and top
112 |  | Cable entry type : | select |  | select | [5 empty] | select | removable-undrilled plate | multi-cable transit (MCT)
113 |  | Control panel anti-condensation heater : | select |  | select | [5 empty] | select | required | not required
114 | 11.4.13.3.1,11.4.17.4.3 | Communication protocol for interface with electrical control system : | select |  | select | [5 empty] | select | Modbus TCP/IP | Modbus RTU | Profinet | Profibus | Ethernet | other | not applicable
115 |  | Anti-condensation heaters
116 | 11.4.14.1 | Anti-condensation heater : | windings |  | windings | [5 empty] | select | windings | windings and line conductor terminal box | not required
117 | 11.4.14.1 | Anti-condensation heater supply voltage (AC) : | select | V | select | V |  |  |  |  | select | 100-120 single phase | 200-240 single phase | 380-440 three phase
118 |  | Warning label language : | select |  | select | [5 empty] | select | English | other
119 |  | Terminal boxes (general)
120 | Table 25 | Degree of ingress protection of all terminal boxes : | IP55 |  | IP55 | [5 empty] | select | IP55 | IP56 | other
121 |  | Line conductor terminal box
122 |  | Line conductor terminal box type : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | air insulated | phase insulated with heat shrink insulation | phase insulated with separable connectors | phase separated | phase segregated | other
123 |  | Line conductor terminal box location viewed from drive end : | select |  | select | [5 empty] | select | right | left | top
124 |  | Line conductor terminal box cable entry location : | bottom |  | bottom | [5 empty] | select | bottom | side
125 | 11.4.7.5 | Line conductor size : | input data | mm² | input data | mm²
126 |  | Line conductor cable type : | input data |  | input data
127 |  | Line conductor cable quantity per phase : | input data |  | input data
128 |  | Line conductor terminal box cable gland plate type : | select |  | select | [5 empty] | select | drilled gland-plate | undrilled gland-plate | other
129 |  | Connection point for portable earth : | not required |  | not required | [5 empty] | select | manufacturer's standard | 20 mm ball connection | 25 mm ball connection | not required
130 |  | Motor surge protection : | not required |  | not required | [5 empty] | select | surge arrester with capacitor in each phase | surge arrester with three phase capacitor | surge arrester only | not required
131 |  | Differential protection
132 |  | Current transformers for differential protection : | select |  | select | [5 empty] | select | full differential | self-balancing | not required
133 |  | Current transformer ratio : | input data |  | input data
134 |  | Current transformer accuracy class : | input data |  | input data
135 |  | Current transformer quantity : | input data |  | input data
136 |  | Winding partial discharge monitoring
137 | 11.4.12.5.2,11.4.12.5.3 | On-line winding partial discharge measurement : | not required |  | not required | [5 empty] | select | required | not required
138 | 11.4.12.5.2,11.4.12.5.3 | Partial discharge (PD) sensors : | select |  | select | [5 empty] | select | capacitive coupler | HFCT | Rogowski coils | other | not required
139 |  | Neutral connection
140 | 11.4.4.6,11.4.7.6 | Neutral connection : | select |  | select | [5 empty] | select | inside motor frame | inside neutral terminal box | inside line conductor terminal box | manufacturer's standard
141 |  | Water-cooled heat exchanger
142 | 11.4.3.3.6 | Cooling water type : | select |  | select | [5 empty] | select | site cooling water | sea water | brackish water | other | not applicable
143 | 11.4.3.3.6 | Maximum cooling water inlet temperature : | input data | °C | input data | °C
144 |  | Miscellaneous
145 |  | Provision for IoT hardware installation : | select |  | select | [5 empty] | select | required | not required
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the equipment.
Note on C7: Select the CAS level to be applied in IOGP S-745Q, Annex A. CAS D requires the fewest quality interventions and information requirements. Default value : D
Note on C8: Specify the country in which the project is located, in accordance with ISO 3166-1.
Note on C9: Specify the geographic location, within the country, which will determine the applicability of local regulatory requirements.
Note on C10: Select the location of the facility where the equipment will be permanently installed.
Note on C11: Select the status of the order.
Note on C12: Specify the name of the motor manufacturer.
Note on C13: Specify the model number of the motor.
Note on C14: Select the required number of poles. If "other" is selected, specify the pole requirements in "Additional notes".
Note on C15: Specify the motor frame size/designation. Where this is not specified by the purchaser, supplier to confirm the frame size as per the standard offering for the application.
Note on C17: Select the location where the motor is to be situated. If "other" is selected, specify in "Additional notes".
Note on C18: This is the altitude above sea level. The IEC 60034-1 default is 1 000 m. Select "other" and specify the value in "Additional notes" only if the site altitude is higher than 1 000 m. Default value : 1 000 or below
Note on C19: The IEC 60034-1 default is 40 °C. Select a value different from 40 °C only if the site conditions are higher than the IEC default. "If other" is selected, specify the temperature values in "Additional notes". Default value : 40
Note on C20: Select "other" and specify the value in "Additional notes" only if the site conditions are lower than 0 °C. Default value : 0
Note on C21: Select the storage conditions of the motor. This may result in the requirement of additional preservation provision at the supplier's discretion.
Note on C22: Where floating or marine location is specified, specify maximum rotation about fore-and-aft axis (rolling) of vessel under dynamic conditions defined in IEC 60092-101 and IEC 61892-5 (e.g. ± 22 ° 30 '). Specify "not applicable" if not applicable.
Note on C23: Where a floating or marine location is specified, specify the max rotation about athwartship axis (pitching) of the vessel under the dynamic conditions defined in IEC 60092-101 and IEC 61892-5 (e.g. ± 7 ° 30 '). Specify "not applicable" if not applicable.
Note on C24: Specify the chemicals and corrosives that may be present in the location environment (e.g. presence of H2S).
Note on C25: Select "yes" for unusual service conditions not covered elsewhere in IOGP S-745 such as salt-laden and abrasive dust. Specify unusual service conditions in "Additional notes". Default value : no
Note on C27: Select which certification is acceptable for motors to be located in a hazardous area. If "other" is selected, specify the certification in "Additional notes".
Note on C28: Select the temperature class for which the motor is rated for in accordance with IEC 60079-0. Default value : T3
Note on C29: Select the gas/dust group for which the motor is to be rated in accordance with IEC 60079.
Note on C30: Select the equipment protection level (EPL) for which the motor is rated in accordance with IEC 60079-14.
Note on C31: Select the type of protection for which the motor is rated in accordance with IEC 60079.
Note on C33: Select the duty type as defined in IEC-60034-1, Clause 4. The JIP33 default is S1 for single-speed use. Default value : S1
Note on C34: Specify the maximum power requirement of the driven equipment. This value should include any sizing margin requirements.
Note on C35: Select the direction of motor shaft rotation observed when facing the drive end when connecting motor terminals U-V-W to supply L1-L2-L3.
Note on C36: Select the equipment intended to be driven by the high-voltage synchronous motor. If "other" is selected, specify details of the driven equipment in "Additional notes".
Note on C37: Select the method of power transfer to the driven equipment. Specify the load drive with details in "Additional notes". Include the gearbox data sheet when provided.
Note on C38: Select the maximum value of current pulsation due to driven equipment load characteristics such as reciprocating compressor or positive displacement pump. If "other", specify the maximum pulsating current due to the coupled load in "Additional notes". Default value : 40
Note on C39: Specify the moment of inertia (MR²) of the load at the motor shaft.
Note on C40: Select the coupling hub type that the motor shaft is designed to accept. If "other" is selected, specify the coupling hub type in "Additional notes".
Note on C41: Select the coupling hub fit that the motor shaft is designed to accept. If "other" is selected, specify the coupling hub fit in "Additional notes".
Note on C43: Specify the input voltage, expressed in kV, for which the motor is rated.
Note on C44: Select the maximum steady-state voltage limit as a percentage of the supply voltage. Figure 11, zone B upper Y boundary default is 1,10 pu (10 %). If "other" is selected, specify the limit requirements in "Additional notes".
Note on C45: Select the minimum steady-state voltage limit as a percentage of the supply voltage. Figure 11, zone B lower Y boundary default is 0,90 pu (-10 %). If "other" is selected, specify the limit requirements in "Additional notes".
Note on C46: Select the supply frequency for which the motor is rated.
Note on C47: Select the maximum frequency limit as a percentage of the supply frequency at which the motor provides its rated torque. If "other" is selected, specify the limit requirements in "Additional notes".
Note on C48: Select the minimum frequency limit as a percentage of the supply frequency at which the motor is to provides rated torque. If "other" is selected, specify the limit requirements in "Additional notes".
Note on C49: Specify the 3-phase fault current at motor terminals in kA (one-half cycle after fault inception) for a duration of 0,5 s to design terminal box for withstanding the pressure buildup during a 3-phase fault.
Note on C51: Select the thermal class of the motor in accordance with IEC 60085. Default value : F
Note on C52: Select the temperature rise class of motor in accordance with IEC 60085. Default value : B
Note on C53: Select the method to be adopted for the measurement of the temperature rise of the windings. Default value : resistance method
Note on C55: Select the motor starting method for which the motor is to be provided. If "other" is selected, specify the bypass requirements in "Additional notes".
Note on C56: Select the load condition as seen by the motor at starting as per the driven equipment data sheet. Specify the load information in "Additional notes" (e.g. valve open/close, damper open/close) and provide the load curve of the driven equipment.
Note on C57: Specify the locked rotor current required to be complied by supplier, expressed as a ratio of starting current to the rated current (Is/In). Also specify the applicable tolerances over the locked rotor current.
Note on C58: Select the required tolerance for locked rotor current. While the default is +20 % as per Table 22, it is acknowledged that some projects may require a more stringent value. Default value : 20
Note on C59: Specify as 'per unit' (pu) value of the full load current (Is/In) at the rated voltage.
Note on C60: Specify at 80 % rated voltage and rated frequency as 'per unit' (pu) value of the full load current (Is/In).
Note on C61: Specify the smallest steady-state asynchronous torque that the motor develops between zero speed and the speed which corresponds to the breakdown torque when the motor is supplied at 100 % rated voltage and rated frequency.
Note on C62: Specify the smallest measured torque the motor develops at its shaft, with the rotor locked, over all its angular positions at rated voltage and rated frequency.
Note on C63: Specify the smallest measured torque the motor develops at its shaft, with the rotor locked, over all its angular positions at 80 % rated voltage and rated frequency.
Note on C64: Specify the power factor as 'per unit' (pu) value with the rotor locked at the rated voltage and rated frequency.
Note on C65: Specify the rotor moment of inertia (MR²) as defined in 3.24.
Note on C67: Specify the rated output, i.e. the required motor shaft rated mechanical power. Supplier to specify the rated output, i.e. the required motor shaft rated mechanical power, if not specified by the purchaser.
Note on C68: Specify the motor rated current while operating at the rated voltage and rated frequency.
Note on C69: Specify the steady-state synchronous rotor speed while delivering the rated output at the rated voltage and rated frequency.
Note on C70: Specify the steady-state synchronous rotor torque while delivering the rated output at the rated voltage and rated frequency.
Note on C71: Specify the maximum steady-state synchronous torque that the motor develops when the motor is supplied at the rated voltage and rated frequency, expressed as per the unit value of the rated (full load) torque.
Note on C72: Specify the efficiency of the motor while operating at the rated output.
Note on C73: Specify the efficiency of the motor while operating at 75 % of the rated output.
Note on C74: Specify the efficiency of the motor while operating at 50 % of the rated output.
Note on C75: Specify the cosine of the angle between active power and apparent power when the motor is operated at rated output.
Note on C76: Confirm the cosine of the angle between active power and apparent power when the motor is operated at 75 % of the rated output.
Note on C77: Confirm the cosine of the angle between active power and apparent power when the motor is operated at 50 % of the rated output.
Note on C79: Select the surface corrosivity category in accordance with ISO 12944-2, 5.1.1. Default value : C3
Note on C80: Select the surface durability category in accordance with ISO 12944-1, 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme. Default value : medium (M) 7 to 15 years
Note on C81: Where the manufacturer's standard paint colour is unacceptable and "other" is selected, specify the paint colour requirements in "Additional notes". Default value : manufacturer's standard
Note on C83: Select the ingress protection value in accordance with IEC 60034-5. If "other" is selected, specify the motor enclosure ingress protection in "Additional notes". Default value : IP44
Note on C84: Select the motor cooling method in accordance with IEC 60034-6. If "other" is selected, specify the motor cooling method in "Additional notes".
Note on C85: Select the heat exchanger tube construction. For water-cooled exchangers, purchaser to provide the cooling water chemistry for tube material compatibility. Specify the tube material details (e.g. 90-10 Cu-Ni, 316L stainless steel) in “Additional notes”.
Note on C86: Specify the fully assembled weight of the motor.
Note on C87: Specify the preliminary value of direct axis subtransient reactance (X''d) (Saturated/Unsaturated) in 'per unit' (pu) values for the base kVA at rated voltage and ambient temperature.
Note on C88: Specify the preliminary value of negative sequence reactance (X2) in 'per unit' (pu) values for the base kVA at rated voltage and ambient temperature.
Note on C89: Specify the preliminary value of armature short-circuit time constant (Ta).
Note on C91: Select the bearing type.
Note on C92: Specify the approved lubrication specification and associated product reference code for bearing lubrication. This applies to bearing oil, depending on bearing type selection.
Note on C93: Select the lubrication system type. Manufacturer to specify the offered system when the purchaser selects as "manufacturer's standard". Specify the need for cross-contamination mitigation measures like dry gas seal systems in "Additional notes".
Note on C94: Select whether the lubrication system needs low-speed barring for the whole train. Default value : not required
Note on C96: Specify the required balancing grade to determine the permissible limits for residual unbalance to achieve the vibrations grade (maximum shaft vibration and run out limits). Default value : G2,5
Note on C97: Select the maximum bearing housing vibration limits in accordance with IEC 60034-14:2018, Table 1. If "other" is selected, specify the bearing housing vibration limits in "Additional notes".
Note on C98: Select the maximum shaft displacement vibration limits in accordance with IEC 60034-14:2018, Table 2. If "other" is selected, specify the shaft displacement vibration limits in "Additional notes".
Note on C99: Select the maximum shaft displacement runout limits in accordance with IEC 60034-14:2018, Table 2. If "other" is selected, specify the shaft displacement vibration limits in "Additional notes".
Note on C100: Specify maximum allowable vibration limit of shaft vibration (Sp-p) in µm at rated output. When motor cannot be loaded to rated output, rotor rated temperature test to be considered before measurement of vibrations.
Note on C101: When "required" is selected, the motor manufacturer will provide analysis and/or data/model required for the lateral vibration analysis to the unit supplier. When "not required" is selected, no action is expected from the motor manufacturer. Default value : not required
Note on C102: When "required" is selected, the motor manufacturer will be responsible for providing the data/model required for the torsional analysis to the unit supplier. When "not required" is selected, no action is expected from the motor manufacturer. Default value : not required
Note on C103: Select whether proximity probe(s) for vibration measurement are required to be installed by the manufacturer. Typically, a speed of 1 200 rpm and above is the threshold value of speed when the motor is provided with means for vibration measurement.
Note on C105: Specify the maximum permissible motor A-weighted sound pressure level at a reference distance of 1 m at no load.
Note on C107: Select the scope of supply of excitation system for the synchronous motor. Default value : by manufacturer
Note on C108: Select the power supply options required for the exciter. For external power supply, provide details in "Additional notes" column.
Note on C110: Select the location of the control panel to be installed at site. Default value : indoor
Note on C111: Select the cable entry location based on the installation planned.
Note on C112: Select the type of cable entry considered for the enclosure.
Note on C113: Select the requirement of anti-condensation heaters in control panel.
Note on C114: Select the communication protocol implemented in components having interface with electrical control system. If "other" is selected, specify in the "Additional notes".
Note on C116: Select the requirement of anti-condensation heaters in the motor. Default value : windings
Note on C117: Select the supply voltage for which the anti-condensation heater will be rated. Refer to the project specified voltage level applicable in the voltage range selected.
Note on C118: Select the language to be used for the label warning that heater terminals may be live when the motor is isolated. When the language is other than English, specify it in "Additional notes".
Note on C120: Select the ingress protection in accordance with IEC 60034-5 for which the terminal boxes are rated. Default value : IP55
Note on C122: Select the line conductor terminal box type to determine the terminal box design and construction principles. For a different termination type like copper busbars, select "other" and specify details in "Additional notes". Default value : manufacturer's standard
Note on C123: Select the line conductor terminal box location when viewed from the drive end of the motor, using coding in accordance with IEC 60034-7:2020. For double ended motors specify the requirement in "Additional notes".
Note on C124: Select the location from which the cable will enter the terminal box at site for the supplier to orient the terminals and terminal box accordingly. Default value : bottom
Note on C125: Specify the size (cross-section area) of the line conductor.
Note on C126: Specify the line conductor cable type (e.g. single-core, multi-core cable, armoured, un-armoured).
Note on C127: Specify the number of runs of cable per phase.
Note on C128: Select which cable gland plate entry system is required for the application. If "other" is selected, specify details in '"Additional notes".
Note on C129: Where a fully insulated termination system is not provided, select the required provision of connection point for attaching a portable earthing device on each phase and earth. Default value : not required
Note on C130: Select whether motor surge protection is required. Manufacturer to ensure that space in the terminal box is provided. Type (capacitor/ surge arrestor), capacitor rating and rated voltage of surge protection device to be specified in "Additional notes". Default value : not required
Note on C132: Select the requirement for the pre-installed differential protection current transformers to be provided by the supplier.
Note on C133: Specify what differential protection current transformer ratio is required (e.g. "400/1 A). Specify "not applicable" where differential protection is not required.
Note on C134: Specify what differential protection current transformer accuracy class is required. Specify "not applicable" when differential protection is not required.
Note on C135: Specify the quantity of differential protection current transformer required. Specify "not applicable" when differential protection is not required.
Note on C137: Select whether on-line winding partial discharge measurement is required. Default value : not required
Note on C138: Select the type of partial discharge sensing element to be provided. If "capacitive coupler" is selected, specify the capacitance value in "Additional notes".
Note on C140: Select where a neutral terminal connection is to be made. This is typically decided as per the differential protection scheme and the connection arrangement will facilitate winding testing activities.
Note on C142: Select the type of cooling water. Provide site utility data for detailed specification of the cooling water available for the project. Where a heat exchanger is not provided, select "not applicable".
Note on C143: Specify the maximum cooling water inlet temperature as per project specification and site conditions.
Note on C145: Select the requirement of mounting provisions of IoT hardware provisions on the motor. Specify the mounting points and installation provisions in "Additional notes". IoT hardware may be procured and mounted by the purchaser at a later date.

## Convertor Duty Motor
Row | IOGP S-745D (1.01) Procurement Data Sheet for High-voltage Synchronous Machines (IEC) Convertor Duty Motor | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Project country : | input data |  | input data
9 |  | Project region : | input data |  | input data
10 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine - coastal | subsea | buried | onshore
11 |  | Order status : | select |  | select | [5 empty] | select | for enquiry | for purchase
12 |  | Manufacturer : | input data |  | input data
13 |  | Model number : | input data |  | input data
14 |  | Number of poles : | select |  | select | [5 empty] | select | 2 pole | 4 pole | 6 pole | 8 pole | other
15 | 11.4.2.3.1 | Frame size/designation : | input data |  | input data
16 |  | Converter manufacturer : | input data |  | input data
17 |  | Converter model number : | input data |  | input data
18 |  | Site conditions
19 | 6.1 | Location environment : | select |  | select | [5 empty] | select | indoor | onshore - coastal | onshore - desert | onshore - inland | offshore - fixed | offshore - floating | marine - ship | other
20 | 6.1 | Altitude : | 1 000 or below | m | 1 000 or below | m |  |  |  |  | select | 1 000 or below | other
21 | 6.1 | Maximum ambient air temperature : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50 | other
22 | 6.1 | Minimum ambient air temperature : | 0 | °C | 0 | °C |  |  |  |  | select | 0 | other
23 | 6.1 | Storage conditions : | select |  | select | [5 empty] | select | conditioned environment | non-conditioned environment
24 | 6.1 | Maximum rolling of vessel in dynamic conditions : | input data |  | input data
25 | 6.1 | Maximum pitching of vessel in dynamic conditions : | input data |  | input data
26 | 6.1 | Chemicals and corrosives : | input data |  | input data
27 | 6.1 | Unusual service conditions : | no |  | no | [5 empty] | select | yes | no
28 |  | Motors rated for use in hazardous area
29 | 11.4.16.1.1,11.4.16.1.2 | Hazardous area equipment certification : | select |  | select | [5 empty] | select | ATEX | IECEx | other | not applicable
30 | 11.4.16.1.1,11.4.16.1.2 | Temperature class : | T3 |  | T3 | [5 empty] | select | T3 | T4 | T5 | T6 | T1 | T2 | not applicable
31 | 11.4.16.1.1,11.4.16.1.2 | Gas/dust group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | not applicable
32 | 11.4.16.1.1,11.4.16.1.2,11.4.16.3 | Equipment protection level : | select |  | select | [5 empty] | select | EPL Gb | EPL Gc | EPL Db | EPL Dc | not applicable
33 | 11.4.16.1.1,11.4.16.1.2,11.4.16.3 | Type of protection : | select |  | select | [5 empty] | select | Ex db | Ex db eb | Ex pxb | Ex pxb eb | Ex pzc | not applicable
34 |  | Driven equipment interface
35 | 4.1 | Duty type : | S1 |  | S1 | [5 empty] | select | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8
36 | 5.5.3 | Duty point shaft power : | input data | kW | input data | kW
37 | 10.4.2 | Direction of rotation : | select |  | select | [5 empty] | select | clockwise | counter-clockwise
38 |  | Driven equipment type : | select |  | select | [5 empty] | select | centrifugal pump | centrifugal fan | centrifugal compressor | reciprocating pump | reciprocating compressor | positive displacement pump | other
39 |  | Load drive : | select |  | select | [5 empty] | select | direct coupled | gearbox | other
40 | 11.3.3.2 | Maximum pulsating current : | 40 | % of FLC | 40 | % of FLC |  |  |  |  | select | 40 | other
41 | 11.3.3.2 | Moment of inertia of load (Jext) : | input data | kg·m² | input data | kg·m²
42 |  | Coupling hub type : | select |  | select | [5 empty] | select | integral flange | cylindrical | taper | other
43 |  | Coupling hub fit : | select |  | select | [5 empty] | select | keyed | keyless | hydraulic | other
44 |  | Electrical operating conditions
45 |  | Impulse voltage insulation class : | select |  | select | [5 empty] | select | none | IVIC Class 1 | IVIC Class 2 | IVIC Class 3 | IVIC Class 4 | IVIC Class 5 | IVIC Class 6 | IVIC Class 7 | IVIC Class S
46 | 7.4 | Motor rated voltage : | input data | kV | input data | kV
47 | 7.4 | Motor rated frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
48 |  | Thermal performance
49 | 8.1 | Insulation thermal class : | F |  | F | [5 empty] | select | F | H
50 | 8.1 | Temperature rise class : | B |  | B | [5 empty] | select | B | F
51 |  | Determination of winding temperature rise : | resistance method |  | resistance method | [5 empty] | select | resistance method | embedded temperature detector method | manufacturer's standard
52 |  | Starting performance
53 |  | Starting load : | select |  | select | [5 empty] | select | unloaded | loaded
54 |  | Moment of inertia of the rotor (Jm) : | input data | kg·m² | input data | kg·m²
55 |  | Operating performance
56 |  | Converter operation mode : | select |  | select | [5 empty] | select | variable torque | constant torque | constant power | other
57 | 5.5.3 | Rated output : | input data | kW | input data | kW
58 |  | Rated current : | input data | A | input data | A
59 |  | Rated synchronous speed : | input data | min⁻¹ | input data | min⁻¹
60 |  | Maximum continuous operating speed : | input data | min⁻¹ | input data | min⁻¹
61 |  | Minimum continuous operating speed : | input data | min⁻¹ | input data | min⁻¹
62 |  | Rated torque : | input data | N·m | input data | N·m
63 | 5.9,Table 24 | Efficiency at maximum continuous operating speed : | input data | % | input data | %
64 | 5.9,Table 24 | Efficiency at minimum continuous operating speed : | input data | % | input data | %
65 | 5.9,Table 24 | Efficiency at maximum continuous operating speed at maximum torque : | input data | % | input data | %
66 |  | Power factor at rated output : | input data | pu | input data | pu
67 |  | Power factor at maximum continuous operating speed : | input data | pu | input data | pu
68 |  | Power factor at minimum continuous operating speed : | input data | pu | input data | pu
69 |  | Surface protection
70 | 11.4.2.3.4,11.4.2.4.1,11.4.2.4.2,Table 27 | Surface protection corrosivity category : | C3 |  | C3 | [5 empty] | select | C3 | C4 | C5 | CX
71 | 11.4.2.3.4,11.4.2.4.3,Table 27 | Surface protection durability category : | medium (M) 7 to 15 years |  | medium (M) 7 to 15 years | [5 empty] | select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
72 |  | Paint colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
73 |  | Motor construction
74 | 6.8,Table 25 | Motor enclosure ingress protection : | IP44 |  | IP44 | [5 empty] | select | IP56 | IP55 | IP44 | IPW24 | IP23 | other
75 | 11.4.3.1.1,Table 28 | Cooling method : | select |  | select | [5 empty] | select | IC4A1A1 | IC5A1A1 | IC6A1A1 | IC7A1W7 | IC8A1W7 | other
76 | 11.4.3.2.3 | Heat exchanger tube construction : | select |  | select | [5 empty] | select | single tubing | double tubing | not applicable
77 |  | Motor weight : | input data | kg | input data | kg
78 |  | Direct axis subtransient reactance (X''d)(Saturated/Unsaturated) : | input data | pu | input data | pu
79 |  | Negative sequence reactance (X2) : | input data | pu | input data | pu
80 |  | Armature short-circuit time constant (Ta) : | input data | s | input data | s
81 |  | Bearings (general)
82 |  | Bearing type : | select |  | select | [5 empty] | select | sleeve bearings | tilted pad bearings
83 | 9.1 | Lubrication specification : | input data |  | input data
84 |  | Lubrication system : | select |  | select | [5 empty] | select | manufacturer's standard | self-lubrication | flooded lubrication provided by others | flooded independent lubrication | flooded common lubrication system with driven equipment
85 | 11.4.9.2.13 | Low-speed barring : | not required |  | not required | [5 empty] | select | required | not required
86 |  | Vibration
87 | 11.4.5.3 | Applicable rotor balancing grade : | G2,5 |  | G2,5 | [5 empty] | select | G2,5 | G1,0 | G0,665 | manufacturer's standard
88 | 9.1,11.4.5.4,11.4.5.5,11.4.5.6,11.4.5.7 | Bearing housing vibration limits : | select |  | select | [5 empty] | select | grade A - IEC 60034-14:2018 Table 1 | grade B - IEC 60034-14:2018 Table 1 | other | not applicable
89 | 9.1,11.3.4.2,11.4.5.4,11.4.5.5,11.4.5.6,11.4.5.7 | Maximum shaft vibration limit : | select |  | select | [5 empty] | select | grade A - IEC 60034-14:2018 Table 2 | grade B - IEC 60034-14:2018 Table 2 | other | not applicable
90 | 9.1,11.3.4.2,11.4.5.4,11.4.5.5,11.4.5.6,11.4.5.7 | Maximum shaft runout limit : | select |  | select | [5 empty] | select | grade A - IEC 60034-14:2018 Table 2 | grade B - IEC 60034-14:2018 Table 2 | other | not applicable
91 | 11.3.4.2 | Maximum allowable vibration limit of shaft vibration (Sp-p) at rated output : | input data | µm | input data | µm
92 | 11.3.4.2,11.4.10 | Lateral vibration analysis : | not required |  | not required | [5 empty] | select | required for standalone motor | required for standalone motor and data/model for driven equipment supplier | not required
93 | 11.4.11,11.4.15.3 | Torsional vibration analysis : | not required |  | not required | [5 empty] | select | required data/model input for driven equipment supplier | not required
94 | 11.4.9.2.7 | Proximity probes for vibration measurement : | select |  | select | [5 empty] | select | two non-contacting proximity probes per sleeve bearing | two non-contacting proximity probes per sleeve bearing and one phase reference transducer | not required
95 |  | Noise
96 | 11.3.5.2,11.3.5.3 | Sound pressure level at no load : | input data | dB(A) | input data | dB(A)
97 |  | Excitation data
98 |  | Excitation system scope : | by manufacturer |  | by manufacturer | [5 empty] | select | by manufacturer | by purchaser
99 |  | Exciter power : | select |  | select | [5 empty] | select | external power supply | permanent magnet generator (PMG)
100 |  | Control and protection
101 |  | Control panel location : | indoor |  | indoor | [5 empty] | select | indoor | outdoor
102 |  | Cable entry location : | select |  | select | [5 empty] | select | bottom | top | bottom and top
103 |  | Cable entry type : | select |  | select | [5 empty] | select | removable-undrilled plate | multi-cable transit (MCT)
104 |  | Control panel anti-condensation heater : | select |  | select | [5 empty] | select | required | not required
105 | 11.4.13.3.1,11.4.17.4.3 | Communication protocol for interface with electrical control system : | select |  | select | [5 empty] | select | Modbus TCP/IP | Modbus RTU | Profinet | Profibus | Ethernet | other | not applicable
106 |  | Anti-condensation heaters
107 | 11.4.14.1 | Anti-condensation heater : | windings |  | windings | [5 empty] | select | windings | windings and line conductor terminal box | not required
108 | 11.4.14.1 | Anti-condensation heater supply voltage (AC) : | select | V | select | V |  |  |  |  | select | 100-120 single phase | 200-240 single phase | 380-440 three phase
109 |  | Warning label language : | select |  | select | [5 empty] | select | English | other
110 |  | Terminal boxes (general)
111 | Table 25 | Degree of ingress protection of all terminal boxes : | IP55 |  | IP55 | [5 empty] | select | IP55 | IP56 | other
112 |  | Line conductor terminal box
113 |  | Line conductor terminal box type : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | air insulated | phase insulated with heat shrink insulation | phase insulated with separable connectors | phase separated | phase segregated | other
114 |  | Line conductor terminal box location viewed from drive end : | select |  | select | [5 empty] | select | right | left | top
115 |  | Line conductor terminal box cable entry location : | bottom |  | bottom | [5 empty] | select | bottom | side
116 | 11.4.7.5 | Line conductor size : | input data | mm² | input data | mm²
117 |  | Line conductor cable type : | input data |  | input data
118 |  | Line conductor cable quantity per phase : | input data |  | input data
119 |  | Line conductor terminal box cable gland plate type : | select |  | select | [5 empty] | select | drilled gland-plate | undrilled gland-plate | other
120 |  | Connection point for portable earth : | not required |  | not required | [5 empty] | select | manufacturer's standard | 20 mm ball connection | 25 mm ball connection | not required
121 |  | Differential protection
122 |  | Current transformers for differential protection : | select |  | select | [5 empty] | select | full differential | self-balancing | not required
123 |  | Current transformer ratio : | input data |  | input data
124 |  | Current transformer accuracy class : | input data |  | input data
125 |  | Current transformer quantity : | input data |  | input data
126 |  | Winding partial discharge monitoring
127 | 11.4.12.5.2,11.4.12.5.3 | On-line winding partial discharge measurement : | not required |  | not required | [5 empty] | select | required | not required
128 | 11.4.12.5.2,11.4.12.5.3 | Partial discharge (PD) sensors : | select |  | select | [5 empty] | select | capacitive coupler | HFCT | Rogowski coils | other | not required
129 |  | Neutral connection
130 | 11.4.4.6,11.4.7.6 | Neutral connection : | select |  | select | [5 empty] | select | inside motor frame | inside neutral terminal box | inside line conductor terminal box | manufacturer's standard
131 |  | Water-cooled heat exchanger
132 | 11.4.3.3.6 | Cooling water type : | select |  | select | [5 empty] | select | site cooling water | sea water | brackish water | other | not applicable
133 | 11.4.3.3.6 | Maximum cooling water inlet temperature : | input data | °C | input data | °C
134 |  | Miscellaneous
135 |  | Provision for IoT hardware installation : | select |  | select | [5 empty] | select | required | not required
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the equipment.
Note on C7: Select the CAS level to be applied in IOGP S-745Q, Annex A. CAS D requires the fewest quality interventions and information requirements. Default value : D
Note on C8: Specify the country in which the project is located, in accordance with ISO 3166-1.
Note on C9: Specify the geographic location, within the country, which will determine the applicability of local regulatory requirements.
Note on C10: Select the location of the facility where the equipment will be permanently installed.
Note on C11: Select the status of the order.
Note on C12: Specify the name of the motor manufacturer.
Note on C13: Specify the motor model number.
Note on C14: Select the required number of poles. If "other" is selected, specify the pole requirements in "Additional notes".
Note on C15: Specify the motor frame size/designation. Where this is not specified by the purchaser, supplier to confirm the frame size as per the standard offering for the application.
Note on C16: Specify the manufacturer of the converter from which the motor is to be driven.
Note on C17: Specify the model number of converter from which the motor is to be driven.
Note on C19: Select the location where the motor is to be situated. If "other" is selected, specify in "Additional notes".
Note on C20: This is the altitude above sea-level. The IEC 60034-1 default is 1 000 m. Select "other" and specify the value in "Additional notes" only if the site altitude is higher than 1 000 m. Default value : 1 000 or below
Note on C21: The IEC 60034-1 default is 40 °C. Select a value different from 40 °C only if the site conditions are higher than the IEC default. "If other" is selected, specify the temperature values in "Additional notes". Default value : 40
Note on C22: Select "other" and specify the value in "Additional notes" only if the site conditions are lower than 0 °C. Default value : 0
Note on C23: Select the storage conditions of the motor. This may result in the requirement of additional preservation provision at the supplier's discretion.
Note on C24: Where floating or marine location is specified, specify maximum rotation about fore-and-aft axis (rolling) of vessel under dynamic conditions defined in IEC 60092-101 and IEC 61892-5 (e.g. ± 22 ° 30 '). Specify "not applicable" if not applicable.
Note on C25: Where a floating or marine location is specified, specify the max rotation about athwartship axis (pitching) of the vessel under the dynamic conditions defined in IEC 60092-101 and IEC 61892-5 (e.g. ± 7 ° 30 '). Specify "not applicable" if not applicable.
Note on C26: Specify the chemicals and corrosives that may be present in the location environment.
Note on C27: Select "yes" for unusual service conditions not covered elsewhere in IOGP S-745 such as salt-laden and abrasive dust. Specify unusual service conditions in "Additional notes". Default value : no
Note on C29: Select which certification is acceptable for motors to be located in a hazardous area. If "other" is selected, specify the certification in "Additional notes".
Note on C30: Select the temperature class for which the motor is rated for in accordance with IEC 60079-0. Default value : T3
Note on C31: Select the gas/dust group for which the motor is to be rated in accordance with IEC 60079.
Note on C32: Select the equipment protection level (EPL) for which the motor is rated in accordance with IEC 60079-14.
Note on C33: Select the type of protection for which the motor is rated in accordance with IEC 60079.
Note on C35: Select the duty type as defined in IEC-60034-1, clause 4. The JIP33 default is S1 for single-speed use. Default value : S1
Note on C36: Specify the maximum power requirement of the driven equipment. This value should include any sizing margin requirements.
Note on C37: Select the direction of motor shaft rotation observed when facing the drive end when connecting motor terminals U-V-W to supply L1-L2-L3.
Note on C38: Select the equipment intended to be driven by the high-voltage synchronous motor. If "other" is selected, specify details of the driven equipment in "Additional notes".
Note on C39: Select the method of power transfer to the driven equipment. Specify the load drive with details in "Additional notes". Include the gearbox data sheet when provided.
Note on C40: Select the maximum value of current pulsation due to driven equipment load characteristics such as reciprocating compressor or positive displacement pump. If "other", specify the maximum pulsating current due to the coupled load in "Additional notes". Default value : 40
Note on C41: Specify the moment of inertia (MR²) of the load at the motor shaft.
Note on C42: Select the coupling hub type that the motor shaft is designed to accept. If "other" is selected, specify the coupling hub type in "Additional notes".
Note on C43: Select the coupling hub fit that the motor shaft is designed to accept. If "other" is selected, specify the coupling hub fit in "Additional notes".
Note on C45: Supplier to specify the insulation class as defined in IEC 60034-18-42 Table D.2.
Note on C46: Specify the input voltage, expressed in kV, for which the motor is rated.
Note on C47: Select the supply frequency for which the motor is rated.
Note on C49: Select the thermal class of the motor in accordance with IEC 60085. Default value : F
Note on C50: Select the temperature rise class of motor in accordance with IEC 60085. Default value : B
Note on C51: Select the method to be adopted for the measurement of the temperature rise of the windings. Default value : resistance method
Note on C53: Select the load condition as seen by the motor at starting as per the driven equipment data sheet. Specify the load information in "Additional notes" (e.g. valve open/close, damper open/close) and provide the load curve of the driven equipment.
Note on C54: Specify the rotor moment of inertia (MR²) as defined in 3.24.
Note on C56: Select the converter operation mode based on the driven equipment type. Select "other" for a different or combination of torque and power characteristics and specify in "Additional notes".
Note on C57: Specify the rated output, i.e. the required motor shaft rated mechanical power. Supplier to specify the rated output, i.e. the required motor shaft rated mechanical power, if not specified by the purchaser.
Note on C58: Specify the motor rated current while operating at the rated voltage and rated frequency.
Note on C59: Specify the steady-state synchronous rotor speed while delivering the rated output at the rated voltage and rated frequency.
Note on C60: Specify the maximum continuous motor operating speed required by the driven equipment.
Note on C61: Specify the minimum continuous motor operating speed required by the driven equipment.
Note on C62: Specify the steady-state synchronous rotor torque while delivering the rated output at the rated voltage and rated frequency.
Note on C63: Specify the efficiency at the maximum continuous operating speed at the upper torque value of the load window as per IEC 61800-2.
Note on C64: Specify the efficiency at the minimum continuous operating speed at the upper torque value of the load window as per IEC 61800-2.
Note on C65: Specify the efficiency at the maximum continuous operating speed at the upper torque value of the load window as per IEC 61800-2.
Note on C66: Specify the cosine of the angle between active power and apparent power when the motor is operated at the rated output.
Note on C67: Specify the cosine of the angle between active power and apparent power at the maximum continuous operating speed at the upper torque value of the load window as per IEC 61800-2.
Note on C68: Specify the cosine of the angle between active power and apparent power at the minimum continuous operating speed at the upper torque value of the load window as per IEC 61800-2.
Note on C70: Select the surface corrosivity category in accordance with ISO 12944-2, 5.1.1. Default value : C3
Note on C71: Select the surface durability category in accordance with ISO 12944-1, 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme. Default value : medium (M) 7 to 15 years
Note on C72: Where the manufacturer's standard paint colour is unacceptable and "other" is selected, specify the paint colour requirements in "Additional notes". Default value : manufacturer's standard
Note on C74: Select the ingress protection value in accordance with IEC 60034-5. If "other" is selected, specify the motor enclosure ingress protection in "Additional notes". Default value : IP44
Note on C75: Select the motor cooling method in accordance with IEC 60034-6. If "other" is selected, specify the motor cooling method in "Additional notes".
Note on C76: Select the heat exchanger tube construction. For water-cooled exchangers, purchaser to provide the cooling water chemistry for tube material compatibility. Specify the tube material details (e.g. 90-10 Cu-Ni, 316L stainless steel) in “Additional notes”.
Note on C77: Specify the fully assembled weight of the motor.
Note on C78: Specify the preliminary value of direct axis subtransient reactance (X''d) (Saturated/Unsaturated) in 'per unit' (pu) values for the base kVA at rated voltage and ambient temperature.
Note on C79: Specify the preliminary value of negative sequence reactance (X2) in 'per unit' (pu) values for the base kVA at rated voltage and ambient temperature.
Note on C80: Specify the preliminary value of armature short-circuit time constant (Ta).
Note on C82: Select the bearing type.
Note on C83: Specify the approved lubrication specification and associated product reference code for bearing lubrication. This applies to bearing oil, depending on bearing type selection.
Note on C84: Select the lubrication system type. Manufacturer to specify the offered system when the purchaser selects as "manufacturer's standard". Specify the need for cross-contamination mitigation measures like dry gas seal systems in "Additional notes".
Note on C85: Select whether the lubrication system needs low-speed barring for the whole train. Default value : not required
Note on C87: Specify the required balancing grade to determine the permissible limits for residual unbalance to achieve the vibrations grade (maximum shaft vibration and run out limits). Default value : G2,5
Note on C88: Select the maximum bearing housing vibration limits in IEC 60034-14:2018, Table 1. If "other" is selected, specify the bearing housing vibration limits in "Additional notes".
Note on C89: Select the maximum shaft displacement vibration limits in accordance with IEC 60034-14:2018, Table 2. If "other" is selected, specify the shaft displacement vibration limits in "Additional notes".
Note on C90: Select the maximum shaft displacement runout limits in accordance with IEC 60034-14:2018, Table 2. If "other" is selected, specify the shaft displacement vibration limits in "Additional notes".
Note on C91: Specify maximum allowable vibration limit of shaft vibration (Sp-p) in µm at rated output. When motor cannot be loaded to rated output, rotor rated temperature test to be considered before measurement of vibrations.
Note on C92: When "required" is selected, the motor manufacturer will provide analysis and/or data/model required for the lateral vibration analysis to the unit supplier. When "not required" is selected, no action is expected from the motor manufacturer. Default value : not required
Note on C93: When "required" is selected, the motor manufacturer will be responsible for providing the data/model required for the torsional analysis to the unit supplier. When "not required" is selected, no action is expected from the motor manufacturer. Default value : not required
Note on C94: Select whether proximity probe(s) for vibration measurement are required to be installed by the manufacturer. Typically, a speed of 1 200 rpm and above is the threshold value of speed when the motor is provided with means for vibration measurement.
Note on C96: Specify the maximum permissible motor A-weighted sound pressure level at a reference distance of 1 m at no load.
Note on C98: Select the scope of supply of excitation system for the synchronous motor. Default value : by manufacturer
Note on C99: Select the power supply options required for the exciter. For external power supply, provide details in "Additional notes" column.
Note on C101: Select the location of the control panel to be installed at site. Default value : indoor
Note on C102: Select the cable entry location based on the installation planned.
Note on C103: Select the type of cable entry considered for the enclosure (gland plate or multi-cable transit).
Note on C104: Select the requirement of anti-condensation heaters in control panel.
Note on C105: Select the communication protocol implemented in components having interface with electrical control system. If "other" is selected, specify in the "Additional notes".
Note on C107: Select the requirement of anti-condensation heaters in the motor. Default value : windings
Note on C108: Select the supply voltage for which the anti-condensation heater will be rated. Refer to the project specified voltage level applicable in the voltage range selected.
Note on C109: Select the language to be used for the label warning that heater terminals may be live when the motor is isolated. When the language is other than English, specify it in "Additional notes".
Note on C111: Select the ingress protection in accordance with IEC 60034-5 for which the terminal boxes are rated. Default value : IP55
Note on C113: Select the line conductor terminal box type to determine the terminal box design and construction principles. For a different termination type like copper busbars, select "other" and specify details in "Additional notes". Default value : manufacturer's standard
Note on C114: Select the line conductor terminal box location when viewed from the drive end of the motor, using coding in accordance with IEC 60034-7:2020. For double ended motors specify the requirement in "Additional notes".
Note on C115: Select the location from which the cable will enter the terminal box at site for the supplier to orient the terminals and terminal box accordingly. Default value : bottom
Note on C116: Specify the size (cross-section area) of the line conductor.
Note on C117: Specify the line conductor cable type (e.g. single-core, multi-core cable, armoured, un-armoured).
Note on C118: Specify the number of runs of cable per phase.
Note on C119: Select which cable gland plate entry system is required for the application. If "other" is selected, specify details in '"Additional notes".
Note on C120: Where a fully insulated termination system is not provided, select the required provision of connection point for attaching a portable earthing device on each phase and earth. Default value : not required
Note on C122: Select the requirement for the pre-installed differential protection current transformers to be provided by the supplier.
Note on C123: Specify what differential protection current transformer ratio is required (e.g. "400/1 A). Specify "not applicable" where differential protection is not required.
Note on C124: Specify what differential protection current transformer accuracy class is required. Specify "not applicable" when differential protection is not required.
Note on C125: Specify the quantity of differential protection current transformer required. Specify "not applicable" when differential protection is not required.
Note on C127: Select whether on-line winding partial discharge measurement is required. Default value : not required
Note on C128: Select the type of partial discharge sensing element to be provided. If "capacitive coupler" is selected, specify the capacitance value in "Additional notes".
Note on C130: Select where a neutral terminal connection is to be made. This is typically decided as per the differential protection scheme and the connection arrangement will facilitate winding testing activities.
Note on C132: Select the type of cooling water. Provide site utility data for detailed specification of the cooling water available for the project. Where a heat exchanger is not provided, select "not applicable".
Note on C133: Specify the maximum cooling water inlet temperature as per project specification and site conditions.
Note on C135: Select the requirement of mounting provisions of IoT hardware provisions on the motor. Specify the mounting points and installation provisions in "Additional notes". IoT hardware may be procured and mounted by the purchaser at a later date.

## Generators
Row | IOGP S-745D (1.01) Procurement Data Sheet for High-voltage Synchronous Machines (IEC) Generators | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Project country : | input data |  | input data
9 |  | Project region : | input data |  | input data
10 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine - coastal | subsea | buried | onshore
11 |  | Order status : | select |  | select | [5 empty] | select | for enquiry | for purchase
12 |  | Generator manufacturer : | input data |  | input data
13 |  | Generator model number : | input data |  | input data
14 |  | Number of poles : | select |  | select | [5 empty] | select | 2 pole | 4 pole | 6 pole | 8 pole | other
15 | 11.4.2.3.1 | Frame size/designation : | input data |  | input data
16 |  | Site conditions
17 | 6.1 | Location environment : | select |  | select | [5 empty] | select | indoor location | onshore - coastal | onshore - desert | onshore - inland | offshore - fixed | offshore - floating | marine - ship | other
18 | 6.1 | Altitude : | 1 000 or below | m | 1 000 or below | m |  |  |  |  | select | 1 000 or below | other
19 | 6.1 | Maximum ambient air temperature : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50 | other
20 | 6.1 | Minimum ambient air temperature : | 0 | °C | 0 | °C |  |  |  |  | select | 0 | other
21 | 6.1 | Storage conditions : | select |  | select | [5 empty] | select | conditioned environment | non-conditioned environment
22 | 6.1 | Maximum rolling of vessel in dynamic conditions : | input data |  | input data
23 | 6.1 | Maximum pitching of vessel in dynamic conditions : | input data |  | input data
24 | 6.1 | Chemicals and corrosives : | input data |  | input data
25 | 6.1 | Unusual service conditions : | no |  | no | [5 empty] | select | yes | no
26 |  | Electrical system data
27 | 7.4 | System rated voltage : | input data | kV | input data | kV
28 | 7.4 | Maximum voltage variation : | select | % | select | % |  |  |  |  | select | 10 | 5 | other
29 | 7.4 | Minimum voltage variation : | select | % | select | % |  |  |  |  | select | -10 | -5 | other
30 | 7.4 | System rated frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
31 | 7.4 | Maximum frequency variation : | select | % | select | % |  |  |  |  | select | 2 | 4 | other
32 | 7.4 | Minimum frequency variation : | select | % | select | % |  |  |  |  | select | -2 | -6 | other
33 |  | 3-phase short-circuit MVA rating at generator bus : | input data | MVA | input data | MVA
34 |  | Maximum earth fault current : | input data | A | input data | A
35 |  | Neutral earthing : | select |  | select | [5 empty] | select | resistance | reactance | unearthed | solidly earthed | other
36 |  | Generator operation mode : | select |  | select | [5 empty] | select | independent | parallel with grid | parallel with other generators
37 | 5.5.2,11.4.17.1.1,5.5.4 | Generator output at rated power factor : | input data | kVA | input data | kVA
38 |  | Generator to be installed in hazardous area
39 | 11.4.16.1.1,11.4.16.1.2 | Hazardous area equipment certification : | select |  | select | [5 empty] | select | ATEX | IECEx | other | not applicable
40 | 11.4.16.1.1,11.4.16.1.2 | Temperature class : | T3 |  | T3 | [5 empty] | select | T3 | T4 | T5 | T6 | T1 | T2 | not applicable
41 | 11.4.16.1.1,11.4.16.1.2 | Gas/dust group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | not applicable
42 | 11.4.16.1.1,11.4.16.1.2,11.4.16.3 | Equipment protection level : | select |  | select | [5 empty] | select | EPL Gb | EPL Gc | EPL Db | EPL Dc | not applicable
43 | 11.4.16.1.1,11.4.16.1.2,11.4.16.3 | Type of protection : | select |  | select | [5 empty] | select | Ex db | Ex db eb | Ex pxb | Ex pxb eb | Ex pzc | not applicable
44 |  | Driver equipment interface
45 | 11.3.3.2 | Driver moment of inertia reflected to generator (Jext) : | input data | kg·m² | input data | kg·m²
46 |  | Coupling with drive : | select |  | select | [5 empty] | select | direct coupled | gearbox | other
47 |  | Coupling hub type : | select |  | select | [5 empty] | select | integral flange | cylindrical | taper | other
48 |  | Coupling hub fit : | select |  | select | [5 empty] | select | keyed | keyless | hydraulic | other
49 |  | Generator data
50 | 5.5.2 | Rated power factor : | input data |  | input data
51 | 6.8,Table 25 | Generator ingress protection : | IP44 |  | IP44 | [5 empty] | select | IP55 | IP56 | IP54 | IP44 | IP23 | other
52 | 10.4.2 | Direction of rotation : | select |  | select | [5 empty] | select | clockwise | counter-clockwise
53 | 11.4.3.1.1,Table 28 | Cooling method : | select |  | select | [5 empty] | select | IC4A1A1 | IC5A1A1 | IC6A1A1 | IC7A1W7 | IC8A1W7 | other
54 | 11.4.3.2.3 | Heat exchanger tube construction : | select |  | select | [5 empty] | select | single tubing | double tubing | not applicable
55 |  | Generator speed : | input data | min⁻¹ | input data | min⁻¹
56 |  | Generator full load current : | input data | A | input data | A
57 |  | Rotor construction : | select |  | select | [5 empty] | select | solid cylindrical | laminated cylindrical | salient pole - solid | salient pole - laminated/bolted | retaining rings
58 |  | Generator weight : | input data | kg | input data | kg
59 |  | Minimum allowed direct-axis transient reactance (X'd)(Saturated) : | input data | pu | input data | pu
60 |  | Maximum allowed direct-axis transient reactance (X'd)(Saturated) : | input data | pu | input data | pu
61 |  | Direct-axis sub-transient reactance (X''d)(Unsaturated) : | input data | pu | input data | pu
62 |  | Direct -axis transient reactance (X'd)(Unsaturated) : | input data | pu | input data | pu
63 |  | Negative sequence reactance (X2) : | input data | pu | input data | pu
64 |  | Armature short-circuit time constant (Ta) : | input data | s | input data | s
65 |  | Generator controls
66 |  | Automatic voltage regulator manufacturer : | input data |  | input data
67 |  | Automatic voltage regulator model : | input data |  | input data
68 |  | Voltage regulation grade as per BS 4999-140 : | select |  | select | [5 empty] | select | VR2.13 | VR2.23 | VR2.33 | VR3.11 | other
69 |  | Automatic synchronizer : | select |  | select | [5 empty] | select | required | not required
70 |  | Thermal performance of generator and exciter
71 | 8.1 | Insulation thermal class : | F |  | F | [5 empty] | select | F | H
72 | 8.1 | Temperature rise class : | B |  | B | [5 empty] | select | B | F
73 |  | Determination of winding temperature rise : | resistance method |  | resistance method | [5 empty] | select | resistance method | embedded temperature detector method | manufacturer's standard
74 |  | Operating performance
75 | 5.9,Table 24 | Efficiency at rated output : | input data | % | input data | %
76 | 5.9,Table 24 | Efficiency at 75 % of rated output : | input data | % | input data | %
77 | 5.9,Table 24 | Efficiency at 50 % of rated output : | input data | % | input data | %
78 |  | Power factor at rated output : | input data |  | input data
79 |  | Power factor at 75 % rated output : | input data |  | input data
80 |  | Power factor at 50 % rated output : | input data |  | input data
81 |  | Surface protection
82 | 11.4.2.3.4,11.4.2.4.1,11.4.2.4.2,Table 27 | Surface protection corrosivity category : | C3 |  | C3 | [5 empty] | select | C3 | C4 | C5 | CX
83 | 11.4.2.3.4,11.4.2.4.3,Table 27 | Surface protection durability category : | medium (M) 7 to 15 years |  | medium (M) 7 to 15 years | [5 empty] | select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
84 |  | Paint colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
85 |  | Bearings (general)
86 |  | Bearing type : | select |  | select | [5 empty] | select | sleeve bearings | tilted pad bearings
87 | 9.1 | Lubrication specification : | input data |  | input data
88 |  | Lubrication system : | select |  | select | [5 empty] | select | manufacturer's standard | self-lubrication | flooded lubrication provided by others | flooded independent lubrication | flooded common lubrication system with driven equipment
89 | 11.4.9.2.13 | Low-speed barring : | not required |  | not required | [5 empty] | select | required | not required
90 |  | Vibration
91 | 11.4.5.3 | Applicable rotor balancing grade : | G2,5 |  | G2,5 | [5 empty] | select | G2,5 | G1,0 | G0,665 | manufacturer's standard
92 | 9.1,11.4.5.4,11.4.5.6 | Bearing housing vibration limits : | select |  | select | [5 empty] | select | grade A - IEC 60034-14:2018 Table 1 | grade B - IEC 60034-14:2018 Table 1 | other | not applicable
93 | 9.1,11.4.5.4,11.4.5.6 | Maximum shaft vibration limit : | select |  | select | [5 empty] | select | grade A - IEC 60034-14:2018 Table 2 | grade B - IEC 60034-14:2018 Table 2 | other | not applicable
94 | 9.1,11.4.5.4,11.4.5.6 | Maximum shaft runout limit : | select |  | select | [5 empty] | select | grade A - IEC 60034-14:2018 Table 2 | grade B - IEC 60034-14:2018 Table 2 | other | not applicable
95 |  | Maximum allowable vibration limit on generator shaft vibration (Sp-p) at rated output : | input data | µm | input data | µm
96 | 11.4.10 | Lateral vibration analysis : | not required |  | not required | [5 empty] | select | required for standalone generator | required for standalone generator and data/model for driving equipment supplier | not required
97 | 11.4.11 | Torsional vibration analysis : | not required |  | not required | [5 empty] | select | required data/model input for driving equipment supplier | not required
98 | 11.4.9.2.7 | Proximity probes for vibration measurement : | select |  | select | [5 empty] | select | two non-contacting proximity probes per sleeve bearing | two non-contacting proximity probes per sleeve bearing and one phase reference transducer | not required
99 |  | Noise
100 | 11.3.5.2,11.3.5.3 | Sound pressure level at no load : | input data | dB(A) | input data | dB(A)
101 |  | Excitation data
102 |  | Excitation system scope : | by manufacturer |  | by manufacturer | [5 empty] | select | by manufacturer | by purchaser
103 |  | Exciter power : | select |  | select | [5 empty] | select | external power supply | permanent magnet generator (PMG)
104 |  | Control and protection
105 |  | Control panel location : | indoor |  | indoor | [5 empty] | select | indoor | outdoor
106 | 11.4.18.2 | Control panel ingress protection : | select |  | select | [5 empty] | select | IP 21 | IP 31 | IP 44 | IP 55 | IP 56 | Other
107 |  | Cable entry location : | select |  | select | [5 empty] | select | bottom | top | bottom and top
108 |  | Cable entry type : | select |  | select | [5 empty] | select | removable-undrilled plate | multi-cable transit (MCT)
109 |  | Control panel anti-condensation heater : | select |  | select | [5 empty] | select | required | not required
110 | 11.4.13.3.1,11.4.17.4.3,11.4.17.4.5 | Communication protocol for interface with electrical control system : | select |  | select | [5 empty] | select | Modbus TCP/IP | Modbus RTU | Profinet | Profibus | Ethernet | other | not applicable
111 |  | Generator metering, control and protection system scope : | by manufacturer |  | by manufacturer | [5 empty] | select | by manufacturer | by purchaser
112 |  | Generator protection scheme : | select |  | select | [5 empty] | select | purchaser input document | manufacturer's standard | N/A
113 |  | Anti-condensation heaters
114 | 11.4.14.1 | Anti-condensation heater : | windings |  | windings | [5 empty] | select | windings | windings and line conductor terminal box | not required
115 | 11.4.14.1 | Anti-condensation heater supply voltage (AC) : | select | V | select | V |  |  |  |  | select | 100-120 single phase | 200-240 single phase | 380-440 three phase
116 |  | Warning label language : | select |  | select | [5 empty] | select | English | other
117 |  | Terminal boxes (general)
118 | Table 25 | Degree of ingress protection of all terminal boxes : | IP55 |  | IP55 | [5 empty] | select | IP55 | IP56 | other
119 |  | Line conductor terminal box
120 |  | Line conductor terminal box type : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | air insulated | phase insulated with heat shrink insulation | phase insulated with separable connectors | phase separated | phase segregated | other
121 |  | Line conductor terminal box location viewed from driven end : | select |  | select | [5 empty] | select | right | left | top
122 |  | Line conductor terminal box cable entry location : | bottom |  | bottom | [5 empty] | select | bottom | side
123 | 11.4.7.5 | Line conductor size : | input data | mm² | input data | mm²
124 |  | Line conductor cable type : | input data |  | input data
125 |  | Line conductor cable quantity per phase : | input data |  | input data
126 |  | Line conductor terminal box cable gland plate type : | select |  | select | [5 empty] | select | drilled gland-plate | undrilled gland-plate | other
127 |  | Connection point for portable earth : | not required |  | not required | [5 empty] | select | manufacturer's standard | 20 mm ball connection | 25 mm ball connection | not required
128 |  | Generator surge protection : | not required |  | not required | [5 empty] | select | required | not required
129 |  | Differential protection
130 |  | Current transformers for differential protection : | select |  | select | [5 empty] | select | full differential | self-balancing | not required
131 |  | Current transformer ratio : | input data |  | input data
132 |  | Current transformer accuracy class : | input data |  | input data
133 |  | Current transformer quantity : | input data |  | input data
134 |  | Online monitoring
135 |  | Rotor field earth fault circuit detection : | select |  | select | [5 empty] | select | required | not required
136 |  | Monitoring of insulation resistance : | select |  | select | [5 empty] | select | required | not required
137 | 11.4.12.5.2,11.4.12.5.3 | On-line winding partial discharge measurement : | not required |  | not required | [5 empty] | select | required | not required
138 | 11.4.12.5.2,11.4.12.5.3 | Partial discharge (PD) sensors : | select |  | select | [5 empty] | select | capacitive coupler | HFCT | Rogowski coils | other | not required
139 |  | Neutral connection
140 | 11.4.4.6,11.4.7.6 | Neutral connection : | select |  | select | [5 empty] | select | inside generator frame | inside neutral terminal box | inside line conductor terminal box | manufacturer's standard
141 |  | Water-cooled heat exchanger
142 | 11.4.3.3.6 | Cooling water type : | select |  | select | [5 empty] | select | site cooling water | sea water | brackish water | other | not applicable
143 | 11.4.3.3.6 | Maximum cooling water inlet temperature : | input data | °C | input data | °C
144 |  | Cooling water inlet supply maximum design pressure : | input data | select | input data | select |  |  |  |  | select | psi g | bar g
145 |  | Miscellaneous
146 |  | Provision for IoT hardware installation : | select |  | select | [5 empty] | select | required | not required
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the equipment.
Note on C7: Select the CAS level to be applied in IOGP S-745Q, Annex A. CAS D requires the fewest quality interventions and information requirements. Default value : D
Note on C8: Specify the country in which the project is located, in accordance with ISO 3166-1.
Note on C9: Specify the geographic location, within the country, which will determine the applicability of local regulatory requirements.
Note on C10: Select the location of the facility where the equipment will be permanently installed.
Note on C11: Select the status of the order.
Note on C12: Specify the generator manufacturer name.
Note on C13: Specify the generator model number.
Note on C14: Select the required number of poles. If "other" is selected, specify the pole requirements in "Additional notes".
Note on C15: Specify the generator frame size/designation. Where this is not specified by the purchaser, supplier to confirm the frame size as per the standard offering for the application.
Note on C17: Select the location where the generator is to be situated. If "other" is selected, specify in "Additional notes".
Note on C18: This is the altitude above sea-level. The IEC 60034-1 default is 1 000 m. Select "other" and specify the value in "Additional notes" only if the site altitude is higher than 1 000 m. Default value : 1 000 or below
Note on C19: The IEC 60034-1 default is 40 °C. Select a value different from 40 °C only if the site conditions are higher than the IEC default. "If other" is selected, specify the temperature values in "Additional notes". Default value : 40
Note on C20: Select "other" and specify the value in "Additional notes" only if the site conditions are lower than 0 °C. Default value : 0
Note on C21: Select the storage conditions of the generator. This may result in the requirement of additional preservation provision at the supplier's discretion.
Note on C22: Where floating or marine location is specified, specify maximum rotation about fore-and-aft axis (rolling) of vessel under dynamic conditions defined in IEC 60092-101 and IEC 61892-5 (e.g. ± 22 ° 30 '). Specify "not applicable" if not applicable.
Note on C23: Where a floating or marine location is specified, specify the max rotation about athwartship axis (pitching) of the vessel under the dynamic conditions defined in IEC 60092-101 and IEC 61892-5 (e.g. ± 7 ° 30 '). Specify "not applicable" if not applicable.
Note on C24: Specify the chemicals and corrosives that may be present in the location environment.
Note on C25: Select "yes" for unusual service conditions not covered elsewhere in IOGP S-745 such as salt-laden and abrasive dust. Specify unusual service conditions in "Additional notes". Default value : no
Note on C27: Specify the system rated voltage, expressed in kV, to which the generator will be connected.
Note on C28: Select the maximum steady-state voltage limit as a percentage of the supply voltage. Figure 11, zone B upper Y boundary default is 1.10 pu (10 %). If "other" is selected, specify the limit requirements in "Additional notes".
Note on C29: Select the minimum steady-state voltage limit as a percentage of the supply voltage. Figure 11, zone B lower Y boundary default is 0.90 pu (-10 %). If "other" is selected, specify the limit requirements in "Additional notes".
Note on C30: Select the supply frequency of the power system.
Note on C31: Select the maximum frequency limit as a percentage of the supply frequency to which the generator feeds. If "other" is selected, specify the limit requirements in "Additional notes".
Note on C32: Select the minimum frequency limit as a percentage of the supply frequency to which the generator will feed. If "other" is selected, specify the limit requirements in "Additional notes".
Note on C33: Specify the 3-phase short-circuit MVA rating value as calculated by purchaser on the connecting generator bus.
Note on C34: Specify the value of maximum earth fault current of the power system.
Note on C35: Select the method of neutral earthing of the power system to which the generator is connected. For a different arrangement, select "other" and specify in "Additional notes".
Note on C36: Select the mode of operation of generator.
Note on C37: Specify the generator power output expressed in kVA at the rated power factor. Supplier to specify the maximum generator power output if different from the purchaser's specified value.
Note on C39: Select which certification is acceptable for the generator to be located in a hazardous area. If "other" is selected, specify the certification in "Additional notes".
Note on C40: Select the temperature class for which the generator is rated for in accordance with IEC 60079-0. Default value : T3
Note on C41: Select the gas/dust group for which the generator is to be rated in accordance with IEC 60079.
Note on C42: Select the equipment protection level (EPL) for which the generator is rated in accordance with IEC 60079-14.
Note on C43: Select the type of protection for which the generator is rated in accordance with IEC 60079.
Note on C45: Specify the moment of inertia (MR²) of the driver, gearbox (if installed) and half coupling as seen towards the generator shaft at the rated generator speed.
Note on C46: Select the type of connection of the generator with the prime mover. Specify the gear ratio in "Additional notes" column, when gearbox is installed. Include the gearbox data sheet when provided.
Note on C47: Select the coupling hub type that the generator shaft is designed to accept. If "other" is selected, specify the coupling hub fit in "Additional notes".
Note on C48: Select the coupling hub fit that the generator shaft is designed to accept. If "other" is selected, specify the coupling hub fit in "Additional notes".
Note on C50: Specify the rated power factor for synchronous generator with lagging and leading power factor requirement.
Note on C51: Select the ingress protection value in accordance with IEC 60034-5. If "other" is specified, specify the enclosure ingress protection in "Additional notes". Default value : IP44
Note on C52: Select the direction of generator shaft rotation observed when facing the drive end when connecting generator terminals U-V-W.
Note on C53: Select the generator cooling method in accordance with IEC 60034-6. If "other is selected, specify the cooling method in "Additional notes".
Note on C54: Select the heat exchanger tube construction. For water-cooled exchangers, purchaser to provide the cooling water chemistry for tube material compatibility. Specify the tube material details (e.g. 90-10 Cu-Ni, 316L stainless steel) in “Additional notes”.
Note on C55: Specify the synchronous rotor speed while delivering the rated output at the rated voltage and rated frequency.
Note on C56: Specify the generator rated current when generating the rated voltage at the rated frequency.
Note on C57: Select the type of rotor construction adopted in the generator.
Note on C58: Specify the fully assembled weight of the generator.
Note on C59: Value of direct axis transient reactance (X'd) (Saturated) in 'per unit' (pu) values for the generator base kVA at rated voltage and ambient temperature provided by the purchaser is minimum
Note on C60: Value of direct axis transient reactance (X'd) (Saturated) in 'per unit' (pu) values for the generator base kVA at rated voltage and ambient temperature provided by the purchaser is maximum
Note on C61: Specify the preliminary value of direct axis subtransient reactance (X''d) (Unsaturated) in 'per unit' (pu) values for the generator base kVA at rated voltage and ambient temperature.
Note on C62: Specify the preliminary value of direct axis transient reactance (X'd) (Unsaturated) in 'per unit' (pu) values for the generator base kVA at rated voltage and ambient temperature.
Note on C63: Specify the preliminary value of negative sequence reactance (X2) in 'per unit' (pu) values for the generator base kVA at rated voltage and ambient temperature.
Note on C64: Specify the preliminary value of armature short-circuit time constant (Ta).
Note on C66: Specify the manufacturer of the automatic voltage regulator unit.
Note on C67: Specify the model of the automatic voltage regulator unit.
Note on C68: Select the applicable voltage regulation grade in accordance with BS 4999-140:1987, Table-1.
Note on C69: Select whether the automatic synchronizer feature is required.
Note on C71: Select the thermal class of the generator (stator and rotor) and exciter in accordance with IEC 60085. Default value : F
Note on C72: Select the temperature rise class of generator (stator and rotor) and exciter in accordance with IEC 60085. Default value : B
Note on C73: Select the method to be adopted for the measurement of the temperature rise of the windings. Default value : resistance method
Note on C75: Specify the efficiency of the generator while operating at rated output.
Note on C76: Specify the efficiency of the generator while operating at 75 % of rated output.
Note on C77: Specify the efficiency of the generator while operating at 50 % rated output.
Note on C78: Specify the cosine of the angle between active power and apparent power when the generator is operated at rated output.
Note on C79: Specify the cosine of the angle between active power and apparent power when the generator is operated at 75 % of rated output.
Note on C80: Specify the cosine of the angle between active power and apparent power when the generator is operated at 50 % of rated output.
Note on C82: Select the surface corrosivity category in accordance with ISO 12944-2, 5.1.1. Default value : C3
Note on C83: Select the surface durability category in accordance with ISO 12944-1, 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme. Default value : medium (M) 7 to 15 years
Note on C84: Where the manufacturer's standard paint colour is unacceptable and "other" is selected, specify the paint colour requirements in "Additional notes". Default value : manufacturer's standard
Note on C86: Select the bearing type.
Note on C87: Specify the approved lubrication specification and associated product reference code for bearing lubrication. This applies to bearing oil, depending on bearing type selection.
Note on C88: Select the lubrication system type. Manufacturer to specify the offered system when the purchaser selects as "manufacturer's standard". Specify the need for cross-contamination mitigation measures like dry gas seal systems in "Additional notes".
Note on C89: Select whether the lubrication system needs low-speed barring for the whole train. Default value : not required
Note on C91: Specify the required balancing grade to determine the permissible limits for residual unbalance to achieve the vibrations grade (maximum shaft vibration and run out limits). Default value : G2,5
Note on C92: Select the maximum bearing housing vibration limits in IEC 60034-14:2018, Table 1. If "other" is selected, specify the bearing housing vibration limits in "Additional notes".
Note on C93: Select the maximum shaft displacement vibration limits in accordance with IEC 60034-14:2018, Table 2. If "other" is selected, specify the shaft displacement vibration limits in "Additional notes".
Note on C94: Select the maximum shaft displacement runout limits in accordance with IEC 60034-14:2018, Table 2. If "other" is selected, specify the shaft displacement vibration limits in "Additional notes".
Note on C95: Specify maximum allowable vibration limit of shaft vibration (Sp-p) in µm at rated output. When generator cannot be loaded to rated output, rotor rated temperature test to be considered before measurement of vibrations.
Note on C96: When "required" is selected, the generator manufacturer will provide analysis and/or data/model required for the lateral vibration analysis to the unit supplier. When "not required" is selected, no action is expected from the generator manufacturer. Default value : not required
Note on C97: When "required" is selected, the generator manufacturer will be responsible for providing the data/model required for the torsional analysis to the unit supplier. When "not required" is selected, no action is expected from the generator manufacturer. Default value : not required
Note on C98: Select whether proximity probe(s) for vibration measurement are required to be installed by the manufacturer. Typically, a speed of 1 200 rpm and above is the threshold value of speed when the generator is provided with means for vibration measurement.
Note on C100: Specify the maximum permissible generator A-weighted sound pressure level at a reference distance of 1 m at no load.
Note on C102: Select the scope of supply of excitation system for the synchronous generator. Default value : by manufacturer
Note on C103: Select the power supply options required for the exciter. For external power supply, provide details in "Additional notes" column.
Note on C105: Select the location of the control panel to be installed at site. Default value : indoor
Note on C106: Select control panel ingress protection
Note on C107: Select the cable entry location based on the installation planned.
Note on C108: Select the type of cable entry considered for the enclosure (gland plate or multi-cable transit).
Note on C109: Select the requirement of anti-condensation heaters in control panel.
Note on C110: Select the communication protocol implemented in components having interface with electrical control system. If "other" is selected, specify in the "Additional notes".
Note on C111: Select the scope of supply of generator metering, control and protection system for the synchronous generator. Default value : by manufacturer
Note on C112: Select whether the generator protection scheme as per either purchaser's input document or manufacturer's standard.
Note on C114: Select the requirement of anti-condensation heaters in the generator. Default value : windings
Note on C115: Select the supply voltage for which the anti-condensation heater will be rated. Refer to the project specified voltage level applicable in the voltage range selected.
Note on C116: Select the language to be used for the label warning that heater terminals may be live when the generator is isolated. When the language is other than English, specify it in "Additional notes".
Note on C118: Select the ingress protection in accordance with IEC 60034-5 for which the terminal boxes are rated. Default value : IP55
Note on C120: Select the line conductor terminal box type to determine the terminal box design and construction principles. For a different termination type like copper busbars, select "other" and specify details in "Additional notes". Default value : manufacturer's standard
Note on C121: Select the line conductor terminal box location when viewed from the driven end of the generator, using coding in accordance with IEC 60034-7:2020.
Note on C122: Select the location from which the cable will enter the terminal box at site for the supplier to orient the terminals and terminal box accordingly. Default value : bottom
Note on C123: Specify the size (cross-section area) of the line conductor.
Note on C124: Specify the line conductor cable type (e.g. single-core, multi-core cable, armoured, un-armoured).
Note on C125: Specify the number of runs of cable per phase.
Note on C126: Select which cable gland plate entry system is required for the application. If "other" is selected, specify details in '"Additional notes".
Note on C127: Where a fully insulated termination system is not provided, select the required provision of connection point for attaching a portable earthing device on each phase and earth. Default value : not required
Note on C128: Select whether surge protection is required. Manufacturer to ensure that space in the terminal box is provided. Type (capacitor/ surge arrestor), capacitor rating and rated voltage of the surge protection device to be specified in "Additional notes". Default value : not required
Note on C130: Select the requirement for the pre-installed differential protection current transformers to be provided by the supplier.
Note on C131: Specify what differential protection current transformer ratio is required (e.g. "400/1 A). Specify "not applicable" where differential protection is not required.
Note on C132: Specify what differential protection current transformer accuracy class is required. Specify "not applicable" when differential protection is not required.
Note on C133: Specify the quantity of differential protection current transformer required. Specify "not applicable" when differential protection is not required.
Note on C135: Select whether rotor field earth fault circuit detection is required.
Note on C136: Select whether monitoring of insulation resistance is required.
Note on C137: Select whether on-line winding partial discharge measurement is required. Default value : not required
Note on C138: Select the type of partial discharge sensing element to be provided. If "capacitive coupler" is selected, specify the capacitance value in "Additional notes".
Note on C140: Select where a neutral terminal connection is to be made. This is typically decided as per the differential protection scheme and the connection arrangement will facilitate winding testing activities.
Note on C142: Select the type of cooling water. Provide site utility data for detailed specification of the cooling water available for the project. Where a heat exchanger is not provided, select "not applicable".
Note on C143: Specify the maximum cooling water inlet temperature as per project specification and site conditions.
Note on C144: Specify the cooling water inlet supply maximum design pressure as per project specification and site conditions.
Note on C146: Select the requirement of mounting provisions of IoT hardware provisions on the generator. Specify the mounting points and installation provisions in "Additional notes". IoT hardware may be procured and mounted by the purchaser at a later date.

## Testing
Row | IOGP S-745D (1.01) Procurement Data Sheet for High-voltage Synchronous Machines (IEC) Testing | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Routine test
4 | Table 16 | Routine test : | required |  | required | [5 empty] | select | required
5 |  | Performance test
6 | Table 16 | Performance test - Locked rotor current test : | select |  | select | [5 empty] | select | required | not required
7 | Table 16 | Performance test - Locked rotor torque test : | select |  | select | [5 empty] | select | required | not required
8 | Table 16 | Performance test - Temperature rise test : | select |  | select | [5 empty] | select | required | not required
9 | Table 16 | Performance test - Sleeve bearing inspection : | select |  | select | [5 empty] | select | required | not required
10 | Table 16 | Performance test - Determination of efficiency at 100 %, 75 % and 50 % load at rated power factor : | select |  | select | [5 empty] | select | required | not required
11 |  | Special test
12 | Table 16 | Special test - Rated rotor temperature vibration test (heat run test) : | select |  | select | [5 empty] | select | required | not required
13 | Table 16 | Special test - Measurements of shaft voltage at no-load : | select |  | select | [5 empty] | select | required | not required
14 | Table 16 | Special test - Bearing temperature rise at no-load : | select |  | select | [5 empty] | select | required | not required
15 | Table 16 | Special test - Tests for the construction of the no-load V curve : | select |  | select | [5 empty] | select | required | not required
16 | Table 16 | Special test - Noise level at no load : | select |  | select | [5 empty] | select | required | not required
17 | Table 16 | Special test - Measurement of moment of inertia : | select |  | select | [5 empty] | select | required | not required
18 | Table 16 | Special test - Measurement of torque and current as function of speed during starting : | select |  | select | [5 empty] | select | required | not required
19 | Table 16 | Special test - Dielectric dissipation test (tan δ) on stator windings : | select |  | select | [5 empty] | select | required | not required
20 | Table 16 | Special test - Partial discharge test on complete stator : | select |  | select | [5 empty] | select | required | not required
21 | Table 16 | Special test - Stator External Discharge test : | select |  | select | [5 empty] | select | required | not required
22 | Table 16 | Special test - Sealed winding conformance test : | select |  | select | [5 empty] | select | required | not required
23 | Table 16 | Special test - Unbalanced response test : | select |  | select | [5 empty] | select | required | not required
24 | Table 16 | Special test - Bearing housing natural frequency test : | select |  | select | [5 empty] | select | required | not required
25 | Table 16 | Special test - Stator core test : | select |  | select | [5 empty] | select | required | not required
26 | Table 16 | Special test - Surge comparison test on complete stator assembly : | select |  | select | [5 empty] | select | required | not required
27 | Table 16 | Special test - Sample coil test : | select |  | select | [5 empty] | select | required | not required
28 | Table 16 | Special test - Sudden short-circuit test : | select |  | select | [5 empty] | select | required | not required
29 | Table 16 | Special test - Heat exchanger performance verification test : | select |  | select | [5 empty] | select | required | not required
30 | Table 16 | Special test - Hydrostatic pressure test of heat exchanger tubing devices : | select |  | select | [5 empty] | select | required | not required
31 | Table 16 | Special test - Generator control panel functional test : | select |  | select | [5 empty] | select | required | not required
32 | Table 16 | Special test - Generator waveform analysis test : | select |  | select | [5 empty] | select | required | not required
33 | Table 16 | Special test - Rotor impedance test at rated frequency for the machine (stator frequency) : | select |  | select | [5 empty] | select | required | not required
34 | Table 16 | Special test - Test for determination of unsaturated Negative Sequence Reactance (X2) : | select |  | select | [5 empty] | select | required | not required
35 | Table 16 | Special test - Test for determination of unsaturated Zero Sequence Reactance (X0) : | select |  | select | [5 empty] | select | required | not required
36 | Table 16 | Special test - Test for determination of Direct-Axis Open Circuit Time Constant (T'do) : | select |  | select | [5 empty] | select | required | not required
37 | Table 16 | Special test - End Winding Impact Test : | select |  | select | [5 empty] | select | required | not required
38 | Table 16 | Special test - Overspeed test : | select |  | select | [5 empty] | select | required | not required
Note on C4: The routine tests (excluding "Performance tests") listed in Table 16 are mandatory as per procedure and acceptance criteria in the reference standard mentioned against respective test in Table 16. Default value : required
Note on C6: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C7: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C8: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C9: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C10: Select whether the test is required or not. The test procedure and acceptance criteria will be as per reference standard in Table 16 or as mutually agreed between purchaser and supplier.
Note on C12: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C13: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C14: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C15: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C16: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C17: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C18: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C19: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C20: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C21: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C22: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C23: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C24: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C25: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C26: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C27: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C28: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C29: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C30: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C31: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C32: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C33: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C34: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C35: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C36: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C37: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.
Note on C38: Select whether the test is required. The test procedure and acceptance criteria are as per the reference standard in Table 16 or as mutually agreed between the purchaser and the supplier.

## Supplement
Row |  | IOGP S-745D (1.01) Procurement Data Sheet for High-voltage Synchronous Machines (IEC) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-745D (1.01) Procurement Data Sheet for
High-voltage Synchronous Machines (IEC)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-745 Supplementary Specification to IEC 60034-1 for High-voltage Synchronous Machines.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data