## Addendum 1
Date of issue:
April 2026
Affected publication:
IOGP S-745L, Information Requirements for High-voltage Synchronous Machines (IEC), First Edition, April 2024
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in April 2024.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Worksheet | IR ID | Column | Update
| Definitions | IR-04 | F - CFIHOS Code | CFIHOS code CFIHOS-70000451 added
| Definitions | IR-09 | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000260
| Definitions | IR-33 | C - Description | Description amended
| Definitions | IR-25 | C - Description | Description amended
|  |  | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000438
| Definitions | IR-28 | F - CFIHOS Code | CFIHOS code CFIHOS-70000445 added
| Definitions | IR-47 | C - Description | Description amended
|  |  | F - CFIHOS Code | CFIHOS code CFIHOS-70000449 added
| Definitions | IR-46 | F - CFIHOS Code | CFIHOS code CFIHOS-70000449 added
| Definitions | IR-45 | C - Description | Description amended
|  |  | F - CFIHOS Code | CFIHOS code CFIHOS-70000449 added
| Definitions | IR-49 | F - CFIHOS Code | CFIHOS code CFIHOS-700004203 added
| Definitions | IR-32 | F - CFIHOS Code | CFIHOS code CFIHOS-70000444 added
| Definitions | IR-35 | C - Description | Description amended
| Definitions | IR-36 | C - Description | Description amended
| Definitions | IR-37 | C - Description | Description amended
| Definitions | IR-51 | F - CFIHOS Code | CFIHOS code CFIHOS-70000245 added
| Requirements | IR-24 | C - Condition Invoking Requirement | Condition invoking requirement amended
| Definitions |  | C - Description | Description amended
| Definitions | IR-52 | C - Description | Description amended
|  |  | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000083
| Requirements Definitions | IR-54 | All | New information requirement
| Requirements Definitions | IR-55 | All | New information requirement
| Requirements Definitions | IR-57 | All | New information requirement
| Requirements Definitions | IR-58 | All | New information requirement
List of updates (continued)
| Worksheet | IR ID | Column | Update
| Requirements Definitions | IR-59 | All | New information requirement
| Requirements Definitions | IR-62 | All | New information requirement
| Requirements Definitions | IR-65 | All | New information requirement
| Requirements Definitions | IR-67 | All | New information requirement
| Requirements Definitions | IR-68 | All | New information requirement
| Definitions | Various | D - Reference | List of references updated

## Front & Preliminaries
[5 empty] | SPECIFICATION | April 2026
[5 empty] | IOGP S-745L | Version 1.01
ADDENDUM 1 TO FIRST EDITION (APRIL 2024)
Information Requirements for
High-voltage Synchronous Machines
(IEC)
Revision history
| VERSION | DATE | PURPOSE
| 1.01 | April 2026 | Addendum 1
| 1 | April 2024 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-745L (1.01) Information Requirements for
High-voltage Synchronous Machines (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-745L (1.01) Information Requirements for
High-voltage Synchronous Machines (IEC)
Introduction
The purpose of this information requirements specification (IRS) is to define information requirements for the procurement of high-voltage synchronous machines in accordance with IOGP S-745 for application in the petroleum and natural gas industries. The IRS defines the information requirements, including format, timing and purpose, for information to be provided by the supplier. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the specification (IOGP S-745), procurement data sheet (IOGP S-745D) and quality requirements specification (IOGP S-745Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification (IRS)

## Instructions
IOGP S-745L (1.01) Information Requirements for
High-voltage Synchronous Machines (IEC)
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS Structure Contents
| 1 | 'Front & Preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes / No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information Submission Abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS .
Column K — 'Translation Required' (Yes / No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable Formats
Column F — 'CFIHOS Document Type Code' relates to the CFIHOS document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3 below. Metadata listed below are as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The document master to which this revision is related |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification |  |  | The Export Control Rule that is applicable for the document revision (e.g., ECCN, EAR). |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
| Security classification |  |  | Indicates internal Owner-Operator access restriction applicable for the document |  |  | TBA
Table 3 — Supplier Deliverable Metadata

## Requirements
IOGP S-745L (1.01) Information Requirements for High-voltage Synchronous Machines (IEC)
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Document Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S745-IR-1 | Supplier master information schedule |  | Information deliverables list | No | For Acceptance |  | - | - |  | -
S745-IR-2 | Delivery schedule |  | Delivery/Production schedule | Yes | For Information |  | - | - |  | -
S745-IR-3 | Progress report |  | Progress report | No | For Information |  | - | - |  | -
S745-IR-4 | Quality plan | Required for CAS A | Quality plan | - | - |  | - | - |  | -
S745-IR-6 | Inspection and test plan for complete package |  | Inspection and test plan (ITP) | No | For Acceptance |  | - | - |  | -
S745-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | - | - |  | -
S745-IR-8 | Non-conformance records |  | Non-conformance records | No | For Acceptance |  | - | - |  | -
S745-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | - | - |  | -
Technical Information Requirements
S745-IR-33 | Equipment data sheet |  | Manufacturer data sheet | No | For Acceptance |  | - | - |  | -
S745-IR-26 | General arrangement drawing |  | General arrangement diagram | Yes | For Acceptance |  | - | - |  | -
S745-IR-25 | Equipment detailed drawing |  | Detailed drawing | No | For Acceptance |  | - | - |  | -
S745-IR-28 | Name plate drawing |  | Name plate drawing | No | For Acceptance |  | - | - |  | -
S745-IR-27 | Foundation loading diagram |  | Foundation loading diagram | Yes | For Acceptance |  | - | - |  | -
S745-IR-47 | Single-speed motor performance curves |  | Motor performance and electrical data and curves | No | For Acceptance |  | - | - |  | -
S745-IR-46 | Converter duty motor performance curves | Where purchaser confirms the motor is converter duty | Motor performance and electrical data and curves | No | For Acceptance |  | - | - |  | -
S745-IR-45 | Generator performance and capability curves |  | Curves and tables calculations | No | For Acceptance |  | - | - |  | -
S745-IR-29 | Termination diagram |  | Termination diagram | No | For Acceptance |  | - | - |  | -
S745-IR-30 | Wiring diagram |  | Wiring diagram | No | For Acceptance |  | - | - |  | -
S745-IR-48 | Inter-connection diagram |  | Connection diagram | No | For Acceptance |  | - | - |  | -
S745-IR-49 | Utilities schedule |  | Utility consumption report | Yes | For Information |  | - | - |  | -
S745-IR-31 | Bill of materials |  | Bill of materials | No | For Information |  | - | - |  | -
S745-IR-32 | Lubrication data |  | Lubrication list | No | For Information |  | - | - |  | -
S745-IR-34 | Consolidated spare parts list |  | Consolidated spare parts list | No | For Information |  | - | - |  | - | Information for installation, operation and maintenance
S745-IR-35 | Installation manual |  | Installation manual | No | For Information |  | - | - |  | - | Installation Manual index, if required, should be provided in first revision of the document. When index agreed, Installation manual content shall be provided in subsequent revision of the document.
S745-IR-36 | Maintenance manual |  | Maintenance manual | No | For Information |  | - | - |  | - | Maintenance Manual index, if required, should be provided in first revision of the document. When index agreed, Maintenance manual content shall be provided in subsequent revision of the document.
S745-IR-37 | Operating manual |  | Operating manual | No | For Information |  | - | - |  | - | Operating Manual index, if required, should be provided in first revision of the document. When index agreed, Operating manual content shall be provided in subsequent revision of the document.
S745-IR-38 | Factory acceptance test (FAT) protocol |  | Factory acceptance test (FAT) procedure | Yes | For Acceptance |  | - | - |  | -
S745-IR-41 | Factory acceptance test (FAT) records |  | Factory acceptance test (FAT) records | No | For Acceptance |  | - | - |  | -
S745-IR-51 | Type test certificate |  | Type test report | No | For Information |  | - | - |  | -
S745-IR-24 | Hazardous area certificate (type) | Machine rated for use in hazardous area | Hazardous area certificate | No | For Information |  | - | - |  | -
S745-IR-50 | Weight certificate | As per project requirement | Weight certificate | No | For Information |  | - | - |  | -
S745-IR-22 | Declaration of conformity |  | Declaration of conformity | No | For Information |  | - | - |  | -
S745-IR-42 | Manufacturer record book (MRB) |  | Manufacturer record book (MRB) | No | For Information |  | - | - |  | - | Manufacturer Record Book index, if required, shall be provided in first revision of the document. When index agreed, Manufacturer Record Book content shall be provided in subsequent revision of the document.
S745-IR-52 | Input data for lateral and torsional analysis | Selection of lateral and/or torsional analysis 'required' on data sheet | Interface document | No | For Acceptance |  | - | - |  | -
S745-IR-54 | Painting and Coating Procedure |  | Painting and coating procedure | No | For Acceptance |  | - | - |  | -
S745-IR-55 | Painting and coating inspection records |  | Painting and coating inspection records | No | For Acceptance |  | - | - |  | -
S745-IR-57 | Functional Description | Where generator control panel is supplied | Functional Description for Generator Control Panel | No | For Acceptance |  | - | - |  | -
S745-IR-58 | Synchronous machine model for dynamical analysis | Where generator is supplied and where purchaser confirms the motor is single speed motor | Block diagram | No | For Information |  | - | - |  | -
S745-IR-59 | Lateral analysis report | Where purchaser confirms for standalone machine lateral analysis is 'required' on datasheet | Lateral analysis | No | For Acceptance |  | - | - |  | -
S745-IR-62 | Special tools list |  | Special tools list | No | For Information |  | - | - |  | -
S745-IR-65 | Parameter setting tables | Where generator control panels are supplied | Parameter setting tables | No | For Acceptance |  | - | - |  | -
S745-IR-67 | 3D CAD model | Where purchaser confirms it is required in scope of supply | Database and data set (models) | No | For Acceptance |  | - | - |  | -
S745-IR-68 | Stator and rotor thermal analysis | Where purchaser confirms the motor is converter duty | Thermal calculations | No | For Acceptance |  | - | - |  | -
Purchase Order Specific Information Requirements

## Definitions
IOGP S-745L (1.01) Information Requirements for High-voltage Synchronous Machines (IEC)
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Document Type Code — CFIHOS document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Deliverables
S745-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S745-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by [vendor/sub-vendors]. Schedule details typically** include; a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (calendar dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [vendor's] standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S745-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S745-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] |  | PDF | CFIHOS-70000451
S745-IR-6 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. The non-destructive test describing which NDT test (i.e. MT, PT, RT, UT, VT or ET) to be performed for a given object, including acceptance criteria and reporting document will be a part of the Quality Assurance Plan, where applicable. |  | PDF | CFIHOS-70000180
S745-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container(s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. | 6.6 | PDF | CFIHOS-70000154
S745-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S745-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000260
Technical Information Requirements
S745-IR-33 | Equipment data sheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data containing part number/model, design information, operational data and limitations of the equipment. The equipment data sheet shall include all relevant design data and information required for power system study, including but not limited to, - machine data (basic design, area classification, enclosure, mounting, bearing, heaters and auxiliaries, monitoring sensors & detectors, terminals and terminal boxes, etc.) - performance data (starting, operating, etc.) - Excitation system data (Exciter data, excitation controls, metering, AVR, synchronisation, protection, communications, etc.) - Prime mover and generator data, generator controls (for generator only) - reactance (Direct and quadrature axis, transient/sub-transient, saturated/unsaturated, synchronous, armature) - reactance and resistance (zero sequence, negative sequence) - time constant (Direct and quadrature axis, transient/sub-transient, open-circuit, short-circuit) - Short circuit ratio - Field resistance - Field leakage reactance - Potier resistance - Stator Armature resistance/phase - Armature leakage reactance - Synchronization: maximum permissible deviations of the amplitudes, frequency and phase of the generator or compensator voltages with respect to the grid voltages | 11.4.13.1.1, 5.9, 11.3.1.1, 11.3.1.5, 11.4.15.2, 11.4.17.1.2, 11.4.2.3.4, 11.4.3.1.1, 11.4.4.11, 11.4.9.1.1, 6.1, 6.8, 7.4, 8.6.1, Table 24, Table 25, Table 27, Table 28 | PDF | CFIHOS-70000416
S745-IR-26 | General arrangement drawing | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment, and components. The drawing shall contain reference to main specifications and standards. The drawing shall include cross sectional views if a separate document for detailed drawing is not furnished. For synchronous machines, the drawing shall contain the following minimum information- - Dimensions – overall, maintenance clearances. - Weights – overall, erection, largest maintenance weight for each item. - Drawings – dimensional outline, cross sections, details of parts. - Heat exchanger detailed specifications (pressure, temperature, cooling medium details, cooling tube arrangement and materials, etc.) - Schematics diagrams identifying mounted components by make, type, size, rating, materials, other data as applicable. - Lifting provisions and rigging arrangement for removal of parts. - Location, orientation, and dimensions of all terminal boxes. - Interface connections (including earthing points, piping connections where applicable). - Centre of gravity. - Installation and mounting details. - Location of machine accessories (Lube oil skid, oil reservoir, rundown tank, etc.). | 10.4.6, 11.1, 11.4.12.4.1.1, 11.4.12.1.1, 11.4.12.3.1, 11.4.12.4.2.1, 11.4.12.4.2.2, 11.4.12.5.1, 11.4.12.5.2, 11.4.14.2, 11.4.17.3.1, 11.4.17.3.4, 11.4.17.4.4, 11.4.18.1, 11.4.18.12, 11.4.18.13, 11.4.18.14, 11.4.18.15, 11.4.18.4, 11.4.2.1.1, 11.4.2.1.2, 11.4.2.2.1, 11.4.2.3.1, 11.4.2.3.3, 11.4.2.3.5, 11.4.3.2.1, 11.4.3.2.2, 11.4.3.2.3, 11.4.3.3.1, 11.4.3.3.2, 11.4.3.3.3, 11.4.3.3.4, 11.4.4.5, 11.4.4.6, 11.4.7.1, 11.4.7.10, 11.4.7.2, 11.4.7.3, 11.4.7.6, 11.4.7.7, 11.4.7.8, 11.4.7.9, 11.4.8.1, 11.4.8.2, 11.4.8.3, 11.4.9.1.3, 11.4.9.2.11, 11.4.9.2.12, 11.4.9.2.13, 11.4.9.2.5, 11.4.9.2.6, 11.4.9.2.7, 11.4.9.2.9, 6.8, Table 25 | PDF | CFIHOS-70000153
S745-IR-25 | Equipment detailed drawing | Drawing showing parts of a construction or a component, generally enlarged, and including specific information about the form and construction or about the assembly and joints Also supports other documents where a cross-sectional view or part list is necessary for clarity. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. (Source: ISO 10209). Detail drawing to provide details of external and internal components of the machine, e.g. rotor detailed drawing. Method of assembly showing how sub-components are constructed including fixings and gaskets. All components to be labelled using terminology consistent to that found in other drawings and documentation by the manufacturer. Detail drawings will be elaborate and include details not found on general arrangement drawing. To include rotor detail drawing including shaft end details, heat exchanger drawing (where applicable), terminal box detail drawing (line and neutral)​. To include installation and mounting details of measurement and safety probes/sensors. To include the bearings and exciter details. For machines with sleeve bearings, the drawing shall show the rotor permanently marked to be visible in operation and standstill position with the magnetic centre and limits of permissible shaft axial movement. NOTE Manufacturer may choose to merge the contents of this document with general arrangement drawing, which is acceptable. | 11.4.18.13, 11.4.18.14, 11.4.4.11, 11.4.5.17, 11.4.7.1, 11.4.7.11, 11.4.7.12, 11.4.7.2, 11.4.7.3, 11.4.7.6, 11.4.7.7, 11.4.7.8, 11.4.8.1, 11.4.8.2, 11.4.8.4, 11.4.8.5, 11.4.9.2.11, 11.4.9.2.5, 11.4.9.2.6, 11.4.9.2.7, 11.4.9.2.9,11.4.2.2.3.11 | PDF | CFIHOS-70000438
S745-IR-28 | Name plate drawing | A drawing that depicts basic information of the machine in accordance with IEC 60034-1:2022, clause 10 and IOGP S-745. The drawings may be of multiple sheets with one sheet each for main machine, exciter, Permanent Magnet Generator (where applicable), lubrication system, labels & markings, etc. | 10.3, 10.4.2, 10.4.6, 9.1, 11.4.8.3, 11.4.9.1.3 | PDF | CFIHOS-70000445
S745-IR-27 | Foundation loading diagram | A diagram detailing static and dynamic forces or movements acting on foundations or other load bearing supports, anchor bolt details, lengths and pre-tensioning. May include Civil Structural for loads imposed, and Civil Foundations for foundation design. Document or drawing detailing foundation loads to permit adequate foundation design by the purchaser. This shall include the following items: - the size and location of foundation bolts; - the weight distribution for each bolt and sub-soleplate location; - minimum foundation stiffness required to achieve specified vibration levels; - any unbalanced forces or moments generated by the machine in the specified operating range; - resultant forces and moments resolved at the centerline of the machine; - thermal displacements (where applicable); - the location of the center of gravity; and - foundation forces as a result of worst case transient conditions. | 11.3.4.1 | PDF | CFIHOS-70000151
S745-IR-47 | Single-speed motor performance curves | Curves to indicate torque and current against speed for 80% and 100% voltage conditions and at rated frequency, superimposed on driven equipment torque curve to confirm that there is adequate net torque for acceleration. Motor performance curves shall include the following information: - Torque curve at 80% rated voltage expressed as a percentage of rated torque. - Torque curve at rated voltage expressed as a percentage of rated torque. - Power factor curve at rated voltage. - Current curve at 80% rated voltage expressed as a percentage of rated current. - Current curve at rated voltage expressed as a percentage of rated current. - Torque curve of the load expressed as a percentage of rated torque. - Hot and cold thermal withstand time curves. - Thermal time constants including heating time constant, cooling time constant when machine is running, and cooling time constant when machine is stopped. - Number of starts per hour. | 11.3.1.6 | PDF | CFIHOS-70000449
S745-IR-46 | Converter duty motor performance curves | Performance data/curve to include the following - Data for continuous operating region of converter as per IEC 61800-2:2021, 5.3.3.2 and Figure 10. - rated torque (MN ) [N⋅m]; - rated speed (NN ) [r/min]; - maximum rated speed (NNMax) [r/min]; - minimum rated speed (NNMin) [r/min]; - minimum speed (NMin) [r/min]; - maximum rated safe speed (NSNMax) [r/min]; - rated output power (PsN) [kW]. Voltage/frequency characteristics as per IEC TS 60034-25:2022, Figure 3, indicating maximum converter output voltage, field-weakening frequency and maximum allowable frequency. Converter duty motor operating data as per below: - voltage (V) - current (A) - power factor (pu) - efficiency (%) - torque (Nm) - speed (min-1) - frequency (Hz) - for the following operating conditions: maximum torque at minimum rated speed (NNMin) maximum torque at rated speed (NN ) maximum torque at maximum rated speed (NNMax) | 11.3.1.6 | PDF | CFIHOS-70000449
S745-IR-45 | Generator performance and capability curves | Describe the main characteristic and limits of a product. Information to be used into system engineering Characteristics and functional parameters should be documented and performance shall be shown to be probable. This should include but not be limited to calculations, curves, tables, reference to similar applications and test data. This shall as a minimum be at a level customary for the equipment and to the extent such data are of importance for interfaces to plant and system. The document shall include the following curves as a minimum - - Open circuit characteristics (OCC) curve, - Short-circuit characteristics (SCC) curve, - Generator capability curve - Generator V curves. - Generator decrement curve for a 3 phase short circuit from full load - Variation of Efficiency with load - Variation of generator power output with coolant temperature - Generator Volt/Hertz (V/Hz) capability - Permissible duration of negative sequence current - Permitted duration of stator, field winding , and exciter current - Permitted voltage and frequency variation. - Exciter open circuit and loaded characteristic curve - Diode failure analysis (Supplier shall provide a circuit analysis from PSPICE or a similar simulation software. The output report shall show the steady state operation of the rotating exciter in normal configuration, steady state operation with a shorted diode, steady state operation with an open diode, and the transient analysis of the diode failing open or failing closed. In the report the supplier shall compare the voltage and current ratings of the rotating exciter components with the voltage and currents in the analyses, indicate their typical design margins and safety factors, and declare conformance.) | 11.4.17.2.1 | PDF | CFIHOS-70000449
S745-IR-29 | Termination diagram | A diagram which identifies all connections and cable terminations to facilitate installation, removal, maintenance and fault finding. To include - - Vendor interfaces; - Motor or generator terminations; - Instrument and auxiliary terminations; - Package interfaces (Control panels, relay panels, converters, switchboards, electrical network system, etc.) terminations. | 11.4.12.1.2, 11.4.12.1.3, 11.4.7.10 | PDF | CFIHOS-70000330
S745-IR-30 | Wiring diagram | Description: Schematic of electrical and instrument circuit connections based on the principles in IEC 61082-1, Preparation of documents used in electrotechnology – Part 1: Rules. The wiring to be shown to the extent necessary for the understanding of how the components are interconnected. The drawing includes details of all device hardwired connections within the functional unit and external interfaces to terminal blocks. Hardwired connections internal to the functional unit, devices and external interface terminal blocks are to be identified as per manufacturer's standard. Diagram providing information on the circuitry of control panels (excitation system, generator metering, control & protection system, etc.). Mandatory content of information: – Graphical symbols representing the objects; – Graphical symbols representing the connections among objects; – Reference designations; – Terminal designations; – Signal level conventions (applicable to logic signals). – Information necessary to trace paths and circuits (signal designations, location references) – Supplementary information necessary for the understanding of functions Optional content of information: – Technical data; – Reference to other documents; – Information about wiring performance; – Cable and cable core identification. (Source: IEC 61355-1, D00053) | 11.4.12.2.1, 11.4.13.3.1, 11.4.16.4, 11.4.17.3.1, 11.4.17.4.4, 11.4.18.11, 11.4.18.18 | PDF | CFIHOS-70000268
S745-IR-48 | Inter-connection diagram | Diagram providing information about the physical connections among components or units like machine components, lube oil skid, High Voltage / Low Voltage switchgear, control panels, electrical control system, machine monitoring system, etc. to facilitate design and execution activities at site. Mandatory content of information: - Conductor or cable type information (e.g. recognized type designation, catalogue or part number, material, construction, size, insulation, voltage rating, colour, number of conductors, other technical data); - Reference designation or conductor or cable number; - Identification or representation of the connected objects (e.g. Panel/equipment tag, terminal block and/or terminal designation); - Signal interface list including signal designation and/or technical data about the signal, interface data between control panels and electrical network monitoring system; - Mapping address of interface signals. Optional content of information: - Instruction for or methods of laying, routing, termination, attachment, twisting, screening, etc. - Length of connection - Special classification or information (Source: IEC 61355-1, D0057) | 11.4.16.4 | PDF | CFIHOS-70000055
S745-IR-49 | Utilities schedule | Document providing input to engineering for design of the customer's installation or utility arrangement. Document stating the normal and maximum consumption of e.g. compressed air, heating/cooling media etc., for the equipment(s) or unit(s). The utility schedule shall list the individual electrical consumers as per various voltage levels. A list of utilities derived externally, for which the motor is reliant under normal operation. To include details of electrical, pneumatic, hydraulic and other utilities with battery limit operating conditions and limits/tolerances to be provided at the machine location to facilitate operation. | 11.4.3.3.6 | PDF | CFIHOS-70000203
S745-IR-31 | Bill of materials | A list of parts, components and sub-assemblies for equipment with original equipment manufacturer part numbers, item numbers, quantities, material legends/designations and cross-references to associated drawing/diagram/document/specifications. A separate list should be provided for control panels and bought out items. Note When agreed includes details of sub-suppliers & associated purchase orders. | 11.4.13.3.1, 11.4.18.17 | PDF | CFIHOS-70000028
S745-IR-32 | Lubrication data | Schedule to indicate type and grade of lubricants and other consumables required for all supplied equipment. For each schedule entry the following is to be included as a minimum: Tag number, tag description / component (e.g. bearings, etc.), lubricant manufacturer, lubricant type and grade (product reference code and specification), first fill capacities, rate of consumption (litres/month) and the following details for sleeve bearings- - Oil change intervals - Inlet maximum oil temperature - Top-up procedure | 10.4.6 | PDF | CFIHOS-70000444
S745-IR-34 | Consolidated spare parts list | A document detailing commissioning and startup spare parts list and two-year operational spare parts list. This list shall also include the following as a minimum: - Part name - Recommended quantity - Supplier part number (where applicable) - Reference to 'Bill of materials' document |  | PDF | CFIHOS-70000420
S745-IR-35 | Installation manual | The manual shall provide information regarding normal and safe methods of handling, installing of synchronous machine and auxiliaries. Installation refers to the mounting, setting, erection, etc. Equipment lifting manual shall be included. If included in scope of supply, the equipment installation manual shall cover Exp control units, AVRs, Generator Control Panels, Synchronoscope and IEDs. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a standalone document. | 11.4.2.2.2, 11.4.2.3.3 | PDF | CFIHOS-70000181
S745-IR-36 | Maintenance manual | The manual shall provide information of manufacturer's recommended methods and practices for inspection and maintenance of synchronous machine and auxiliaries. This shall be complete with information for both hardware and software regarding predictive/preventive maintenance, fault detection/diagnosis and fault isolation/rectification and ensuring equipment reliability. The instructions shall include information concerning: - the nature and frequency of inspections; - safety precautions and warnings for maintenance carried out on running or live equipment; - information for fault diagnosis and identification; - instructions for repairs and adjustments; - description of built-in diagnostic systems to aid fault finding, when applicable; - information on need for and use of special tools and tackles, where applicable; - drawings and diagrams enabling maintenance personnel to carry out their task rationally (especially fault-finding tasks); - regular checking of warning devices; - description of all predictable tasks performed at specific intervals to be consolidated in the form of maintenance schedules and, if necessary, master schedules; - If included in scope of supply, the equipment maintenance manual shall cover Exp control units, AVRs, Generator Control Panels, Synchronoscope and IEDs. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a standalone document. | 11.4.1.1, 11.4.3.2.1, 11.4.3.3.2, 11.4.3.3.3, 11.4.8.1, 11.4.9.2.10, 11.4.9.2.2 | PDF | CFIHOS-70000206
S745-IR-37 | Operating manual | The manual shall provide information of methods and modes of operating synchronous machine and auxiliaries, including but not limited to instructions, procedures, drawings, tables, etc. for the operation (stop, start), parameter description list for programable units in Generator Control Panel, control and emergency shutdown. This shall be complete with information regarding operational limits, control functions, testing interlocks and safeties, possible interruptions, corrective actions, hazards and corrective measures to be taken. If included in scope of supply, the equipment operating manual shall cover Exp control units, AVRs, Generator Control Panels, Synchronoscope and IEDs. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a standalone document. | 11.4.9.2.10, 11.4.9.2.3 | PDF | CFIHOS-70000228
S745-IR-38 | Factory acceptance test (FAT) protocol | The FAT procedure will be used to reach a common understanding of the required testing and acceptance criteria. The FAT protocol shall detail all tests specified in S-745 Table 16 on the synchronous machine including the acceptance criteria. Test set-up and test equipment should also be defined. This protocol shall also include special tests as defined in S-745 Table 16, that are specified in the data sheet. | Table 16 | PDF | CFIHOS-70000427
S745-IR-41 | Factory acceptance test (FAT) records | The FAT report will be used to verify that the equipment has been tested according to FAT protocol. The FAT report will be used for acceptance of the equipment delivery. This document shall include all results from the activities performed in routine tests, type tests (if any) and special tests requested in data sheet, in accordance with IOGP S-745 Table 16, FAT protocol, applicable standards, specifications and requirements. Every test report/result in addition to the inspection/measurements/data/graphs/charts/prints, should be endorsed with the following information as a minimum - Date of testing; - Signature of person responsible for test; - Object identification (type, series number, etc.). - Statement of compliance, where applicable; - Test set-up and equipment / instruments used; - Reference to test procedure. - A list of punch items on the observations during the FAT that require corrective action (modification/replacement/repair) for acceptance may be included in this document. | 11.4.17.2.1, 11.3.1.5, 11.3.3.1, 11.3.4.1, 11.3.4.2, 11.3.5.2, 11.3.5.3, 11.4.17.4.5, 11.4.18.7, 11.4.2.3.6, 11.4.2.3.7, 11.4.2.3.8, 11.4.9.2.8, 9.1, Table 16 | PDF | CFIHOS-70000429
S745-IR-51 | Type test certificate | The certificate to confirm that the results of test performed to provide evidence that the design meets the requirements of the functional specification (See ISO 13880:1999). (When specified, type test shall be independently verified by a third part and supported by a Certificate of Conformance - CFIHOS-70000013). | 11.3.2.1, 11.4.17.2.1, 11.4.6.1, 13.1, 13.2.2, 13.3, 11.3.1.2, 11.3.1.4, 11.3.5.2, 11.3.5.3, 11.3.5.4, 11.4.16.1.2, 11.4.18.2, 11.4.3.3.5, 11.4.5.9, Table 26 | PDF | CFIHOS-70000245
S745-IR-24 | Hazardous area certificate (type) | Attestation issued by a recognised independent authority certifying that the machine and all its auxiliary components have satisfied the requirements for use in hazardous area. | 11.4.12.5.3, 11.4.16.1.2, 11.4.16.2 | PDF | CFIHOS-70000160
S745-IR-50 | Weight certificate | Certificate of gross weight of machine inclusive of all add-on items complete in all respect. Source ISO 19901-5. This document may contain weight of individual components like heat exchangers, terminal boxes, etc. for selection of appropriate material handling devices during assembly/dis-assembly activities. | 10.4.2, 11.4.2.3.2 | PDF | CFIHOS-70000358
S745-IR-22 | Declaration of conformity | Declaration that contains sufficient information to enable a recipient of the declaration of conformity to identify the issuer of the declaration, the object of the declaration, the standards and other specified requirements with which conformity is declared, and the person signing for and on behalf of the issuer of the declaration of conformity (first party). Declares conformance with all standards relating to the machine in its region of use and for application, as defined by the purchaser in the procurement specification. | 11.3.1.3, 11.4.1.1, 11.4.1.2, 11.4.1.3, 11.4.15.1, 11.4.18.17, 11.4.3.3.5, 11.4.5.1 | PDF | CFIHOS-70000431
S745-IR-42 | Manufacturer record book (MRB) | Detailed information/description for the documents to be included in MRB as agreed between Purchaser and Supplier. The document shall include, but not be limited to, the following - calculations and study reports, - documents recording compliance with statutory and/or local regulations, and inspection and testing results, - documents recording compliance with environmental requirements for installed components such as pressure relief diaphragm etc., - reports for all the testing carried out at supplier / sub-supplier shop, e.g. Rotor balancing report, Lateral vibration analysis report, Any other test report or measurement data that is not part of Factory acceptance test (FAT) records. - documents related to sub-supplier certificates, test reports and catalogues, - any other information about the machine, its associated system or components, etc. that would be required for installation, testing, commissioning, operation and maintenance. | 11.4.10, 11.4.11, 11.4.13.2.1, 11.4.13.2.2, 11.4.15.3, 11.4.17.3.4, 11.4.18.7, 11.4.3.2.3, 11.4.3.3.6, 11.4.4.2, 11.4.4.3, 11.4.5.1, 11.4.5.13, 11.4.5.14, 11.4.7.7, 11.4.9.2.1 | PDF | CFIHOS-70000178
S745-IR-52 | Input data for lateral and torsional analysis | This document provides input data for lateral and torsional critical speed analysis by driven equipment supplier. The maximum air gap torque shall be calculated for 2-phase and 3-phase short-circuit, 120º and 180º out of synch conditions as input to drive train torsional analysis. | 11.4.10 | PDF | CFIHOS-70000083
S745-IR-54 | Painting and Coating Procedure | Verification of suppliers compliance with surface protection and coating requirements. This document provides a procedure for coating operator to ensure repeatability and formalism and hence prove the quality of the coating work. This document details the work process and how the defined requirements to surface treatment, application and quality control shall be met. A procedure may cover wet paint, powder coating, or metallic coatings. The document shall include reference to applied standards and the information about revision of the applied standard. |  | PDF | CFIHOS-70000384
S745-IR-55 | Painting and coating inspection records | This document is used for verification of compliance with surface protection and coating requirements. Document containing records of performed surface protection and coating work. |  | PDF | CFIHOS-70000245
S745-IR-57 | Functional Description | The purpose of this document is for the Supplier to define all his requirements for safe and reliable control and monitoring function of his equipment. The functional description shall give engineering a description of how the functional requirement for the product is implemented. Note: It will describe the function and not the design and contain sufficient information for the use. | 11.4.17.4.1, 11.4.17.4.2, 11.4.17.4.3, 11.4.17.4.4, 11.4.17.4.5 | PDF | CFIHOS-70000244
S745-IR-58 | Synchronous machine model for dynamical analysis | A mathematical model of the synchronous machine as per one of the models in IEEE Std 1110 including a representative model of the excitation system as per one of the models in IEEE 421.5 (including AVR, PSS, limiters and superimposed regulators). |  | PDF | CFIHOS-70000237
S745-IR-59 | Lateral analysis report | Lateral analysis report of the complete coupled train, including but not limited to the following: Damped: Damped lateral analysis report of the complete coupled train, including but not limited to the following: a) Complete description of the method used. b) Identification of the frequency of each critical speed, regardless of AF, in the range from 0 % to 150 % of the maximum continuous speed. c) Frequency, phase, and response amplitude data (Bode plots) at the vibration probe locations through the range of each critical speed resulting from the unbalance specified in 6.6.2.3.3. d) The plot of deflected rotor shape for each critical speed resulting from the unbalances specified in 6.6.2.3.3, showing the major-axis amplitude at each coupling plane of flexure, the centerlines of each bearing, and the locations of each radial probe throughout the gear unit, as appropriate. e) Additional Bode plots that compare absolute shaft motion with shaft motion relative to the bearing housing for gear units where the casing support structure stiffness is less than 3.5 times the oil-film stiffness. f) Graphic display of bearing and support stiffness and its effect on critical speeds(Undamped critical speed-support stiffness map for bull gear rotor & both high speed pinion rotors). g) Graphic display of rotor response to unbalance (including damping) (deflected rotor shape showing the major-axis amplitude at key locations - radial bearing, shaft seal, oil seal to demonstrate amplitude well within diametral running clearance). h) Journal static and dynamic loads. i). Stiffness and damping coefficients for minimum and maximum clearance (minimum and maximum pre-loads). j) Tilting-pad bearing geometry and configuration. k) Rotor stability analysis. l) List of gear structural support system resonance frequencies. m) Support stiffness dynamic characteristics and basis for these values. Undamped: Undamped lateral analysis report of the complete coupled train, including but not limited to the following: a) Complete description of the method used. b) Mode shape plots of all undamped critical speeds in the range from 0 % to 125 % of trip speed (relative amplitude vs axial position on the rotor). c) Critical speed-support stiffness map (frequency vs support stiffness). Superimposed on this map shall be the calculated system support stiffness, horizontal (kxx) and vertical (kyy). d) At least three power levels, 10 %, 50 %, and 100 % of gear unit rated power analyzed. e) The bearing-oil film, bearing structure, and gear unit casing structure stiffness to be included. f) The coupling weight to be supported by each gearbox shaft. g) Bearing dynamic stiffness curves for the 10 %, 50 % and 100 % power levels to be plotted over undamped critical speed map (reference figure 5). | 11.4.10 | PDF | CFIHOS-70000449
S745-IR-62 | Special tools list | The special tools list shall identify all special tools necessary for handling, dismantling, maintenance etc. of equipment. Special tools list shall include: a) Identification of the tag number the special tool shall support. b) Description of the special tool. c) Storage, i.e. the location where the special tool can be found. d) Document references, if applicable. Note that the actual special tool is to be marked with the identification, i.e. tag number that it supports. |  | PDF | CFIHOS-70000454
S745-IR-65 | Parameter setting tables | The document shall contain a template including all adjustable parameters, indicating which parameters are fixed by the project. For parameters which have individual setting the criteria/formula for defining/calculating the individual setting shall be given. In addition the document shall include a table listing all individual settings. This table shall on one axis list all equipment (tags) and the other all parameter requiring individual setting. Examples of relevant equipment are: Synchronising Equipment, Insulation Monitoring equipment, Intelligent electrical devices (IED), Automatic voltage regulator (AVR). |  | PDF | CFIHOS-70000007
S745-IR-67 | 3D CAD model | Data stored in a format from which multiple information contents can be generated by computer software including 3D Model. Note: Final agreement for the format to be made between Contractor/Purchaser and Supplier. |  | Native | CFIHOS-70000083
S745-IR-68 | Stator and rotor thermal analysis | Where synchronous motors are fed from a frequency converter, rotor hot spot temperatures at the most severe conditions within the operating load envelope shall be evaluated, and included in the design and Stator and rotor thermal analysis. |  | PDF | CFIHOS-70000335
Purchase Order Specific Information Requirements

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: