## Addendum 1
Date of issue:
April 2026
Affected publication:
IOGP S-747D, Procurement Data Sheet for High-voltage AC Drive Systems (IEC), First Edition, September 2022
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in September 2022.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Row | Column | Update
| 53 | Purchaser requirement / Supplier offered value - options | Option "12" added
| 66 | All | New data sheet item "Drive configuration / parameter setting responsibility"
| 82 | All | New data sheet item "Conformal coating of control boards"
| 83 | All | New data sheet item "Acoustic noise test"
| 97 | Purchaser requirement / Supplier offered value - options | Option "tinned copper" deleted
| 112 | All | New data sheet item "Converter transformer"
| 113 | All | New data sheet item "Converter transformer and output transformer specification"
| 114 | All | New data sheet item "Output transformer"
| 108* | All | Data sheet item "BDM audible noise (dBA) at 1 m distance" * deleted
| 110 * through 126 * 128 * through 130 * | All | Transformer-related data sheet items deleted
| 132 | Purchaser requirement / Supplier offered value - options | Options "copper, fiber, none" * amended to "manufacturer standard, not required, hardwired discrete, serial cable, ethernet (cu), ethernet (fibre), multiple, other"
| 133 | Purchaser requirement / Supplier offered value - options | Options "Modbus TCP/IP, Modbus RTU, Profinet, Profibus, Ethernet, other, not applicable" * amended to "Modbus RTU, Profinet, Profibus, other"
| 135 | All | New data sheet item "Interface network redundancy for process control system"
| 136 | All | New data sheet item "Remote monitoring"
| 151 | All | New data sheet item "Motor specification"
| 154 | Description | Embedded guidance amended
| Various | Row | Numbering updated as per new and deleted rows

## Front & Preliminaries
|  |  |  | SPECIFICATION | April 2026
|  |  |  | IOGP S-747D | Version 1.01
ADDENDUM 1 TO FIRST EDITION (SEPTEMBER 2022)
Procurement Data Sheet for High-voltage AC Drive Systems (IEC)
Revision history
VERSION | DATE | PURPOSE
1.01 | April 2026 | Addendum 1
1 | September 2022 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-747D (1.01) Procurement Data Sheet for High-voltage AC Drive Systems (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-747D (1.01) Procurement Data Sheet for High-voltage AC Drive Systems (IEC)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of high-voltage AC drive systems in accordance with IOGP S-747 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-747), information requirements specification (IOGP S-747L) and quality requirements specification (IOGP S-747Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Procurement Data Sheet
Row | IOGP S-747D (1.01) Procurement Data Sheet for High-voltage AC Drive Systems (IEC) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | GENERAL
4 | Table 22 | BDM tag number : | input data |  | input data
5 | Table 22 | BDM tag description : | input data |  | input data
6 | Table 22 | Purchase order : | input data |  | input data
7 | Table 22 | BDM/CDM supplier : | input data |  | input data
8 | Table 22 | BDM model number : | input data |  | input data
9 | 9.4.7 | Driven equipment type : | select |  | select | [5 empty] | select | centrifugal pump | centrifugal fan | centrifugal compressor | reciprocating pump | reciprocating compressor | thruster drive | other
10 |  | PROJECT REQUIREMENTS
11 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
12 | 1.2 | Project country : | input data |  | input data
13 | 1.2 | Project region : | input data |  | input data
14 | 7.5.2 | Marine certification (additional) : | not applicable |  | not applicable | [5 empty] | select | DNV | Lloyds | ABS | USCG | NRTL | other | not applicable
15 | 4.3 | Applicable standard for BDM/CDM : | select |  | select | [5 empty] | select | IEC/IOGP | IEEE/ANSI/CSA/IOGP
16 | 4.3 | Applicable standard for motor : | select |  | select | [5 empty] | select | IEC/IOGP | API/IOGP/IEEE | NEMA/API/IOGP/IEEE
17 | 7.2 | NRTL certification and label on product : | select |  | select | [5 empty] | select | required | not required
18 | 5.3.6.2.3.1 | Insulation co-ordination study of PDS : | select |  | select | [5 empty] | select | required | not required
19 |  | INSTALLATION
20 | 1.2 | Location/area : | select |  | select | [5 empty] | select | onshore | offshore-fixed | offshore-floating | marine (ship)
21 | 5.9.6 | Location environment of BDM : | indoor conditioned |  | indoor conditioned | [5 empty] | select | indoor conditioned | indoor unconditioned | outdoor unconditioned
22 | 5.9.2.2.1 | Front access only for maintenance : | yes |  | yes | [5 empty] | select | yes | no
23 | 5.9.2.2.1 | Front access clearance dimensions for operation and maintenance : | input data | select | input data | select |  |  |  |  | select | mm | in
24 | 5.9.2.2.1 | Side clearance (if required) : | input data | select | input data | select |  |  |  |  | select | mm | in
25 | 5.9.2.2.1 | Rear clearance (if required) : | input data | select | input data | select |  |  |  |  | select | mm | in
26 |  | ENVIRONMENTAL CONDITIONS - STORAGE AND TRANSPORTATION
27 | 5.9.3.1 | Minimum ambient temperature (storage and transportation) : | input data | °C | input data | °C
28 | 5.9.3.1 | Maximum ambient temperature (storage and transportation) : | input data | °C | input data | °C
29 | 5.9.3.1 | Maximum relative humidity, non-condensing (storage and transportation) : | input data | % | input data | %
30 | 5.9.3.1 | Temperature at which relative humidity is specified (storage and transportation) : | input data | °C | input data | °C
31 | 5.9.2.3 | Additional or unusual conditions (storage and transportation) : | input data |  | input data
32 | 5.9.3.1 | Storage site : | select |  | select | [5 empty] | select | indoor-climate controlled (humidity and temperature) | indoor-temperature controlled only | indoor-natural ventilation | outdoor | other
33 |  | ENVIRONMENTAL CONDITIONS - OPERATION
34 | 9.3.1 | Minimum ambient temperature - BDM/CDM location (operation) : | input data | °C | input data | °C
35 | 9.3.1 | Maximum ambient temperature - BDM/CDM location (operation) : | input data | °C | input data | °C
36 | 9.3.1 | Maximum relative humidity - BDM/CDM location (operation) : | input data | % | input data | %
37 | 9.3.1 | Temperature at which relative humidity is specified - BDM/CDM location (operation) : | input data | °C | input data | °C
38 | 5.3.6.2.3.5 | Minimum outdoor ambient temperature : | input data | °C | input data | °C
39 | 5.3.6.2.3.5 | Maximum outdoor ambient temperature : | input data | °C | input data | °C
40 | 9.3.1 | Maximum altitude (operation) : | input data | m | input data | m
41 | 9.3.1 | Seismic spectral response acceleration at short period (SDS) in accordance with ASCE 7 : | input data | SDS | input data | SDS
42 | 9.3.1 | Seismic activity zone in accordance with IEC 60721-2-6 : | select |  | select | [5 empty] | select | Zone 1 | Zone 2 | Zone 3 | Zone 4 | not applicable
43 | 5.9.2.3, 9.3.1 | Additional or unusual conditions (operation) : | input data |  | input data
44 |  | SAFETY
45 | Table 22 | Degree of protection (with doors and/or covers closed) for HV compartment : | IP31 |  | IP31 | [5 empty] | select | IP31 | IP42 | IP54 | manufacturer's standard
46 | 5.5 | Applicable standard for safety requirements : | select |  | select | [5 empty] | select | IEC 61800-5-1 | UL 347A | CSA 22.2 NO 274
47 | 7.5.1 | Local language for caution/danger/warning labels : | input data |  | input data
48 | 10.1 | Shock/tilt indicator required : | select |  | select | [5 empty] | select | shock indicator only | shock and tilt indicator | other | not required
49 | 10.4 | Provision for external connection of temporary power supply during storage : | select |  | select | [5 empty] | select | required | not required
50 | 5.9.2.5 | BDM/CDM maximum sound pressure level at 1 m distance : | manufacturer's standard | dBA | manufacturer's standard | dBA |  |  |  |  | select | manufacturer's standard | other
51 |  | BDM/CDM CONFIGURATION
52 | 5.2.1 | BDM type : | select |  | select | [5 empty] | select | VSI | CSC | LCI
53 | 5.2.1 | BDM converter pulses : | select |  | select | [5 empty] | select | 12 | 18 | 24 | 36 | other
54 | 5.2.1 | BDM quadrant capability : | two quadrants |  | two quadrants | [5 empty] | select | two quadrants | four quadrants
55 | 5.11 | Redundancy of power semi-conductor devices : | not required |  | not required | [5 empty] | select | required | not required
56 | 5.3.6.2.6.4 | Electrostatic shield between transformer primary and all secondary windings : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | required
57 | 5.2.4.1 | BDM/CDM cooling method : | select |  | select | [5 empty] | select | air-cooled | water-cooled
58 | Table 11 | Continued operation with single ground fault : | not required |  | not required | [5 empty] | select | required | not required
59 | 8.3.2.2 | Upstream switchboard feeder disconnect device : | select |  | select | [5 empty] | select | circuit breaker | fused contactor | other
60 | 8.3.2.2 | Maximum opening time of disconnect device in upstream switchboard feeder : | input data | ms | input data | ms
61 | 8.3.7 | BDM/CDM output isolating device : | select |  | select | [5 empty] | select | circuit breaker | contactor | off load isolating switch | none
62 | Table 11 | Emergency stop button : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | on drive control panel only | on drive control panel and terminals for external stop input
63 | 5.15, 8.3.7 | Earthing provision : | select |  | select | [5 empty] | select | output side only | both input and output side | not required
64 | 5.15 | Earthing device : | select |  | select | [5 empty] | select | 20 mm (0.79 in) earthing ball | 25 mm (1 in) earthing ball | fixed earthing switch | not applicable
65 | Table 7 | Input harmonic filter : | select |  | select | [5 empty] | select | required at BDM/CDM input | required at upstream switchboard | manufacturer to propose | not required
66 |  | Drive configuration / parameter setting responsibility : | select |  | select | [5 empty] | select | by purchaser | by supplier
67 |  | BDM COOLING SYSTEM
68 | 8.3.3.3.5 | BDM cooling liquid type (secondary cooling circuit) : | select |  | select | [5 empty] | select | fresh water | sea water | not applicable | other
69 | 8.3.3.3.5 | Heat exchanger location : | select |  | select | [5 empty] | select | indoor - adjacent compartment of BDM line-up | indoor - separate from BDM enclosure | open ventilated area | outdoor | not applicable
70 | 8.3.3.1.2 | Heat exchanger redundancy : | not required |  | not required | [5 empty] | select | required | not required | not applicable
71 | 8.3.3.3.6 | Cooling liquid inlet temperature : | input data | °C | input data | °C
72 | 8.3.3.3.6 | Cooling liquid supply pressure : | input data | select | input data | select |  |  |  |  | select | bar | kPa
73 | 8.3.3.3.6 | Cooling liquid flow rate : | input data | m3/hr | input data | m3/hr
74 | 8.3.3.3.6 | Redundancy of conductivity sensors : | select |  | select | [5 empty] | select | required | not required | not applicable
75 |  | BDM SPECIAL FEATURES
76 | 5.6 | SIL level for safety functions : | select |  | select | [5 empty] | select | SIL1 | SIL 2 | SIL 3 | not applicable
77 | 5.2.2 | Insulation of internal wiring : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | low halogen and flame retardant | low halogen and flame retardant with low smoke index | manufacturer's standard
78 | 5.6 | Thermal monitoring of bus bar joints and cable connections : | select |  | select | [5 empty] | select | non-contact infrared sensors monitoring | infrared windows | not applicable
79 | 9.2.3, 9.3.1 | Active VAr control : | select |  | select | [5 empty] | select | required | not required | not applicable
80 | 5.3.6.3.1 | Exciter thermal overload protection (for synchronous motor) : | select |  | select | [5 empty] | select | manufacturer's standard | required | not applicable
81 | 5.11 | BDM remote access software and hardware : | select |  | select | [5 empty] | select | required - software with read access only | required - software with read/write access | required - hardware and software with read access only | required - hardware and software with read/write access | not required
82 |  | Conformal coating of control boards : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | required
83 | 6.6.11 | Acoustic noise test : | not required |  | not required | [5 empty] | select | required | not required
84 |  | BDM/CDM ENCLOSURE
85 | 8.2.3.1 | Arc flash detection sensor type : | select |  | select | [5 empty] | select | current | light | light + current | not applicable
86 | Table 22 | Overall enclosure dimensions - length : | input data | select | input data | select |  |  |  |  | select | mm | in
87 | Table 22 | Overall enclosure dimensions - depth : | input data | select | input data | select |  |  |  |  | select | mm | in
88 | Table 22 | Overall enclosure dimensions - height : | input data | select | input data | select |  |  |  |  | select | mm | in
89 | Table 22 | Total mass of enclosure : | input data | kg | input data | kg
90 | Table 22 | Maximum mass of transportation unit : | input data | kg | input data | kg
91 | 5.9.2.2.1 | Air ventilation arrangement : | select |  | select | [5 empty] | select | exhaust within the room | exhaust out of the room via duct | not applicable
92 | 8.2.1.7 | Cable entry location : | select |  | select | [5 empty] | select | bottom | top | both bottom and top
93 | 8.2.1.7 | Cable entry type : | select |  | select | [5 empty] | select | removable-undrilled plate | multi-cable transit
94 | 5.9.2.2.1 | Anti-vibration pads (offshore installations) : | select |  | select | [5 empty] | select | required | not required | not applicable
95 | Table 22 | Paint colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
96 | 10.4, Table 25 | Anti-condensation heater : | not required |  | not required | [5 empty] | select | required | not required
97 |  | Busbar material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | copper
98 | 8.6.1 | Earth bar material : | select |  | select | [5 empty] | select | manufacturer's standard | copper | tinned copper
99 | 5.2.2 | Canopy for enclosure : | not required |  | not required | [5 empty] | select | required | not required
100 | Table 22 | Document holder inside : | no |  | no | [5 empty] | select | yes | no
101 | 5.2.2 | LED lamps for internal illumination : | select |  | select | [5 empty] | select | required | not required
102 | 5.2.2 | Socket outlet in control compartment : | select |  | select | [5 empty] | select | required | not required
103 |  | BDM/CDM PERFORMANCE
104 | 5.8.2 | Efficiency of BDM (100 % of rated BDM load) : | input data | % | input data | %
105 | 5.8.2 | Efficiency of BDM (75 % of rated BDM load) : | input data | % | input data | %
106 | 5.3.6.2.2 | Efficiency of converter transformer at rated load : | input data | % | input data | %
107 | 5.3.6.2.2 | Efficiency of output transformer at rated load, when installed : | input data | % | input data | %
108 | 5.2.4.1 | Heat dissipation data to room (at converter rating) : | input data | W | input data | W
109 | 5.2.4.1 | Heat dissipation to cooling liquid (at converter rating) : | input data | W | input data | W
110 | 5.2.4.1 | Heat dissipation data (standby mode) : | input data | W | input data | W
111 |  | TRANSFORMER SPECIFICATIONS
112 | 5.3.6.2.1 | Converter transformer : | required (use IOGP S-720D) |  | required (use IOGP S-720D) | [5 empty] | select | required (use IOGP S-720D) | not required
113 | 5.3.6.2.1 | Output transformer : | required (use IOGP S-720D) |  | required (use IOGP S-720D) | [5 empty] | select | required (use IOGP S-720D) | not required
114 | 5.3.6.2.1 | Converter transformer and output transformer specification : | IEC 60076 (all parts) and IEC 61378 (all parts) |  | IEC 60076 (all parts) and IEC 61378 (all parts) | [5 empty] | select | IEC 60076 (all parts) and IEC 61378 (all parts) | IEEE C57.18.10 and IEEE C57.110
115 | 5.3.6.2.1, 5.3.6.2.2 | Water type for water cooled transformer : | select |  | select | [5 empty] | select | not applicable | fresh water | sea water | other
116 |  | INTERFACES - CABLES
117 | 8.4.3 | Cable type - input mains : | select |  | select | [5 empty] | select | armoured | unarmoured
118 | 8.4.3 | Cable details - input mains : | input data | select | input data | select |  |  |  |  | select | mm² | AWG | kcmil
119 | 5.3.2.1 | Input side cable length : | input data | select | input data | select |  |  |  |  | select | m | ft
120 | 8.4.3 | Cable type - between converter transformer and BDM : | select |  | select | [5 empty] | select | armoured | unarmoured | not applicable
121 | 8.4.3 | Cable details - between converter transformer and BDM : | input data | select | input data | select |  |  |  |  | select | mm² | AWG | kcmil
122 | 8.4.3 | Cable type - between BDM and output transformer : | select |  | select | [5 empty] | select | armoured screened | unarmoured screened | not applicable
123 | 8.4.3 | Cable details - between BDM and output transformer : | input data | select | input data | select |  |  |  |  | select | mm² | AWG | kcmil
124 | 8.4.3 | Cable type - motor : | select |  | select | [5 empty] | select | armoured screened | unarmoured screened
125 | 8.4.3 | Cable details - motor : | input data | select | input data | select |  |  |  |  | select | mm² | AWG | kcmil
126 | 5.3.6.3.6 | Motor cable length : | input data | select | input data | select |  |  |  |  | select | m | ft
127 |  | INTERFACES - CONTROLS AND AUXILIARY POWER
128 | Table 25 | External control supply voltage : | input data | select | input data | select |  |  |  |  | select | VAC | VDC
129 | Table 25 | Auxiliary power supply voltage : | input data | VAC | input data | VAC
130 | Table 23, Table 24 | Motor sensor inputs to BDM : | input data |  | input data
131 |  | INTERFACES - COMMUNICATION
132 | 5.4.4.2.6 | Interface media for process control system : | select |  | select | [5 empty] | select | manufacturer's standard | not required | hardwired discrete | serial cable | Ethernet (cu) | Ethernet (fibre) | multiple | other
133 | 5.4.4.2.6 | Interface protocol for process control system : | select |  | select | [5 empty] | select | Modbus RTU | Profinet | Profibus | other
134 | 5.4.4.2.6 | Interface protocol for time synchronization : | select |  | select | [5 empty] | select | IRIG-B | NTP | PTP | SNTP | not applicable
135 |  | Interface network redundancy for process control system : | not applicable |  | not applicable | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
136 |  | Remote monitoring : | not required |  | not required | [5 empty] | select | required | not required
137 |  | AC INPUT SPECIFICATIONS
138 | 5.3.2.2, 5.3.4.1, 9.1.1 | Rated voltage : | input data | VAC | input data | VAC
139 | 5.3.2.2, 5.3.4.1 | Voltage tolerance : | input data | % | input data | %
140 | 5.3.2.2, 5.3.4.1 | Rated frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
141 | 5.3.2.2, 5.3.4.1 | Frequency tolerance : | input data | % | input data | %
142 | 5.3.2.3, 5.3.4.1 | Rated input current (BDM/CDM) : | input data | A | input data | A
143 | 9.4.1 | Maximum symmetrical fault current : | input data | kA | input data | kA
144 | 9.1, Table 22 | Minimum short circuit current : | input data | kA | input data | kA
145 | 5.3.2.1 | Additional or unusual conditions : | input data |  | input data
146 |  | AC OUTPUT SPECIFICATIONS
147 | 5.3.3.1, 5.3.4.1 | Rated output power (apparent) : | input data | kVA | input data | kVA
148 | 5.3.3.1, 5.3.4.1 | Rated output voltage : | input data | VAC | input data | VAC
149 | 5.3.3.1, 5.3.4.1 | Rated output current : | input data | A | input data | A
150 |  | MOTOR SPECIFICATIONS
151 |  | Motor specification : | select |  | select | [5 empty] | select | yes - use IOGP S-704D | yes - use IOGP S-745D | manufacturer's standard | other
152 | 5.3.6.3.6 | Motor type : | select |  | select | [5 empty] | select | induction motor | synchronous motor | permanent magnet motor
153 | 5.3.3.2, 7.2, 5.3.6.3.6 | Motor power rating : | input data | select | input data | select |  |  |  |  | select | kW | HP
154 | 5.3.3.2, 5.3.6.3.6 | Motor rated voltage : | input data | VAC | input data | VAC
155 | 5.3.6.3.6 | Motor rated full load current : | input data | A | input data | A
156 | 5.3.3.2, 7.2, 5.3.6.3.6 | Motor rated speed : | input data | rpm | input data | rpm
157 | 5.3.3.2, 7.2, 5.3.6.3.6 | Motor rated torque : | input data | select | input data | select |  |  |  |  | select | Nm | lb-ft
158 | 5.3.6.3.6 | Power factor at 100 % of rated motor power : | input data |  | input data
159 | 5.3.6.3.6 | Power factor at 75 % of rated motor power : | input data |  | input data
160 | 5.3.6.3.6 | Efficiency at 100 % of rated motor power : | input data | % | input data | %
161 | 5.3.6.3.6 | Efficiency at 75 % of rated motor power : | input data | % | input data | %
162 | 5.3.3.2, 5.3.6.3.6 | Minimum continuous operating speed for process : | input data | rpm | input data | rpm
163 | 5.3.3.2, 5.3.6.3.6 | Maximum continuous operating speed for process : | input data | rpm | input data | rpm
164 | 5.3.6.3.6 | Moment of inertia of the load : | input data | select | input data | select |  |  |  |  | select | kg.m² | lb.ft²
165 | 5.3.6.3.6 | Hazardous area classification : | select |  | select | [5 empty] | select | non-hazardous | Zone 1 | Zone 2 | Zone 21 | Zone 22 | Class I Div 1 | Class I Div 2 | Class II Div 1 | Class II Div 2
166 | 5.3.6.3.6 | Type of protection : | select |  | select | [5 empty] | select | Ex-db | Ex-px | Ex-py | Ex-pz | Class I Div 1 | Class I Div 2 | Class II Div 1 | Class II Div 2 | not applicable
167 | 5.3.6.3.6 | Temperature class : | select |  | select | [5 empty] | select | T3 | T3A | T3B | T3C | T4 | T4A | T5 | not applicable
168 | 5.3.6.3.6 | Gas group : | select |  | select | [5 empty] | select | IIA | IIB | IIB + H2 | IIC | Group A | Group B | Group C | Group D | not applicable
169 | 5.3.6.3.6 | Dust group : | select |  | select | [5 empty] | select | IIIA | IIIB | IIIC | Group E | Group F | Group G | not applicable
170 | 5.3.6.3.4.1, 5.3.6.3.6 | Bearing insulation required : | select |  | select | [5 empty] | select | one end | both ends | both ends with jumper at one end | both ends with brush at one end | manufacturer's standard
Note on C4: Specify the unique tag number for the equipment (BDM).
Note on C5: Specify the functional description of the equipment (BDM).
Note on C6: Specify the purchase order number.
Note on C7: Specify the BDM/CDM supplier's name.
Note on C8: Specify the product series, range or model number, etc.
Note on C9: Select the equipment intended to be driven by the HV AC drive system. If "other" is selected, specify details in the "Additional notes" column.
Note on C11: Select the CAS level as applied in IOGP S-747Q, Annex A. Default value : D
Note on C12: Specify the country for the final installation of the BDM/CDM to enable the supplier to provide the required product marking and certification for the region.
Note on C13: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C14: Select the marine certification requirement according to the project. Specify any other certification requirements in the "Additional notes" column. Default value : not applicable
Note on C15: Select the applicable standards for the components of the BDM/CDM.
Note on C16: Select the applicable standard for main motor as part of the PDS.
Note on C17: Select the choice of NRTL certification and label on the product. Customer to specify the "Authority Having Jurisdiction (AHJ)" for the project region by providing details in the "Additional notes" column.
Note on C18: Customer to select whether the supplier must perform an insulation co-ordination study of the PDS to ascertain the overvoltage conditions to specify insulation levels of cables, transformer and motors.
Note on C20: Select the location/area where the HV AC drive system is to be installed. Additionally, if the location/area selected is either offshore-floating or marine (ship), specify the pitch and roll requirements in the "Additional notes" column.
Note on C21: Select the environmental service conditions in accordance with Table 12. Default value : indoor conditioned
Note on C22: Select the requirement for front access for maintenance of the HV AC drive system. This data sheet element is specifically added to address any rear space limitation. Select "yes" in case of space limitation or when planned to install against a wall. Default value : yes
Note on C23: Specify the front clearance dimension required in mm (in).
Note on C24: Specify the side clearance dimension required in mm (in).
Note on C25: Specify the rear clearance dimension required in mm (in).
Note on C27: Specify the minimum ambient temperature expected during storage and transportation.
Note on C28: Specify the maximum ambient temperature expected at the BDM/CDM location during operation with HVAC (heating, ventilation and air conditioning). Specify the maximum ambient temperature faced during HVAC failure in the "Additional notes" column.
Note on C29: Specify the maximum relative humidity, non-condensing, expected during storage and transportation.
Note on C30: Specify the temperature at which the relative humidity is specified during storage and transportation.
Note on C31: Specify additional or unusual conditions expected during storage and transportation.
Note on C32: Select the choice of storage site for the HV AC drive. If "other" is selected, specify in the "Additional notes" column.
Note on C34: Specify the minimum ambient temperature expected at the BDM/CDM location during operation.
Note on C35: Specify the maximum ambient temperature expected at the BDM/CDM location during operation with HVAC (heating, ventilation and air conditioning). Specify the maximum ambient temperature faced during HVAC failure in the "Additional notes" column, if required.
Note on C36: Specify the maximum relative humidity expected at the BDM/CDM location during operation.
Note on C37: Specify the temperature at which the relative humidity is specified at the BDM/CDM location while in operation.
Note on C38: Specify the minimum outdoor ambient temperature expected for mitigation measures to avoid condensation within BDM/CDM.
Note on C39: Specify the maximum outdoor ambient temperature expected for the heat exchanger design.
Note on C40: Specify the installation altitude above mean sea level.
Note on C41: Where seismic certification in accordance with ASCE 7 is required, specify the SDS value as defined in ASCE 7 for the location where the HV AC drive is used. Where seismic certification is not required, specify "not applicable".
Note on C42: Where seismic certification in accordance with IEC 60068-3-3 is required, select the seismic activity zone as defined in IEC 60721-2-6 for the location where the HV AC drive is used. Where seismic certification is not required, select "not applicable".
Note on C43: Specify additional or unusual conditions like gas (e.g. H2S) expected during operation.
Note on C45: Select the ingress protection (air or water cooled unit as selected) based on the installation location with enclosure doors and/or covers closed. IP31 is still the minimum requirement even when the manufacturer's standard is selected. Default value : IP31
Note on C46: Select the choice of applicable standard for safety requirements to be complied with by the supplier based on the project region.
Note on C47: Specify if any additional local/native language is to be used for describing Caution/Danger/Warning information on the equipment labels.
Note on C48: Select whether each transportation unit should be installed with shock/tilt indicator. Select "other" and specify in the "Additional Notes" column any additional requirements such as datalogging or tracking during transportation.
Note on C49: Select whether each shipping section should have a provision for external connection of temporary power supply to space heater during storage. Specify the voltage level required in the "Additional notes" column.
Note on C50: Select "other" if it is not the manufacturer's standard and specify in the "Additional notes" column the acceptable limit of BDM/CDM maximum sound pressure level in dBA measured at 1 m distance in any direction from the source. Default value : manufacturer's standard
Note on C52: Select the required BDM type for the HV AC drive or let the manufacturer select based on the application mentioned. Voltage source converter (VSC), current source converter (CSC), load commutation inverter (LCI).
Note on C53: Select the required converter pulses or let the manufacturer select based on the HV AC drive model offered. If “other” is selected, specify in the "Additional notes" column.
Note on C54: Select the number of quadrants in which the BDM can perform its operation. Default value : two quadrants
Note on C55: Select whether the HV AC drive needs to have redundancy of power semi-conductor devices. Default value : not required
Note on C56: Select whether the transformer should have an electrostatic shield between the transformer primary and all secondary windings in accordance with IEC 61800-2, 5.3.6.2.6.4. Default value : manufacturer's standard
Note on C57: Select the required cooling method for the BDM/CDM.
Note on C58: Select whether the HV AC drive system is expected to continue operation with single ground fault (occurring on transformer secondary, cable connection, drive, motor cables or motor). Default value : not required
Note on C59: Select which input disconnect device is installed in the feeder of upstream switchboard feeding the HV AC drive system. If "other" is selected, specify in the "Additional notes" column.
Note on C60: Specify in milliseconds (ms) the maximum opening time of the disconnect device installed in the upstream switchboard feeder that feeds the HV AC drive system.
Note on C61: Select which isolating device is installed at the output side of the BDM/CDM.
Note on C62: Select whether the drive must be provided with an emergency stop on the drive panel and have terminals for remote input. Default value : manufacturer's standard
Note on C63: Select the requirement of earthing provision within BDM/CDM.
Note on C64: Select the type of earthing device to be considered within BDM/CDM.
Note on C65: If the customer's preliminary study has identified the need of harmonic filter, select the appropriate option to include the design and supply of harmonic filter along with the HV AC drive package. If manufacturer to propose, select accordingly.
Note on C66: Select which party (purchaser or supplier) will be responsible for configuration and parameter setting of the drive, to suit the specific application and driven equipment.
Note on C68: Select the type of liquid considered for liquid cooling of the BDM in the secondary cooling circuit. If "other" is selected, specify the information on liquid in the "Additional notes" column.
Note on C69: Select the location where the heat exchanger will be installed.
Note on C70: Select whether redundancy is required for the installed heat exchanger. Default value : not required
Note on C71: Specify the cooling liquid (secondary circuit) temperature at the inlet of heat exchanger.
Note on C72: Specify the pressure of cooling liquid (secondary circuit) at the inlet of heat exchanger.
Note on C73: Specify the flow rate of cooling liquid (secondary circuit) required through the heat exchanger.
Note on C74: Select whether redundancy of conductivity sensors is required.
Note on C76: Select the required SIL level of safety functions for explosive atmospheres.
Note on C77: Select the choice of insulation of internal wiring based on the criticality of application or the location of installation of the drive system. Default value : manufacturer's standard
Note on C78: Specify whether thermal monitoring of bus bar joints and cable connections is required and what measurement arrangement is to be considered.
Note on C79: Select whether active VAr control is required. Select "not applicable" when the BDM is without AFE/AIC and "yes" or "no" when the BDM is with AFE/AIC.
Note on C80: Select whether the exciter thermal overload protection (ANSI 49RTD - Source: ANSI/IEEE Standard C37.2) is required in addition to exciter stator winding over temperature protection. Applicable for brushless exciter of synchronous motor.
Note on C81: Select if the HV AC drive needs to be accessed from a central location or a remote location through intranet (factory network) or internet (public network). Specify the hardware details and scope in the "Additional notes" column.
Note on C82: Select whether conformal coating of control boards is required. This requirement is generally applicable in tropical and offshore environments where elevated humidity increases the risk of condensation. Default value : manufacturer's standard
Note on C83: Select if an acoustic noise test is required in addition to the routine testing. Default value : not required
Note on C85: Select the sensor type for detection of arc flash energy.
Note on C86: Specify the overall enclosure dimensions - length.
Note on C87: Specify the overall enclosure dimensions - depth.
Note on C88: Specify the overall enclosure dimensions - height.
Note on C89: Specify the overall enclosure mass.
Note on C90: Specify the mass of the transportation unit that has maximum mass.
Note on C91: Select the ventilation arrangement provided to the exhaust air from the enclosure.
Note on C92: Select the cable entry location based on the installation planned.
Note on C93: Select the type of cable entry considered for the enclosure (gland plate or multi-cable transit).
Note on C94: Select whether anti-vibration pads are required in the enclosure for offshore installations.
Note on C95: Select choice of external paint colour for the enclosure. If "other" is selected, use the "Additional notes" column to specify the paint colour. Default value : manufacturer's standard
Note on C96: Select whether anti-condensation heaters are required within the BDM/CDM enclosure based on the variation in ambient temperature. Specify the voltage in the "Additional notes" column. Default value : not required
Note on C97: Select the material of construction for the internal busbars of the enclosure. Default value : manufacturer's standard
Note on C98: Select the material of construction for the earth bar of the enclosure.
Note on C99: Select whether a canopy is required for the enclosure. Default value : not required
Note on C100: Select whether a document holder is required inside the enclosure. Default value : no
Note on C101: Select whether an LED lamp/panel light is required for illumination within the enclosure. An LED lamp/panel light would normally be supplied from auxiliary supply. Specify the lux level requirement in the "Additional notes" column.
Note on C102: Select whether a socket outlet is required in the control compartment connected to auxiliary supply. Specify the socket type required in the "Additional notes" column.
Note on C104: Specify the efficiency value of the BDM at 100 % of the rated BDM load.
Note on C105: Specify the efficiency value of the BDM at 75 % of the rated BDM load.
Note on C106: Specify the efficiency value of the converter transformer at rated load.
Note on C107: Specify the efficiency value of the output transformer at rated load when installed.
Note on C108: Specify the heat dissipated from the BDM/CDM at converter rating to room to design room air conditioning. Specify the breakup of heat dissipation data as applicable (dissipation within room and to outside via exhaust duct) in "Additional notes" column.
Note on C109: Specify the data for heat dissipation to the cooling liquid.
Note on C110: Specify the heat dissipated from the BDM/CDM in standby mode to design room air conditioning. Specify breakup of heat dissipation data as applicable (to ambient within room, to outside via exhaust duct, to cooling liquid) in "Additional notes" column.
Note on C112: Select whether a transformer is required at the input side. IOGP S‑720D is referenced here solely for the purpose of defining transformer requirements. Compliance with IOGP S-720 is not implied. Default value : required (use IOGP S-720D)
Note on C113: Select whether a transformer is required at the output side. IOGP S‑720D is referenced here solely for the purpose of defining transformer requirements. Compliance with IOGP S-720 is not implied. Default value : required (use IOGP S-720D)
Note on C114: Select the specification for the converter and output transformer. Default value : IEC 60076 (all parts) and IEC 61378 (all parts)
Note on C115: Select the water type used for water cooled transformer. If "other" is selected, specify the information on water in the "Additional notes" column.
Note on C117: Select the type of the power cable for input mains.
Note on C118: Specify the details of the power cable (number of cores, size) of input mains (e.g. 2R x 3C x 120 mm², where R - number of runs; C - number of cores; 120 - example of cross section area; mm² - appropriate UOM).
Note on C119: Specify the input supply cable length. This information is required to assess transient overvoltage impact and consider suitable mitigation measures.
Note on C120: Select the type of power cable between the converter transformer and the BDM, if applicable.
Note on C121: Specify the details of power cable (number of cores and size) between the converter transformer and the BDM, if applicable (e.g. 2R x 3C x 120 mm², where R - number of runs; C - number of cores; 120 - example of cross section area; mm² - appropriate UOM).
Note on C122: Select the type of the power cable between the BDM and the output transformer, if applicable. Screened cables are also referred to as shielded cables.
Note on C123: Specify the details of power cable (number of cores and size) between the BDM and the output transformer, if applicable (e.g. 2R x 3C x 120 mm², where R - number of runs; C - number of cores; 120 - example of cross section area; mm² - appropriate UOM).
Note on C124: Select the type of power cable for the motor. Screened cables are also referred to as shielded cables.
Note on C125: Specify the details of power cable (number of cores and size) for the motor (e.g. 2R x 3C x 120 mm², where R - number of runs; C - number of cores; 120 - example of cross section area; mm² - appropriate UOM).
Note on C126: Specify the approximate motor cable length (from the BDM/CDM to the motor) to evaluate the requirement of output components (e.g. reactor, filters).
Note on C128: Specify the control supply voltage provided from the external source to the HV AC drive. The external control supply is usually from two independent supply sources.
Note on C129: Specify the voltage and power rating required for auxiliary systems like cooling system, pre-charge, space heater, illumination, socket, etc. Use the "Additional notes" column to specify number of phases. amperage or wattage.
Note on C130: Specify the sensors installed on the motor with inputs to the BDM (e.g. vibration/winding and bearing temperature sensor, leakage detection sensor, flow sensor).
Note on C132: Select the interface media connected from the process control system.
Note on C133: Select the interface protocol for the process control system. If "other" is selected, specify in the "Additional notes" column.
Note on C134: Select the communication protocol required for time synchronization with the central time server.
Note on C135: Select the interface network redundancy system. PRP or HSR (IEC 62439-3) provide seamless failover against failure of a network component for most industrial ethernet protocols. Select "other" to specify other redundancy protocols. Default value : not applicable
Note on C136: Select if remote monitoring is required. When "required" is selected, specify in the "Additional notes" column. Default value : not required
Note on C138: Specify the rated input voltage.
Note on C139: Specify the input voltage tolerance.
Note on C140: Select the rated input frequency.
Note on C141: Specify the input frequency tolerance.
Note on C142: Specify the rated input current drawn by the CDM (for upstream device selection).
Note on C143: Specify the maximum symmetrical fault current of the supply system in accordance with IEC 61800-2:2021, 5.4.1.5.2.
Note on C144: Specify the input supply short circuit current capacity (minimum).
Note on C145: Specify additional or unusual conditions envisaged at the AC input supply side of the HV AC drive.
Note on C147: Specify the output power in kVA.
Note on C148: Specify the rated voltage at the output of the BDM. Note that the BDM output defines the motor rated voltage. If the output voltage does not match the motor voltage an output transformer is used.
Note on C149: Specify the value of the rated BDM output current drawn by 100 % converter load.
Note on C151: Select the motor specification for when the motor is to be supplied by the high-voltage AC drive supplier. If the motor is not supplied by the HV AC drive supplier or "other" is selected, use "Additional notes" for further clarification.
Note on C152: Select the type of the motor driven by the BDM/CDM.
Note on C153: Specify the kW or HP rating of the motor driven from the BDM/CDM. In cases where the motor is already sufficiently de-rated, the shaft power required by driven equipment can be specified in the "Additional notes" column.
Note on C154: Specify the rated motor voltage, considering the BDM and output transformer. Generally, this should be determined by the BDM supplier, but it may be determined by the purchaser, particularly in retrofit cases.
Note on C155: Specify the value of the motor rated full load current.
Note on C156: Specify the rated speed of the motor.
Note on C157: Specify the rated torque of the motor.
Note on C158: Specify the power factor value at 100 % of the rated motor power.
Note on C159: Specify the power factor value at 75 % of the rated motor power.
Note on C160: Specify the efficiency value of motor at 100 % of the rated motor power.
Note on C161: Specify the efficiency value of motor at 75 % of the rated motor power.
Note on C162: Specify the minimum continuous motor operating speed required by process for the driven equipment (minimum speed from the operating speed range).
Note on C163: Specify the maximum continuous motor operating speed required by process for the driven equipment (maximum speed from the operating speed range).
Note on C164: Specify the moment of inertia (mr²) of the load (total inertia as transferred on to the motor shaft including the rotor inertia).
Note on C165: Select the area classification of the motor (fed from the BDM/CDM) in accordance with IEC 60079-10, API RP 505 or API RP 500.
Note on C166: Select the type of protection for motors installed in hazardous areas based on the ex-classification certification. Ex-ec and Ex-eb types are excluded intentionally as they are not a preferred due to complexity in application and testing requirements.
Note on C167: Select the motor temperature class rating.
Note on C168: Select the motor gas group rating.
Note on C169: Select the motor dust group rating.
Note on C170: Select the type and location of insulated bearings required in the motor.

## Supplement
Row |  | IOGP S-747D (1.01) Procurement Data Sheet for High-voltage AC Drive Systems (IEC) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
IOGP S-747D (1.01) Procurement Data Sheet for
High-voltage AC Drive Systems (IEC)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-747 Supplementary Specification to IEC 61800-2 High-voltage AC Drive Systems.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data