## Addendum 1
Date of issue:
April 2026
Affected publication:
IOGP S-747L, Information Requirements for High-voltage AC Drive Systems (IEC), First Edition, September 2022
ADDENDUM 1
This addendum (Version 1.01) replaces Edition 1.0 published in September 2022.
NOTE: In addition to the updates listed below, minor editorial/typographical amendments may have been made.
List of updates
| Worksheet | IR ID | Column | Update
| Requirements | IR-67 | C - Conditon Invoking Requirement | Condition invoking requirement amended
| Definitions |  | C - Description | Description amended
| Requirements Definitions | IR-81 | All | New information requirement "Drive configuration / settings file"
| Definitions | IR-4 | F - CFIHOS Code | CFIHOS code CFIHOS-70000451 added
| Definitions | IR-9 | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000260
| Definitions | IR-71 | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000083
| Definitions | IR-31 | F - CFIHOS Code | CFIHOS code CFIHOS-70000449 added
| Definitions | IR-72 | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000083
| Definitions | IR-76 | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000083
| Definitions | IR-73 | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000083
| Definitions | IR-35 | F - CFIHOS Code | CFIHOS code CFIHOS-70000441 added
| Definitions | IR-42 | F - CFIHOS Code | CFIHOS code CFIHOS-70000012 added
| Definitions | IR-47 | F - CFIHOS Code | CFIHOS code CFIHOS-70000454 added
| Definitions | IR-49 | F - CFIHOS Code | CFIHOS code amended to CFIHOS-70000366

## Front & Preliminaries
|  |  |  | SPECIFICATION | April 2026
|  |  |  | IOGP S-747L | Version 1.01
ADDENDUM 1 TO FIRST EDITION (SEPTEMBER 2022)
Information Requirements for High-voltage AC Drive Systems (IEC)
Revision history
VERSION | DATE | PURPOSE
1.01 | April 2026 | Addendum 1
1 | September 2022 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-747L (1.01) Information Requirements for High-voltage AC Drive Systems (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-747L (1.01) Information Requirements for High-voltage AC Drive Systems (IEC)
Introduction
The purpose of this information requirements specification (IRS) is to define information requirements for the procurement of high-voltage AC drive systems in accordance with IOGP S-747 for application in the petroleum and natural gas industries. The IRS defines the information requirements, including format, timing and purpose, for information to be provided by the supplier. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the specification (IOGP S-747), procurement data sheet (IOGP S-747D) and quality requirements specification (IOGP S-747Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification

## Instructions
IOGP S-747L (1.01) Information Requirements for
High-voltage AC Drive Systems (IEC)
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS Structure Contents
| 1 | 'Front & Preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes / No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information Submission Abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS .
Column K — 'Translation Required' (Yes / No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable Formats
Column F — 'CFIHOS Discipline Document Type Code' relates to the CFIHOS discipline document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3 below. Metadata listed below are as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The document master to which this revision is related |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification |  |  | The Export Control Rule that is applicable for the document revision (e.g., ECCN, EAR). |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
| Security classification |  |  | Indicates internal Owner-Operator access restriction applicable for the document |  |  | TBA
Table 3 — Supplier Deliverable Metadata

## Requirements
IOGP S-747L (1.01) Information Requirements for High-voltage AC Drive Systems (IEC)
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Information Deliverable Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S747-IR-20 | Supplier master information schedule |  | Information deliverables list | No | For Acceptance |  | - | - |  | -
S747-IR-2 | Delivery schedule |  | Delivery/production schedule | Yes | For Information |  | - | - |  | -
S747-IR-3 | Progress report |  | Progress report | No | For Information |  | - | - |  | -
S747-IR-4 | Quality plan | Required for CAS A, CAS B, CAS C | Quality plan | - | - |  | - | - |  | -
S747-IR-24 | Sub-supplier list |  | Qualified supplier (vendor) list | Yes | For Information |  | - | - |  | -
S747-IR-21 | Inspection and test plan for complete package | Required for CAS A, CAS B, CAS C | Inspection and test plan (ITP) | - | - |  | - | - |  | -
S747-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | - | - |  | -
S747-IR-22 | Non-conformance records |  | Non-conformance records | No | For Acceptance |  | - | - |  | -
S747-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | - | - |  | -
Technical Information Deliverables
S747-IR-26 | Equipment data sheet (BDM/CDM/PDS) |  | Manufacturer data sheet | Yes | For Acceptance |  | - | - |  | -
S747-IR-27 | General arrangement diagram (BDM/CDM/PDS) |  | General arrangement diagram | No | For Acceptance |  | - | - |  | -
S747-IR-29 | Insulation co-ordination study | Selection of insulation co-ordination study of PDS on data sheet. | System study | No | For Information |  | - | - |  | -
S747-IR-71 | Input data for lateral and torsional critical speed analysis by driven equipment supplier |  | Interface register | No | For Information |  | - | - |  | -
S747-IR-31 | Load data and performance curves |  | Motor performance and electrical data and curves | No | For Information |  | - | - |  | -
S747-IR-72 | Input data for harmonic analysis |  | Interface register | No | For Information |  | - | - |  | -
S747-IR-76 | Input harmonics data from drive supplier for pulsating air gap torque |  | Interface register | No | For Information |  | - | - |  | -
S747-IR-33 | Utility summary, consumption data and electrical load list |  | Consumption data and load list | Yes | For Information |  | - | - |  | -
S747-IR-73 | Upstream feeder protection device data |  | Interface register | No | For Information |  | - | - |  | -
S747-IR-35 | Heat dissipation summary |  | Heat dissipation calculation and loads | Yes | For Information |  | - | - |  | - | Preliminary interface information with proposal.
S747-IR-66 | Control and interface block diagram (BDM/CDM/PDS) |  | Control system diagram | No | For Information |  | - | - |  | -
S747-IR-37 | Wiring diagram |  | Wiring diagram | No | For Acceptance |  | - | - |  | -
S747-IR-70 | Inter-connection diagram |  | Connection diagram | No | For Acceptance |  | - | - |  | -
S747-IR-39 | Earthing diagram |  | Earthing diagram | No | For Information |  | - | - |  | -
S747-IR-40 | Equipment piping and instrumentation diagram | Required for liquid filled transformers and water cooled BDMs | Piping and instrumentation diagram | No | For Information |  | - | - |  | -
S747-IR-41 | Data address mapping list |  | Input, output list | No | For Information |  | - | - |  | -
S747-IR-42 | Drive parameter setting list |  | Configuration file | No | For Information |  | - | - |  | -
S747-IR-43 | Bill of materials (BDM/CDM/PDS) |  | Bill of materials | No | For Information |  | - | - |  | -
S747-IR-44 | Recommended spare part list (BDM/CDM/PDS) |  | Spare part list | Yes | For Information |  | - | - |  | -
S747-IR-46 | Drive configuration and remote access software |  | Application software | No | For Information |  | - | - |  | - | Software and a valid user license will be provided if agreed in contract.
S747-IR-47 | Special tools list |  | Special tools list | No | For Information |  | - | - |  | -
S747-IR-48 | Installation manual (BDM/CDM/PDS) |  | Installation manual | No | For Information |  | - | - |  | - | Installation manual index, if required, should be provided in first revision of the document. When index agreed, installation manual content shall be provided in subsequent revision of the document. Can be accepted as a combined installation, operation and maintenance manual.
S747-IR-49 | Commissioning instruction (BDM/CDM/PDS) |  | Commissioning instruction | No | For Information |  | - | - |  | - | Can be accepted as a part of operation and maintenance (O&M) manual.
S747-IR-50 | Operating manual (BDM/CDM/PDS) |  | Operating manual | No | For Information |  | - | - |  | - | Operating manual index, if required, should be provided in first revision of the document. When index agreed, operating manual content shall be provided in subsequent revision of the document. Can be accepted as a combined installation, operation and maintenance manual.
S747-IR-51 | Maintenance manual (BDM/CDM/PDS) |  | Maintenance manual | No | For Information |  | - | - |  | - | Maintenance manual index, if required, should be provided in first revision of the document. When index agreed, maintenance manual content shall be provided in subsequent revision of the document. Can be accepted as a combined installation, operation and maintenance manual.
S747-IR-67 | Type test certificate | Required for CAS A, CAS B | General certificate | - | - |  | - | - |  | - | Type test certificate required for CAS D, in case of new range of products and new suppliers. Multiple type test certificates may be provided e.g. Arc flash, transformer short circuit, etc.
S747-IR-53 | Hazardous area certificate (equipment and individual components) | Required only for functional protection related to Ex motor and liquid filled transformers (Zone 2) | Hazardous area certificate (type) | No | For Information |  | - | - |  | -
S747-IR-54 | Seismic certification | Where either seismic spectral response acceleration at short period (SDS) in accordance with ACSE 7 or a seismic activity zone in accordance with IEC 60721-2-6 has been specified. | Certificate of conformance | Yes | For Information |  | - | - |  | -
S747-IR-56 | Marine certificate (additional) | If required by the data sheet | General certificate | No | For Information |  | - | - |  | -
S747-IR-57 | Declaration of conformity (BDM/CDM/PDS) |  | Declaration of conformity | No | For Information |  | - | - |  | -
S747-IR-58 | Factory acceptance test (FAT) procedure (BDM/CDM/PDS) | Required for CAS A, CAS B, CAS C | Factory acceptance test (FAT) procedure | - | - |  | - | - |  | -
S747-IR-60 | Factory acceptance test (FAT) records (BDM/CDM/PDS) |  | Factory acceptance test (FAT) records | No | For Acceptance |  | - | - |  | -
S747-IR-63 | Packing list |  | Packing list | No | For Information |  | - | - |  | -
S747-IR-77 | Site acceptance test (SAT) procedure |  | Site acceptance test (SAT) procedure | No | For Acceptance |  | - | - |  | -
S747-IR-78 | Site acceptance test (SAT) records |  | Site acceptance test (SAT) records | No | For Acceptance |  | - | - |  | -
S747-IR-79 | Material safety data sheet |  | Safety data sheet | No | For Information |  | - | - |  | -
S747-IR-81 | Drive configuration / settings file | If "by supplier" is selected on the PDS for "Drive configuration / parameter setting responsibility" | Configuration file | No | For Information |  | - | - |  | -
Purchase Order Specific Information Requirements

## Definitions
IOGP S-747L (1.01) Information Requirements for High-voltage AC Drive Systems (IEC)
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Discipline Document Type Code — CFIHOS discipline document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Deliverables
S747-IR-20 | Supplier master information schedule | Schedule of specific information deliverables developed by the supplier and accepted by the customer to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines: — information deliverable type, title/description; — unique identification (code/number) in the supplier's format unless agreed otherwise in the contract; — planned submission arrangements including; purpose, formats, timing, frequency. Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S747-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by supplier/sub-supplier. Schedule details typically** include; — contractual milestones; — activity early/late start/completion dates, durations, dependencies (calendar dates); — critical path and float; — outsourced services and equipment (cross referenced to purchase order and supplier); — information deliverable submission dates identifying any execution activity dependencies. Progress against planned dates is measured and the schedule updated and reported to the customer in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the supplier's standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S747-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S747-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the supplier, and when applicable sub-suppliers or manufacturers, to deliver the services or procured item(s) in conformance with the agreed requirements. |  | PDF | CFIHOS-70000451
S747-IR-24 | Sub-supplier list | A list of suppliers qualified to deliver a specific scope, products and/or services. | Table 22 | PDF | CFIHOS-70000014
S747-IR-21 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. | 4.2.1, 4.2.2, Table 22, Table 6 | PDF | CFIHOS-70000180
S747-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: — packaging requirements; contents, identification, size, weight and number of packages/container(s); — special packing/unpacking/handling requirements; — storage location and requirements; — preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. |  | PDF | CFIHOS-70000154
S747-IR-22 | Non-conformance records | Details of non-conformances raised by or to the suppliers/sub-suppliers against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the supplier in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the customer in accordance with the concession management protocols defined in the contract. |  | PDF | CFIHOS-70000226
S747-IR-9 | Concession requests | Formal submission seeking customer agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, customer directions, agreed action status provided with progress reports and at contract closeout. |  | PDF | CFIHOS-70000260
Technical Information Deliverables
S747-IR-26 | Equipment data sheet (BDM/CDM/PDS) | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. The document shall provide information on technical data and characteristics about material, products or systems and their environment for proper implementation. The proposal submission of this data sheet should be based on IOGP S-747D. | 5.3.2.2, 5.3.2.3, 5.3.3.1, 5.3.3.2, 5.3.4.1, 7.2, 7.3, 7.4, 7.5.1, 4.2.1, 4.2.2, 8.3.3.3.5, 8.3.4.2, 9.2.2.1, 9.2.2.2, 9.2.2.3, Table 23, Table 24, Table 25, Table 6 | PDF | CFIHOS-70000416
S747-IR-27 | General arrangement diagram (BDM/CDM/PDS) | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing shall contain reference to main specifications and standards. For equipment/components the drawing may include cross sectional views. Document may contain the following information: — main dimensions of BDM/CDM/PDS; — internal arrangement of components & terminations (internal layout and dimensions/clearances) of BDM/CDM; — interface connections of BDM/CDM/PDS; — marking, labelling, nameplate and rating plate information of BDM/CDM/PDS; — weight of BDM/CDM/PDS; — centre of gravity of BDM/CDM/PDS; — withdrawal/installation and maintenance space of BDM/CDM; — sectionalization and transportation unit of BDM/CDM; — installation and mounting details of BDM/CDM/PDS; — lifting arrangement of BDM/CDM/PDS. | 7.2, 5.3.6.3.4.1, 8.2.1.8, 8.2.3.3, 8.3.3.3.5, 8.3.3.3.6, 8.3.8 | PDF | CFIHOS-70000153
S747-IR-29 | Insulation co-ordination study | Document providing information about insulation co-ordination, and basic conditions and assumptions used for selection and application of appropriate insulation co-ordination solutions. Optional study may include load flows, transient and dynamic stability, short circuit, protection study, co-ordination and setting, if requested as part of contract. Supplier of PDS system shall evaluate the overvoltage conditions and suggest suitable insulation levels for transformers, cables and motors. | 5.3.6.2.3.1 | PDF | CFIHOS-70000388
S747-IR-71 | Input data for lateral and torsional critical speed analysis by driven equipment supplier | A register documenting agreements and responsibilities between internal and external parties (especially between contract scopes). An overview of all communications (also called interface queries) and their status between two parties for the management of interface communication. This document provides input data for lateral and torsional critical speed analysis by driven equipment supplier. | 9.4.7 | PDF | CFIHOS-70000083
S747-IR-31 | Load data and performance curves | Curves to indicate torque and current against speed for 100% voltage conditions and at rated frequency, superimposed on driven equipment torque curve to confirm that there is adequate net torque for acceleration. The following performance curves are required for 100% voltage including tolerance: — motor speed 'v' torque; — motor speed 'v' Power factor; — motor speed 'v' current; — driver equipment torque 'v' speed for all start up conditions. Optional information: — negative phase sequence current curve. | 5.3.3.1 | PDF | CFIHOS-70000449
S747-IR-72 | Input data for harmonic analysis | A register documenting agreements and responsibilities between internal and external parties (esp. between contract scopes). An overview of all communications (also called interface queries) and their status between two parties for the management of interface communication. This document provides complete harmonic data (spectrum) of the connected device so as to enable power system engineer to analyze the impact of total harmonic on the overall power system. | 5.3.2.3 | PDF | CFIHOS-70000083
S747-IR-76 | Input harmonics data from drive supplier for pulsating air gap torque | A register documenting agreements and responsibilities between internal and external parties (esp. between contract scopes). An overview of all communications (also called interface queries) and their status between two parties for the management of interface communication. This document provides harmonic data (non-integer and integer harmonics data including Campbell diagram) of the connected device so as to enable the driven equipment supplier to perform torsional studies / analyze the pulsating air gap torque. The typical data that may be shared would be: — calculated rotor responses; — transient air gap torques with their duration following a short circuit at the motor terminals for both 2 and 3 phase faults; — integer and non-integer harmonic torques in amplitude and frequency for running up and continuous operation; — machine air gap torques for agreed conditions, stating all assumptions. This information is critical for LCI drives. | 9.4.7, Table 22 | PDF | CFIHOS-70000083
S747-IR-33 | Utility summary, consumption data and electrical load list | Document providing input to engineering for design of the customer's installation or utility arrangement, stating the normal and maximum consumption of e.g. compressed air, heating/cooling media, electrical power, etc., for the equipment or unit(s). The following generalized index shall be used: — equipment tag no; — type of utility; — utility consumption figures, for example: - individual consumers of high and low voltage switchboards with details of auxiliary loads, type of load, load factors, approximate power consumption data in operation and standby mode; - auxiliary power supply requirements (voltage, kVA) to make provision in the feeding switchgear. | 9.2.2.3 | PDF | CFIHOS-70000203
S747-IR-73 | Upstream feeder protection device data | A register documenting agreements and responsibilities between internal and external parties (esp. between contract scopes). An overview of all communications (also called interface queries) and their status between two parties for the management of interface communication. This document provides details of upstream feeder protection device data including type of device, opening time of breaker, current rating, trip characteristics, etc. as required by the manufacturer to safeguard the drive in accordance with equipment design parameters. | 8.3.2.2 | PDF | CFIHOS-70000083
S747-IR-35 | Heat dissipation summary | This document contains the calculation by the manufacturer to arrive at the heat load produced by the BDM/CDM to enable HVAC sizing and includes generic information on the 'switching frequency value (kHz)' vs. 'heat dissipation data of drive (watts)'. Switching frequency has an impact on the heat dissipation of drive (due to converter switching losses). In case of water cooled drives, the heat loss to air and to water shall be mentioned separately. Heat dissipation data of CDM components (like reactor, transformer, etc.) shall also be included as part of this document. | 5.9.2.1.1 | PDF | CFIHOS-70000441
S747-IR-66 | Control and interface block diagram (BDM/CDM/PDS) | A pictorial representation of the main elements and functions of major components within the system. This diagram details the interfaces between different blocks of the system and external equipment/systems which includes signal exchanges, interlocks and logic functions of the system. The document may also detail the specification of interface hardware (cable specification, communication protocol, etc.). | 9.2.2.1, 9.2.2.2, 9.2.2.3, Table 23, Table 24, Table 25 | PDF | CFIHOS-70000066
S747-IR-37 | Wiring diagram | Diagram providing information on the circuitry of an object. Mandatory content of information: — graphical symbols representing the objects; — graphical symbols representing the connections among objects; — reference designations; — terminal designations; — signal level conventions (applicable to logic signals); — information necessary to trace paths and circuits (signal designations, location references); — supplementary information necessary for the understanding of functions; — technical data; — references to other documents; — information about wiring logic; — cable and cable core identification; — maximum cross section area and number of runs of power cables; — user interfaces (wiring connection with field components / client's equipment). | 5.2.4.3, 5.3.6.2.3.2, 5.4.4.1, 7.2, 8.2.1.1, 8.2.1.2, 8.3.3.3.6, 8.3.8, 8.4.2.2, 8.5.1.1, 8.5.1.2, 8.5.1.3, 9.2.2.1, 9.2.2.2, 9.2.2.3, Table 23, Table 24, Table 25 | PDF | CFIHOS-70000268
S747-IR-70 | Inter-connection diagram | Diagram providing information about the physical connections among components or units. Mandatory content of information: — conductor or cable type information (e.g. recognized type designation, catalogue or part number, material, construction, size, insulation, voltage rating, colour, number of conductors, other technical data); — reference designation or conductor or cable number; — identification or representation of the connected objects (e.g. reference and/or terminal designation); — signal designation and/or technical data about the signal. Optional content of information: — instruction for or methods of laying, routing, termination, attachment, twisting, screening, etc.; — length of connection; — special classification or information. | 8.4.2.2 | PDF | CFIHOS-70000055
S747-IR-39 | Earthing diagram | A diagram detailing earthing (grounding) for plant and equipment. This document shall include customized earthing solutions, detailed installation requirements and associated protections (e.g. ground fault protection, insulation monitoring, etc.) | 9.2.5.2 | PDF | CFIHOS-70000103
S747-IR-40 | Equipment piping and instrumentation diagram | The piping and instrument diagram (P&ID), based on the process flow diagram, represents the technical realization of a process by means of graphical symbols for equipment and piping together with graphical symbols or process measurement and control functions. Mandatory content of information: — function or type of equipment, including drives as well as installed spares; — identification number of equipment including drives as well as installed spares; — characteristic data of equipment; — indication of nominal diameter, pressure rating, material and type of piping; — details of equipment, piping, valves and fittings, thermal insulation; — sensors, probes and interface signals exchange with control system; — process measurement and control functions with identification number; — characteristic data of drives. Optional content of information: — denomination of flow rates and amounts of energy or energy carriers; — route and direction of flow of energy or energy carriers; — type of essential primary elements and sensors; — essential construction materials for equipment; — elevation of platforms and approximate relative vertical position of equipment; — reference designation for valves and fittings; — denomination of equipment. This document is expected for cooling system of liquid cooled drives and liquid filled transformers. The purchaser's instrument / signal tag numbers shall be incorporated in the final submission. | 8.3.3.3.2, 8.3.3.3.6 | PDF | CFIHOS-70000292
S747-IR-41 | Data address mapping list | An authoritative collection of values with a relationship to specific equipment. List to show input and output address map of BDM for communication with (connected to) SAS/SIS system. The columns of this collection are specified and controlled. | 5.9.2.4 | PDF | CFIHOS-70000179
S747-IR-42 | Drive parameter setting list | A structured compilation of parameters, options, settings and preferences stored electronically (different file formats) in the equipment memory for achieving the desired functionality and performance by the equipment. This data can be transferred between the equipment and its programming device via communicating link using the specified protocol and application software. The BDM parameter setting list can be an exhaustive list of the all the configurable parameters with a settable range for each parameter, selectable options, least count of value, default values, etc. The parameter setting list provides the record of set values of the drive during commissioning intended for safe operation. As a minimum, the list contains the set values of following parameters: minimum and maximum speed range — ramping times (up and down); — no-go zones for critical speeds; — maximum current limit; — overcurrent limit; — stop (ramp down/coast to stop); — communication address; — action on loss of speed setpoint; — action on loss of communications. | 5.9.2.4 | PDF | CFIHOS-70000012
S747-IR-43 | Bill of materials (BDM/CDM/PDS) | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and technical specifications. Note: This document includes details of sub-suppliers & items of associated purchase orders. | 8.3.3.3.2, 8.3.3.3.4 | PDF | CFIHOS-70000028
S747-IR-44 | Recommended spare part list (BDM/CDM/PDS) | The recommended spare part list shall cover commissioning spares, 6 years maintenance spares and capital/insurance spares. Table containing list items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for later use. Mandatory content of information: — item reference number; — quantity; — part number or global identifier (together with manufacturer / supplier); — part name; — expected service life and replacement frequency of components, if applicable; — type designation; — specifying technical data. Optional content of information: — descriptive technical data; — mass, dimensions; — reference to document; — remarks. | Table 22 | PDF | CFIHOS-70000374
S747-IR-46 | Drive configuration and remote access software | A computer program designed for a specific task or use. The drive software can be used throughout a drive’s life cycle to: — displays the drive’s parameters and signals — program, review, compare, and drive save parameters; — quick setup/configuration features for easy commissioning; — backup and restore configuration files; — view, clear faults and access to the data and fault loggers — monitor signals graphically (trending) and numerically, set triggers for data monitoring and collection; — control the drive from the desktop/laptop. | 5.9.2.4 | - | CFIHOS-70000012
S747-IR-47 | Special tools list | The special tools list shall identify all special tools necessary for handling, dismantling, maintenance etc. of equipment. The special tools list shall include: — identification - the tag number the special tool shall support; — description of the special tool; — power supply requirement, if any; — storage, i.e. the location where the special tool can be found; — document references, if applicable. Note that the actual special tool shall be marked with the identification, i.e. tag number that it supports. | 5.9.2.4 | PDF | CFIHOS-70000454
S747-IR-48 | Installation manual (BDM/CDM/PDS) | Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. of the equipment. Note: Unless otherwise agreed, this document can be delivered as part of manufacturer's standard installation, operation and maintenance manual or as a standalone document. | 7.3, 7.4, 7.5.1, 10.2, 10.3 | PDF | CFIHOS-70000181
S747-IR-49 | Commissioning instruction (BDM/CDM/PDS) | Instruction providing information on the commissioning of the product. Instructions for commissioning are provided especially for large and highly complex products and for large industrial installations. The purpose of such instructions is to provide the user with the information needed for initial setting-up of the product. These instructions should contain for example: — download program, software instructions; — checking instructions; — checks to be performed before connection to the supply network and before first operation; — details of specifications to apply to acceptance, inspection and performance tests. | 7.3 | PDF | CFIHOS-70000366
S747-IR-50 | Operating manual (BDM/CDM/PDS) | Description of methods of operating a piece of equipment or process unit, including but not limited to instructions, procedures, drawings, tables, etc. for the operation -stop, start, and emergency shutdown. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard installation, operation and maintenance manual or as a stand alone document. | 7.3 | PDF | CFIHOS-70000228
S747-IR-51 | Maintenance manual (BDM/CDM/PDS) | Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package supplier. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard installation, operation and maintenance manual or as a standalone document. The supplier shall confirm the following: — the lifetime of the electronic controls; — the availability of spare parts; — the expected duration of the replacement process; — the availability of software support for the BDM/CDM during the lifetime of the applied control system. | 7.4 | PDF | CFIHOS-70000206
S747-IR-67 | Type test certificate | The certificate to provide evidence that the design meets the requirements of the technical and functional specification, including acoustic noise (type test), NRTL(ACO) product safety certification and listing to UL 61800-5-1 (CSA C22.2 NO. 61800-5-1). | 5.2.4.1, 5.2.4.3, 5.2.4.4, 5.3.6.2.1, 6.6.11, 7.3, 8.1, 8.2.3.2, 8.2.3.3, 8.2.3.4, 8.2.3.5, 8.2.3.6, 8.3.9.1, 8.3.9.2, 9.1.1, 9.1.2, 9.3.1 | PDF | CFIHOS-70000239
S747-IR-53 | Hazardous area certificate (equipment and individual components) | Attestation issued by a recognized independent authority certifying that a type test has satisfied the specified standards; e.g. ATEX, BASEEFA, PTB, UL, CSA, NEMA, EX, etc. Examples of ratings include Intrinsically Safe & Explosion Proof. To include any special requirements for safe use, barrier/isolator to be used, etc. | 5.14 | PDF | CFIHOS-70000160
S747-IR-54 | Seismic certification | Certification by a third party declaring approval of the equipment in accordance with the standards specified to be installed in a location with the seismic activity specified. | 5.9.2.3 | PDF | CFIHOS-70000013
S747-IR-56 | Marine certificate (additional) | A document certifying compliance with specified requirements. [International Maritime Organization (IMO), International Association of Classification Societies Ltd. (IACS) or any other classification societies who provide a list of rules and requirements]. The agency designated for issue of certificates may be DNV, Lloyds, ABS/USCG or other. | 7.5.2 | PDF | CFIHOS-70000239
S747-IR-57 | Declaration of conformity (BDM/CDM/PDS) | Declaration that contains sufficient information to enable a recipient of the declaration of conformity to identify the issuer of the declaration, the object of the declaration, the standards and other specified requirements with which conformity is declared, and the person signing for and on behalf of the issuer of the declaration of conformity (first party). | 5.5, 5.6, 5.7, 7.5.2, 8.2.3.1, 9.1.1, 9.1.2, 9.3.2, 9.3.3 | PDF | CFIHOS-70000431
S747-IR-58 | Factory acceptance test (FAT) procedure (BDM/CDM/PDS) | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document shall include all testing activities and their acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Test set-up and test equipment shall be defined. | Table 22 | PDF | CFIHOS-70000427
S747-IR-60 | Factory acceptance test (FAT) records (BDM/CDM/PDS) | The FAT report will be used to verify that the equipment has been tested according to FAT procedure. The FAT report will be used for acceptance of the equipment delivery. This document shall include all testing activities and their acceptance criteria according, in accordance with the FAT procedure, to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Test set-up and test equipment shall be defined. | 5.2.4.3, 5.4.1.4.1.2, 5.4.1.4.1.3, 5.4.4.1, 5.6, 5.7, 7.3, 5.4.3, 6.5.1, 8.3.3.1.1, 8.3.3.1.2, 8.3.4.3, 9.2.2.1, 9.2.2.2, 9.2.2.3, 9.4.1, 9.4.2, 9.4.3, 9.4.4, 9.4.5, Table 11, Table 22, Table 23, Table 24, Table 25 | PDF | CFIHOS-70000429
S747-IR-63 | Packing list | A list describing the contents of a shipment received. Synonyms: Inventory, packing slip, bill of landing. | 10.2, 10.3 | PDF | CFIHOS-70000269
S747-IR-77 | Site acceptance test (SAT) procedure | Procedure documenting the manufacturer's recommended site tests including discrete functional unit and overall assembly, electrical, mechanical, protection relay, etc. The procedure may include power quality measurements (harmonics) when converter fed motors are installed. | 6.6.3.7.6 | PDF | CFIHOS-70000428
S747-IR-78 | Site acceptance test (SAT) records | Records demonstrating results of site tests typically including discrete functional unit and overall assembly, electrical, mechanical, protection relay, etc. | 6.6.3.7.6 | PDF | CFIHOS-70000430
S747-IR-79 | Material safety data sheet | A data sheet which summarizes the physical and chemical properties of a substance, description of its harmful nature including potential impact on the health and safety of personnel and of the environment and precautions necessary to ensure its safe use and eventual disposal. This document is typically provided for chemicals used in drive cooling systems, transformer oil, etc. | 5.2.4.3 | PDF | CFIHOS-70000211
S747-IR-81 | Drive configuration / settings file | A structured compilation of parameters, options, settings and preferences stored electronically (different file formats) in the equipment memory for achieving the desired functionality and performance by the equipment. This data can be transferred between the equipment and its programming device via communicating link using the specified protocol and application software. | 9.2.2.1 | PDF | CFIHOS-70000012
Purchase Order Specific Information Requirements

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: